## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2029-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2029-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2029-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2029-1_0_4_node_18 | 0.4 | n |  | TRUE
4 | bus_LV_2029-1_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2029-1_0_4_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_2029-1_0_4_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_2029-1_0_4_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_2029-1_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_2029-1_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_2029-1_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2029-1_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_2029-1_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2029-1_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2029-1_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2029-1_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2029-1_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_2029-1_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2029-1_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2029-1_0_4_node_63 | 0.4 | n |  | TRUE
20 | bus_LV_2029-1_0_4_node_64 | 0.4 | n |  | TRUE
21 | bus_LV_2029-1_0_4_node_65 | 0.4 | n |  | TRUE
22 | bus_LV_2029-1_0_4_node_62 | 0.4 | n |  | TRUE
23 | bus_LV_2029-1_0_4_node_59 | 0.4 | n |  | TRUE
24 | bus_LV_2029-1_0_4_node_57 | 0.4 | n |  | TRUE
25 | bus_LV_2029-1_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_2029-1_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_2029-1_0_4_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_2029-1_0_4_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_2029-1_0_4_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_2029-1_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_2029-1_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_2029-1_0_4_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_2029-1_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2029-1_0_4_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_2029-1_0_4_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_2029-1_0_4_node_107 | 0.4 | n |  | TRUE
37 | bus_LV_2029-1_0_4_node_104 | 0.4 | n |  | TRUE
38 | bus_LV_2029-1_0_4_node_105 | 0.4 | n |  | TRUE
39 | bus_LV_2029-1_0_4_node_103 | 0.4 | n |  | TRUE
40 | bus_LV_2029-1_0_4_node_106 | 0.4 | n |  | TRUE
41 | bus_LV_2029-1_0_4_node_108 | 0.4 | n |  | TRUE
42 | bus_LV_2029-1_0_4_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_2029-1_0_4_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_2029-1_0_4_node_79 | 0.4 | n |  | TRUE
45 | bus_LV_2029-1_0_4_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_2029-1_0_4_node_80 | 0.4 | n |  | TRUE
47 | bus_LV_2029-1_0_4_node_78 | 0.4 | n |  | TRUE
48 | bus_LV_2029-1_0_4_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_2029-1_0_4_node_81 | 0.4 | n |  | TRUE
50 | bus_LV_2029-1_0_4_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_2029-1_0_4_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_2029-1_0_4_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_2029-1_0_4_node_75 | 0.4 | n |  | TRUE
54 | bus_LV_2029-1_0_4_node_74 | 0.4 | n |  | TRUE
55 | bus_LV_2029-1_0_4_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_2029-1_0_4_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_2029-1_0_4_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_2029-1_0_4_node_82 | 0.4 | n |  | TRUE
59 | bus_LV_2029-1_0_4_node_102 | 0.4 | n |  | TRUE
60 | bus_LV_2029-1_0_4_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_2029-1_0_4_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_2029-1_0_4_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_2029-1_0_4_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_2029-1_0_4_node_45 | 0.4 | n |  | TRUE
65 | bus_LV_2029-1_0_4_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_2029-1_0_4_node_47 | 0.4 | n |  | TRUE
67 | bus_LV_2029-1_0_4_node_167 | 0.4 | n |  | TRUE
68 | bus_LV_2029-1_0_4_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_2029-1_0_4_node_168 | 0.4 | n |  | TRUE
70 | bus_LV_2029-1_0_4_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_2029-1_0_4_node_51 | 0.4 | n |  | TRUE
72 | bus_LV_2029-1_0_4_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_2029-1_0_4_node_53 | 0.4 | n |  | TRUE
74 | bus_LV_2029-1_0_4_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_2029-1_0_4_node_54 | 0.4 | n |  | TRUE
76 | bus_LV_2029-1_0_4_node_55 | 0.4 | n |  | TRUE
77 | bus_LV_2029-1_0_4_node_56 | 0.4 | n |  | TRUE
78 | bus_LV_2029-1_0_4_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_2029-1_0_4_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_2029-1_0_4_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_2029-1_0_4_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_2029-1_0_4_node_67 | 0.4 | n |  | TRUE
83 | bus_LV_2029-1_0_4_node_68 | 0.4 | n |  | TRUE
84 | bus_LV_2029-1_0_4_node_69 | 0.4 | n |  | TRUE
85 | bus_LV_2029-1_0_4_node_70 | 0.4 | n |  | TRUE
86 | bus_LV_2029-1_0_4_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_2029-1_0_4_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_2029-1_0_4_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_2029-1_0_4_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_2029-1_0_4_node_77 | 0.4 | n |  | TRUE
91 | bus_LV_2029-1_0_4_node_83 | 0.4 | n |  | TRUE
92 | bus_LV_2029-1_0_4_node_84 | 0.4 | n |  | TRUE
93 | bus_LV_2029-1_0_4_node_85 | 0.4 | n |  | TRUE
94 | bus_LV_2029-1_0_4_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_2029-1_0_4_node_87 | 0.4 | n |  | TRUE
96 | bus_LV_2029-1_0_4_node_88 | 0.4 | n |  | TRUE
97 | bus_LV_2029-1_0_4_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_2029-1_0_4_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_2029-1_0_4_node_91 | 0.4 | n |  | TRUE
100 | bus_LV_2029-1_0_4_node_101 | 0.4 | n |  | TRUE
101 | bus_LV_2029-1_0_4_node_92 | 0.4 | n |  | TRUE
102 | bus_LV_2029-1_0_4_node_93 | 0.4 | n |  | TRUE
103 | bus_LV_2029-1_0_4_node_170 | 0.4 | n |  | TRUE
104 | bus_LV_2029-1_0_4_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_2029-1_0_4_node_94 | 0.4 | n |  | TRUE
106 | bus_LV_2029-1_0_4_node_110 | 0.4 | n |  | TRUE
107 | bus_LV_2029-1_0_4_node_97 | 0.4 | n |  | TRUE
108 | bus_LV_2029-1_0_4_node_95 | 0.4 | n |  | TRUE
109 | bus_LV_2029-1_0_4_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_2029-1_0_4_node_98 | 0.4 | n |  | TRUE
111 | bus_LV_2029-1_0_4_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_2029-1_0_4_node_111 | 0.4 | n |  | TRUE
113 | bus_MV_477_0_node_22 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2029-1_0_4_load_0 | 0 | 0.00088206 | 0.00022106 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2029-1_0_4_load_1 | 1 | 0.0024396 | 0.00061143 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2029-1_0_4_load_3 | 4 | 0.00025436 | 6.3748e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2029-1_0_4_load_16 | 5 | 0.011577 | 0.0029014 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2029-1_0_4_load_19 | 7 | 0.00028814 | 7.2216e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2029-1_0_4_load_11 | 8 | 0.00067904 | 0.00017018 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2029-1_0_4_load_13 | 11 | 0.00073852 | 0.00018509 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2029-1_0_4_load_10 | 12 | 0.0015221 | 0.00038146 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2029-1_0_4_load_8 | 13 | 0.00058173 | 0.0001458 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2029-1_0_4_load_6 | 14 | 0.00060421 | 0.00015143 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2029-1_0_4_load_7 | 15 | 0.00022532 | 5.6471e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2029-1_0_4_load_9 | 16 | 0.0020163 | 0.00050533 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2029-1_0_4_load_14 | 17 | 0.0041376 | 0.001037 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2029-1_0_4_load_15 | 18 | 0.0052536 | 0.0013167 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2029-1_0_4_load_64 | 20 | 0.0029958 | 0.00075082 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2029-1_0_4_load_65 | 21 | 0.0020636 | 0.0005172 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2029-1_0_4_load_62 | 22 | 0.0026932 | 0.00067498 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2029-1_0_4_load_59 | 23 | 0.001567 | 0.00039272 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2029-1_0_4_load_57 | 24 | 0.0010007 | 0.0002508 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2029-1_0_4_load_20 | 25 | 0.00083825 | 0.00021008 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2029-1_0_4_load_23 | 28 | 0.001638 | 0.00041051 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2029-1_0_4_load_27 | 29 | 0.0015498 | 0.00038842 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2029-1_0_4_load_24 | 30 | 0.00067686 | 0.00016964 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2029-1_0_4_load_26 | 31 | 0.00083874 | 0.00021021 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2029-1_0_4_load_28 | 32 | 0.0007812 | 0.00019579 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2029-1_0_4_load_25 | 33 | 0.0024886 | 0.00062369 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2029-1_0_4_load_29 | 34 | 0.00089314 | 0.00022384 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2029-1_0_4_load_107 | 36 | 0.0005187 | 0.00013 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2029-1_0_4_load_104 | 37 | 0.00084249 | 0.00021115 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2029-1_0_4_load_105 | 38 | 0.00039211 | 9.8273e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2029-1_0_4_load_103 | 39 | 0.001045 | 0.0002619 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2029-1_0_4_load_106 | 40 | 0.0010088 | 0.00025282 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2029-1_0_4_load_108 | 41 | 0.00072034 | 0.00018054 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2029-1_0_4_load_31 | 42 | 0.0011788 | 0.00029542 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2029-1_0_4_load_32 | 43 | 0.00085047 | 0.00021315 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2029-1_0_4_load_79 | 44 | 0.00060061 | 0.00015053 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2029-1_0_4_load_33 | 45 | 0.00079795 | 0.00019999 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2029-1_0_4_load_80 | 46 | 0.0016894 | 0.00042341 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2029-1_0_4_load_78 | 47 | 0.00022381 | 5.6093e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2029-1_0_4_load_40 | 48 | 0.00078627 | 0.00019706 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2029-1_0_4_load_81 | 49 | 0.0003534 | 8.8569e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2029-1_0_4_load_38 | 50 | 0.00030353 | 7.6072e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2029-1_0_4_load_34 | 51 | 0.0015112 | 0.00037875 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2029-1_0_4_load_35 | 52 | 0.00051235 | 0.00012841 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2029-1_0_4_load_75 | 53 | 0.0012098 | 0.00030322 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2029-1_0_4_load_36 | 55 | 0.0020656 | 0.00051769 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2029-1_0_4_load_37 | 56 | 0.00092387 | 0.00023154 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2029-1_0_4_load_82 | 58 | 0.0019476 | 0.0004881 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2029-1_0_4_load_102 | 59 | 0.00027045 | 6.7781e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2029-1_0_4_load_41 | 60 | 0.00067241 | 0.00016852 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2029-1_0_4_load_42 | 61 | 0.0045386 | 0.0011375 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2029-1_0_4_load_44 | 62 | 0.0015096 | 0.00037835 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2029-1_0_4_load_43 | 63 | 0.0030117 | 0.0007548 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2029-1_0_4_load_45 | 64 | 0.0015679 | 0.00039296 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2029-1_0_4_load_46 | 65 | 0.0015635 | 0.00039186 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2029-1_0_4_load_47 | 66 | 0.0010645 | 0.00026679 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2029-1_0_4_load_167 | 67 | 0.0019453 | 0.00048754 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2029-1_0_4_load_48 | 68 | 0.0024324 | 0.00060962 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2029-1_0_4_load_168 | 69 | 0.00052545 | 0.00013169 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2029-1_0_4_load_51 | 71 | 0.0018999 | 0.00047616 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2029-1_0_4_load_49 | 72 | 0.0021523 | 0.00053941 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2029-1_0_4_load_53 | 73 | 0.0051641 | 0.0012942 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2029-1_0_4_load_52 | 74 | 0.002965 | 0.00074311 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2029-1_0_4_load_54 | 75 | 0.0014543 | 0.00036449 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2029-1_0_4_load_55 | 76 | 0.0012175 | 0.00030514 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2029-1_0_4_load_58 | 78 | 0.0039963 | 0.0010016 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2029-1_0_4_load_60 | 79 | 0.0019529 | 0.00048944 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2029-1_0_4_load_61 | 80 | 0.0018566 | 0.0004653 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2029-1_0_4_load_66 | 81 | 0.0010636 | 0.00026657 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2029-1_0_4_load_67 | 82 | 0.0018091 | 0.0004534 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2029-1_0_4_load_68 | 83 | 0.0031773 | 0.00079631 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2029-1_0_4_load_69 | 84 | 0.0048452 | 0.0012143 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2029-1_0_4_load_70 | 85 | 0.0051567 | 0.0012924 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2029-1_0_4_load_71 | 86 | 0.0041199 | 0.0010325 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2029-1_0_4_load_72 | 87 | 0.0062632 | 0.0015697 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2029-1_0_4_load_73 | 88 | 0.00069775 | 0.00017487 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2029-1_0_4_load_76 | 89 | 0.00411 | 0.0010301 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2029-1_0_4_load_77 | 90 | 0.00057265 | 0.00014352 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2029-1_0_4_load_83 | 91 | 0.003551 | 0.00088997 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2029-1_0_4_load_84 | 92 | 0.0020117 | 0.00050418 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2029-1_0_4_load_85 | 93 | 0.0010165 | 0.00025476 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2029-1_0_4_load_87 | 95 | 0.0019051 | 0.00047747 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2029-1_0_4_load_88 | 96 | 0.00054818 | 0.00013739 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2029-1_0_4_load_89 | 97 | 0.00093261 | 0.00023373 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2029-1_0_4_load_90 | 98 | 0.0006709 | 0.00016814 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2029-1_0_4_load_101 | 100 | 0.00042688 | 0.00010699 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2029-1_0_4_load_93 | 102 | 0.00092816 | 0.00023262 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2029-1_0_4_load_170 | 103 | 0.00048772 | 0.00012224 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2029-1_0_4_load_94 | 105 | 0.00050487 | 0.00012653 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2029-1_0_4_load_110 | 106 | 0.00041451 | 0.00010388 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2029-1_0_4_load_97 | 107 | 0.0011962 | 0.0002998 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2029-1_0_4_load_95 | 108 | 0.00022033 | 5.522e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2029-1_0_4_load_96 | 109 | 0.0011785 | 0.00029537 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2029-1_0_4_load_98 | 110 | 0.00073981 | 0.00018541 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2029-1_0_4_load_100 | 111 | 0.00052342 | 0.00013118 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2029-1_0_4_load_111 | 112 | 0.00054165 | 0.00013575 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 85 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2029-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.023004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2029-1_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.013451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2029-1_0_4_line_2 | NAYY 4x150 SE | 0 | 3 | 0.15686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2029-1_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0022572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2029-1_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.051741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2029-1_0_4_line_5 | NAYY 4x150 SE | 4 | 8 | 0.018016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2029-1_0_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.045872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2029-1_0_4_line_7 | NAYY 4x150 SE | 6 | 7 | 0.036999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2029-1_0_4_line_8 | NAYY 4x150 SE | 8 | 9 | 0.0065684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2029-1_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.0236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2029-1_0_4_line_10 | NAYY 4x150 SE | 10 | 11 | 0.033004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2029-1_0_4_line_11 | NAYY 4x150 SE | 10 | 12 | 0.035047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2029-1_0_4_line_12 | NAYY 4x150 SE | 12 | 13 | 0.020848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2029-1_0_4_line_13 | NAYY 4x150 SE | 13 | 14 | 0.13196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2029-1_0_4_line_14 | NAYY 4x150 SE | 14 | 15 | 0.068721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2029-1_0_4_line_15 | NAYY 4x150 SE | 15 | 16 | 0.021736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2029-1_0_4_line_16 | NAYY 4x150 SE | 16 | 17 | 0.022854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2029-1_0_4_line_17 | NAYY 4x150 SE | 17 | 18 | 0.029356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2029-1_0_4_line_18 | NAYY 4x150 SE | 18 | 19 | 0.030487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2029-1_0_4_line_19 | NAYY 4x150 SE | 19 | 20 | 0.017398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2029-1_0_4_line_20 | NAYY 4x150 SE | 19 | 21 | 0.063164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2029-1_0_4_line_21 | NAYY 4x150 SE | 19 | 22 | 0.021495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2029-1_0_4_line_22 | NAYY 4x150 SE | 20 | 63 | 0.063895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2029-1_0_4_line_23 | NAYY 4x150 SE | 21 | 81 | 0.0081858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2029-1_0_4_line_24 | NAYY 4x150 SE | 22 | 80 | 0.018663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2029-1_0_4_line_25 | NAYY 4x150 SE | 23 | 24 | 0.090234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2029-1_0_4_line_26 | NAYY 4x150 SE | 24 | 77 | 0.01154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2029-1_0_4_line_27 | NAYY 4x150 SE | 25 | 26 | 0.079892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2029-1_0_4_line_28 | NAYY 4x150 SE | 25 | 27 | 0.041344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2029-1_0_4_line_29 | NAYY 4x150 SE | 26 | 28 | 0.1124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2029-1_0_4_line_30 | NAYY 4x150 SE | 26 | 29 | 0.27021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2029-1_0_4_line_31 | NAYY 4x150 SE | 27 | 30 | 0.012749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2029-1_0_4_line_32 | NAYY 4x150 SE | 29 | 31 | 0.0082916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2029-1_0_4_line_33 | NAYY 4x150 SE | 30 | 33 | 0.01592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2029-1_0_4_line_34 | NAYY 4x150 SE | 31 | 32 | 0.024251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2029-1_0_4_line_35 | NAYY 4x150 SE | 32 | 34 | 0.005371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2029-1_0_4_line_36 | NAYY 4x150 SE | 34 | 35 | 0.080347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2029-1_0_4_line_37 | NAYY 4x150 SE | 35 | 36 | 0.38052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2029-1_0_4_line_38 | NAYY 4x150 SE | 36 | 41 | 0.26349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2029-1_0_4_line_39 | NAYY 4x150 SE | 36 | 40 | 0.034489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2029-1_0_4_line_40 | NAYY 4x150 SE | 37 | 38 | 0.011894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2029-1_0_4_line_41 | NAYY 4x150 SE | 37 | 39 | 0.11316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2029-1_0_4_line_42 | NAYY 4x150 SE | 38 | 40 | 0.020815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2029-1_0_4_line_43 | NAYY 4x150 SE | 39 | 59 | 0.2405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2029-1_0_4_line_44 | NAYY 4x150 SE | 39 | 57 | 0.37005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_2029-1_0_4_line_45 | NAYY 4x150 SE | 42 | 43 | 0.029628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
46 | LV_2029-1_0_4_line_46 | NAYY 4x150 SE | 42 | 44 | 0.14493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
47 | LV_2029-1_0_4_line_47 | NAYY 4x150 SE | 43 | 45 | 0.0023506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_2029-1_0_4_line_48 | NAYY 4x150 SE | 44 | 46 | 0.041035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2029-1_0_4_line_49 | NAYY 4x150 SE | 44 | 47 | 0.015117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_2029-1_0_4_line_50 | NAYY 4x150 SE | 45 | 48 | 0.0044133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_2029-1_0_4_line_51 | NAYY 4x150 SE | 46 | 49 | 0.017554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2029-1_0_4_line_52 | NAYY 4x150 SE | 47 | 90 | 0.030689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_2029-1_0_4_line_53 | NAYY 4x150 SE | 48 | 50 | 0.017839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_2029-1_0_4_line_54 | NAYY 4x150 SE | 49 | 58 | 0.052359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2029-1_0_4_line_55 | NAYY 4x150 SE | 50 | 55 | 0.01601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_2029-1_0_4_line_56 | NAYY 4x150 SE | 51 | 52 | 0.001959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2029-1_0_4_line_57 | NAYY 4x150 SE | 52 | 53 | 0.022193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2029-1_0_4_line_58 | NAYY 4x150 SE | 53 | 54 | 0.021194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2029-1_0_4_line_59 | NAYY 4x150 SE | 54 | 89 | 0.040975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_2029-1_0_4_line_60 | NAYY 4x150 SE | 54 | 88 | 0.0076496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
61 | LV_2029-1_0_4_line_61 | NAYY 4x150 SE | 55 | 56 | 0.021476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_2029-1_0_4_line_62 | NAYY 4x150 SE | 56 | 57 | 0.020904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
63 | LV_2029-1_0_4_line_63 | NAYY 4x150 SE | 58 | 91 | 0.0015266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2029-1_0_4_line_64 | NAYY 4x150 SE | 59 | 100 | 0.020073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2029-1_0_4_line_65 | NAYY 4x150 SE | 60 | 61 | 0.02849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2029-1_0_4_line_66 | NAYY 4x150 SE | 60 | 62 | 0.15457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2029-1_0_4_line_67 | NAYY 4x150 SE | 61 | 63 | 0.0055495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2029-1_0_4_line_68 | NAYY 4x150 SE | 64 | 65 | 0.015495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2029-1_0_4_line_69 | NAYY 4x150 SE | 64 | 66 | 0.010445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2029-1_0_4_line_70 | NAYY 4x150 SE | 64 | 67 | 0.28648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2029-1_0_4_line_71 | NAYY 4x150 SE | 65 | 68 | 0.01473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2029-1_0_4_line_72 | NAYY 4x150 SE | 67 | 69 | 0.0083281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2029-1_0_4_line_73 | NAYY 4x150 SE | 68 | 70 | 0.020502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2029-1_0_4_line_74 | NAYY 4x150 SE | 70 | 71 | 0.018102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2029-1_0_4_line_75 | NAYY 4x150 SE | 70 | 72 | 0.056389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2029-1_0_4_line_76 | NAYY 4x150 SE | 71 | 73 | 0.01575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2029-1_0_4_line_77 | NAYY 4x150 SE | 73 | 74 | 0.0098888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2029-1_0_4_line_78 | NAYY 4x150 SE | 74 | 75 | 0.017945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2029-1_0_4_line_79 | NAYY 4x150 SE | 75 | 76 | 0.014094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2029-1_0_4_line_80 | NAYY 4x150 SE | 76 | 77 | 0.020236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2029-1_0_4_line_81 | NAYY 4x150 SE | 77 | 78 | 0.040705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2029-1_0_4_line_82 | NAYY 4x150 SE | 78 | 79 | 0.03376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2029-1_0_4_line_83 | NAYY 4x150 SE | 79 | 80 | 0.025684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2029-1_0_4_line_84 | NAYY 4x150 SE | 81 | 82 | 0.0047583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
85 | LV_2029-1_0_4_line_85 | NAYY 4x150 SE | 82 | 83 | 0.020793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_2029-1_0_4_line_86 | NAYY 4x150 SE | 83 | 84 | 0.014418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
87 | LV_2029-1_0_4_line_87 | NAYY 4x150 SE | 84 | 85 | 0.042508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_2029-1_0_4_line_88 | NAYY 4x150 SE | 85 | 86 | 0.035767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
89 | LV_2029-1_0_4_line_89 | NAYY 4x150 SE | 86 | 87 | 0.0059412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_2029-1_0_4_line_90 | NAYY 4x150 SE | 87 | 88 | 0.0033079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
91 | LV_2029-1_0_4_line_91 | NAYY 4x150 SE | 89 | 90 | 0.02742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
92 | LV_2029-1_0_4_line_92 | NAYY 4x150 SE | 91 | 92 | 0.02502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2029-1_0_4_line_93 | NAYY 4x150 SE | 92 | 93 | 0.022689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2029-1_0_4_line_94 | NAYY 4x150 SE | 93 | 94 | 0.17489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2029-1_0_4_line_95 | NAYY 4x150 SE | 94 | 95 | 0.044556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2029-1_0_4_line_96 | NAYY 4x150 SE | 94 | 96 | 0.043132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2029-1_0_4_line_97 | NAYY 4x150 SE | 95 | 97 | 0.025547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2029-1_0_4_line_98 | NAYY 4x150 SE | 97 | 98 | 0.16903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2029-1_0_4_line_99 | NAYY 4x150 SE | 98 | 99 | 0.021646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2029-1_0_4_line_100 | NAYY 4x150 SE | 99 | 101 | 0.048361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2029-1_0_4_line_101 | NAYY 4x150 SE | 99 | 102 | 0.0081778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2029-1_0_4_line_102 | NAYY 4x150 SE | 101 | 103 | 0.085486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2029-1_0_4_line_103 | NAYY 4x150 SE | 101 | 104 | 0.028349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2029-1_0_4_line_104 | NAYY 4x150 SE | 102 | 105 | 0.015577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2029-1_0_4_line_105 | NAYY 4x150 SE | 103 | 106 | 0.23961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2029-1_0_4_line_106 | NAYY 4x150 SE | 104 | 107 | 0.002556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2029-1_0_4_line_107 | NAYY 4x150 SE | 105 | 108 | 0.015805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2029-1_0_4_line_108 | NAYY 4x150 SE | 106 | 112 | 0.010652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2029-1_0_4_line_109 | NAYY 4x150 SE | 107 | 110 | 0.076178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2029-1_0_4_line_110 | NAYY 4x150 SE | 108 | 109 | 0.01355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2029-1_0_4_line_111 | NAYY 4x150 SE | 110 | 111 | 0.10265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2029-1_0_4_trafo_70 | 0.25 MVA 20/0.4 kV | 113 | 85 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2565948.3046 | 1184509.1548 | 2565946.9917 | 1184505.2623 | 2565941.878 | 1184487.0714
1 | 2565947.2129 | 1184521.2918 | 2565949.7762 | 1184518.3979 | 2565950.2215 | 1184514.8379 | 2565948.3046 | 1184509.1548
2 | 2565948.3046 | 1184509.1548 | 2566103.8479 | 1184488.8505
3 | 2565947.2129 | 1184521.2918 | 2565946.9967 | 1184523.5387
4 | 2566103.8479 | 1184488.8505 | 2566105.1868 | 1184478.6598 | 2566107.3195 | 1184471.1548 | 2566110.5913 | 1184465.3109 | 2566114.1565 | 1184461.4108 | 2566123.7345 | 1184454.5084 | 2566131.9159 | 1184448.9813
5 | 2565946.9967 | 1184523.5387 | 2565946.9967 | 1184523.5387 | 2565937.9895 | 1184535.4519 | 2565935.0957 | 1184536.5084
6 | 2566147.8865 | 1184406.446 | 2566143.8941 | 1184413.0832 | 2566140.2568 | 1184421.7863 | 2566137.26 | 1184433.0537 | 2566135.4755 | 1184442.7467 | 2566131.9159 | 1184448.9813
7 | 2566115.5732 | 1184388.264 | 2566124.2723 | 1184393.2506 | 2566147.8865 | 1184406.446
8 | 2565928.9256 | 1184538.7609 | 2565935.0957 | 1184536.5084
9 | 2565907.4231 | 1184531.8021 | 2565915.481 | 1184531.4337 | 2565916.3283 | 1184532.774 | 2565928.9256 | 1184538.7609
10 | 2565907.4231 | 1184531.8021 | 2565906.1556 | 1184537.0677 | 2565900.7267 | 1184543.3687 | 2565892.1213 | 1184552.1002 | 2565890.6988 | 1184555.6102 | 2565890.678 | 1184557.3224 | 2565890.6561 | 1184558.8344
11 | 2565907.4231 | 1184531.8021 | 2565906.5906 | 1184526.3595 | 2565901.9023 | 1184520.6721 | 2565896.7523 | 1184517.0218 | 2565889.075 | 1184515.865 | 2565882.0993 | 1184519.9707
12 | 2565882.0993 | 1184519.9707 | 2565879.9389 | 1184521.2423 | 2565872.4349 | 1184526.3656 | 2565864.7416 | 1184531.511
13 | 2565763.3785 | 1184519.2286 | 2565763.1061 | 1184522.4335 | 2565762.7623 | 1184526.3709 | 2565763.5957 | 1184533.2809 | 2565767.5908 | 1184540.5063 | 2565771.1417 | 1184544.8105 | 2565775.5145 | 1184548.6875 | 2565783.1606 | 1184552.379 | 2565790.9284 | 1184554.6802 | 2565804.0952 | 1184557.4618 | 2565811.304 | 1184558.0987 | 2565819.2387 | 1184557.5419 | 2565827.332 | 1184555.3722 | 2565843.527 | 1184547.153 | 2565859.5089 | 1184535.0108 | 2565864.7416 | 1184531.511
14 | 2565763.3785 | 1184519.2286 | 2565763.3849 | 1184519.1524 | 2565768.5307 | 1184507.4167 | 2565781.3747 | 1184483.1524 | 2565787.5147 | 1184462.4173 | 2565789.1336 | 1184455.8633
15 | 2565794.3348 | 1184434.7588 | 2565793.6985 | 1184437.3353 | 2565790.424 | 1184450.6389 | 2565789.1336 | 1184455.8633
16 | 2565798.9177 | 1184412.382 | 2565798.7364 | 1184413.4048 | 2565796.5258 | 1184425.8908 | 2565796.0408 | 1184427.8502 | 2565794.3348 | 1184434.7588
17 | 2565798.9177 | 1184412.382 | 2565801.2725 | 1184399.0938 | 2565802.1906 | 1184383.2592
18 | 2565803.2667 | 1184352.8023 | 2565803.2314 | 1184365.3091 | 2565802.1906 | 1184383.2592
19 | 2565803.2667 | 1184352.8023 | 2565789.696 | 1184354.214 | 2565785.9514 | 1184353.9419
20 | 2565803.2667 | 1184352.8023 | 2565802.7167 | 1184347.3914 | 2565800.9601 | 1184339.2083 | 2565796.925 | 1184330.3489 | 2565775.7404 | 1184296.8678
21 | 2565803.2667 | 1184352.8023 | 2565812.6783 | 1184348.8685 | 2565822.4316 | 1184343.1741
22 | 2565785.9514 | 1184353.9419 | 2565784.7326 | 1184353.8534 | 2565766.3351 | 1184350.7682 | 2565753.9431 | 1184350.0722 | 2565744.5598 | 1184350.9598 | 2565736.9894 | 1184352.5263 | 2565729.6155 | 1184355.0699 | 2565724.1721 | 1184358.8917
23 | 2565775.7404 | 1184296.8678 | 2565771.3635 | 1184289.9504
24 | 2565838.5561 | 1184333.776 | 2565836.5808 | 1184334.9133 | 2565822.4316 | 1184343.1741
25 | 2565976.9517 | 1184255.1033 | 2565949.3149 | 1184263.4874 | 2565930.4627 | 1184263.6838 | 2565908.6882 | 1184261.3957 | 2565888.9802 | 1184255.3799
26 | 2565877.9426 | 1184252.0107 | 2565888.9802 | 1184255.3799
27 | 2565336.1792 | 1184484.6862 | 2565323.8804 | 1184506.5804 | 2565289.2817 | 1184549.0517
28 | 2565263.169 | 1184581.106 | 2565289.2817 | 1184549.0517
29 | 2565433.6386 | 1184434.2615 | 2565414.7376 | 1184437.8061 | 2565390.0587 | 1184445.2974 | 2565362.2875 | 1184459.1768 | 2565349.8921 | 1184469.6987 | 2565336.1792 | 1184484.6862
30 | 2565336.1792 | 1184484.6862 | 2565128.2194 | 1184312.1501
31 | 2565263.169 | 1184581.106 | 2565253.7682 | 1184572.4945
32 | 2565120.0353 | 1184310.8194 | 2565128.2194 | 1184312.1501
33 | 2565242.0287 | 1184561.7409 | 2565253.7682 | 1184572.4945
34 | 2565120.0353 | 1184310.8194 | 2565104.4517 | 1184308.2858 | 2565096.6634 | 1184304.974
35 | 2565091.7207 | 1184302.8723 | 2565096.6634 | 1184304.974
36 | 2565023.5141 | 1184261.612 | 2565035.5955 | 1184273.0696 | 2565068.9392 | 1184293.1852 | 2565091.7207 | 1184302.8723
37 | 2565023.5141 | 1184261.612 | 2564939.1822 | 1183890.5595
38 | 2564939.1822 | 1183890.5595 | 2564676.3721 | 1183871.637
39 | 2564971.7743 | 1183879.2785 | 2564939.1822 | 1183890.5595
40 | 2564991.222 | 1183872.0802 | 2565000.2762 | 1183864.3669
41 | 2565105.2355 | 1183842.2585 | 2565042.6091 | 1183838.6532 | 2565028.6757 | 1183842.1699 | 2565009.3258 | 1183856.6576 | 2565000.2762 | 1183864.3669
42 | 2564991.222 | 1183872.0802 | 2564990.299 | 1183872.8665 | 2564971.7743 | 1183879.2785
43 | 2565105.2355 | 1183842.2585 | 2565134.8768 | 1183603.5879
44 | 2565453.3046 | 1183967.8888 | 2565105.2355 | 1183842.2585
45 | 2565533.6014 | 1184046.5487 | 2565526.7097 | 1184041.1816 | 2565511.1606 | 1184027.226
46 | 2565676.8712 | 1184068.4452 | 2565533.6014 | 1184046.5487
47 | 2565509.4113 | 1184025.656 | 2565511.1606 | 1184027.226
48 | 2565676.8712 | 1184068.4452 | 2565676.0581 | 1184048.648 | 2565675.899 | 1184044.8691 | 2565677.371 | 1184028.7187 | 2565677.5542 | 1184027.511
49 | 2565678.8389 | 1184083.4301 | 2565676.9012 | 1184069.1762 | 2565676.8712 | 1184068.4452
50 | 2565509.4113 | 1184025.656 | 2565506.1269 | 1184022.7081
51 | 2565677.5542 | 1184027.511 | 2565680.1875 | 1184010.156
52 | 2565682.8595 | 1184113.8544 | 2565680.687 | 1184097.0248 | 2565678.8389 | 1184083.4301
53 | 2565492.8508 | 1184010.7926 | 2565506.1269 | 1184022.7081
54 | 2565680.1875 | 1184010.156 | 2565685.6891 | 1183973.8974 | 2565686.9202 | 1183966.2974 | 2565687.5946 | 1183958.3395
55 | 2565481.5602 | 1183999.4752 | 2565486.9328 | 1184005.4811 | 2565492.8508 | 1184010.7926
56 | 2565663.4144 | 1184147.8241 | 2565662.1968 | 1184146.2893
57 | 2565677.2074 | 1184165.2103 | 2565663.4144 | 1184147.8241
58 | 2565690.3797 | 1184181.8142 | 2565677.2074 | 1184165.2103
59 | 2565690.3797 | 1184181.8142 | 2565689.9092 | 1184174.324 | 2565689.456 | 1184168.5124 | 2565688.3402 | 1184156.3124 | 2565686.3699 | 1184141.0492
60 | 2565690.3797 | 1184181.8142 | 2565694.7445 | 1184188.0963
61 | 2565481.5602 | 1183999.4752 | 2565467.2416 | 1183983.4688
62 | 2565453.3046 | 1183967.8888 | 2565467.2416 | 1183983.4688
63 | 2565687.7235 | 1183956.8184 | 2565687.5946 | 1183958.3395
64 | 2565127.5722 | 1183584.8906 | 2565134.8768 | 1183603.5879
65 | 2565700.4681 | 1184382.5564 | 2565700.9604 | 1184381.3817 | 2565710.1388 | 1184368.7445 | 2565719.6303 | 1184362.0805
66 | 2565700.4681 | 1184382.5564 | 2565586.8038 | 1184487.2982
67 | 2565724.1721 | 1184358.8917 | 2565719.6303 | 1184362.0805
68 | 2565907.0782 | 1184151.8579 | 2565906.6567 | 1184150.2261 | 2565905.3227 | 1184149.2109 | 2565901.628 | 1184147.809 | 2565893.5436 | 1184146.5506
69 | 2565900.1584 | 1184159.1457 | 2565905.0536 | 1184155.5492 | 2565906.7828 | 1184153.5938 | 2565907.0782 | 1184151.8579
70 | 2565907.0782 | 1184151.8579 | 2566165.1259 | 1184027.4265
71 | 2565893.5436 | 1184146.5506 | 2565893.4304 | 1184146.5329 | 2565887.9048 | 1184146.6645 | 2565884.2251 | 1184147.9084 | 2565879.7018 | 1184150.4812
72 | 2566165.1259 | 1184027.4265 | 2566172.1679 | 1184031.8726
73 | 2565862.5344 | 1184161.6841 | 2565869.4394 | 1184157.1756 | 2565878.6178 | 1184151.0977 | 2565879.7018 | 1184150.4812
74 | 2565862.5344 | 1184161.6841 | 2565868.9556 | 1184178.6088
75 | 2565862.5344 | 1184161.6841 | 2565860.9767 | 1184157.5797 | 2565849.85 | 1184129.9508 | 2565843.2934 | 1184108.7262
76 | 2565868.9556 | 1184178.6088 | 2565874.5424 | 1184193.3342
77 | 2565878.0502 | 1184202.5799 | 2565874.5424 | 1184193.3342
78 | 2565878.0502 | 1184202.5799 | 2565879.5373 | 1184206.4996 | 2565883.4407 | 1184219.687
79 | 2565885.0413 | 1184233.3631 | 2565885.8807 | 1184227.9304 | 2565883.4407 | 1184219.687
80 | 2565877.9426 | 1184252.0107 | 2565883.8417 | 1184241.1268 | 2565885.0413 | 1184233.3631
81 | 2565877.9426 | 1184252.0107 | 2565871.2551 | 1184262.5211 | 2565867.0127 | 1184278.7985 | 2565867.6513 | 1184290.2066
82 | 2565867.6513 | 1184290.2066 | 2565868.6364 | 1184307.8046 | 2565864.8589 | 1184318.6319 | 2565860.8141 | 1184320.9608
83 | 2565838.5561 | 1184333.776 | 2565860.8141 | 1184320.9608
84 | 2565771.3635 | 1184289.9504 | 2565770.4742 | 1184288.5448 | 2565768.5782 | 1184286.0985
85 | 2565768.5782 | 1184286.0985 | 2565755.8407 | 1184269.6637
86 | 2565755.8407 | 1184269.6637 | 2565747.0087 | 1184258.268
87 | 2565747.0087 | 1184258.268 | 2565746.3359 | 1184257.3999 | 2565720.9653 | 1184224.6728
88 | 2565720.9653 | 1184224.6728 | 2565713.2002 | 1184214.6562 | 2565708.4514 | 1184207.8243 | 2565700.0219 | 1184195.6919
89 | 2565700.0219 | 1184195.6919 | 2565696.632 | 1184190.8129
90 | 2565696.632 | 1184190.8129 | 2565694.7445 | 1184188.0963
91 | 2565686.3699 | 1184141.0492 | 2565682.8595 | 1184113.8544
92 | 2565687.7235 | 1183956.8184 | 2565688.5716 | 1183946.8109 | 2565687.1653 | 1183931.9
93 | 2565682.4395 | 1183909.7088 | 2565687.1653 | 1183931.9 | 2565687.1653 | 1183931.9
94 | 2565682.4395 | 1183909.7088 | 2565641.0462 | 1183739.7852
95 | 2565641.0462 | 1183739.7852 | 2565650.4623 | 1183696.2359
96 | 2565641.0462 | 1183739.7852 | 2565600.1619 | 1183726.0432
97 | 2565650.4623 | 1183696.2359 | 2565652.3263 | 1183687.6149 | 2565658.4181 | 1183672.0367
98 | 2565703.0294 | 1183509.0003 | 2565658.4181 | 1183672.0367
99 | 2565705.9032 | 1183487.5456 | 2565703.0294 | 1183509.0003
100 | 2565705.9032 | 1183487.5456 | 2565709.4967 | 1183472.5614 | 2565714.8753 | 1183440.0578
101 | 2565705.9032 | 1183487.5456 | 2565698.5088 | 1183484.0528 | 2565698.5088 | 1183484.0528
102 | 2565770.7874 | 1183501.492 | 2565763.6292 | 1183485.9248 | 2565745.9305 | 1183469.3841 | 2565721.2918 | 1183440.7547 | 2565714.8753 | 1183440.0578
103 | 2565719.5089 | 1183412.0941 | 2565714.8753 | 1183440.0578
104 | 2565694.0158 | 1183469.1698 | 2565694.6339 | 1183472.6357 | 2565698.5088 | 1183484.0528
105 | 2565770.7874 | 1183501.492 | 2566010.1134 | 1183489.8943
106 | 2565719.5089 | 1183412.0941 | 2565719.9113 | 1183409.57
107 | 2565694.0158 | 1183469.1698 | 2565691.241 | 1183453.6105
108 | 2566010.1134 | 1183489.8943 | 2566016.6337 | 1183498.3175
109 | 2565719.9113 | 1183409.57 | 2565731.9037 | 1183334.3417
110 | 2565691.241 | 1183453.6105 | 2565688.862 | 1183440.2705
111 | 2565731.9037 | 1183334.3417 | 2565735.1824 | 1183313.7744 | 2565737.0507 | 1183293.4529 | 2565734.9632 | 1183275.5665 | 2565727.3499 | 1183256.6001 | 2565713.47 | 1183238.2952

## bus_geodata
| x | y | coords
0 | 2565948.3046 | 1184509.1548
1 | 2565941.878 | 1184487.0714
2 | 2565947.2129 | 1184521.2918
3 | 2566103.8479 | 1184488.8505
4 | 2565946.9967 | 1184523.5387
5 | 2566131.9159 | 1184448.9813
6 | 2566147.8865 | 1184406.446
7 | 2566115.5732 | 1184388.264
8 | 2565935.0957 | 1184536.5084
9 | 2565928.9256 | 1184538.7609
10 | 2565907.4231 | 1184531.8021
11 | 2565890.6561 | 1184558.8344
12 | 2565882.0993 | 1184519.9707
13 | 2565864.7416 | 1184531.511
14 | 2565763.3785 | 1184519.2286
15 | 2565789.1336 | 1184455.8633
16 | 2565794.3348 | 1184434.7588
17 | 2565798.9177 | 1184412.382
18 | 2565802.1906 | 1184383.2592
19 | 2565803.2667 | 1184352.8023
20 | 2565785.9514 | 1184353.9419
21 | 2565775.7404 | 1184296.8678
22 | 2565822.4316 | 1184343.1741
23 | 2565976.9517 | 1184255.1033
24 | 2565888.9802 | 1184255.3799
25 | 2565289.2817 | 1184549.0517
26 | 2565336.1792 | 1184484.6862
27 | 2565263.169 | 1184581.106
28 | 2565433.6386 | 1184434.2615
29 | 2565128.2194 | 1184312.1501
30 | 2565253.7682 | 1184572.4945
31 | 2565120.0353 | 1184310.8194
32 | 2565096.6634 | 1184304.974
33 | 2565242.0287 | 1184561.7409
34 | 2565091.7207 | 1184302.8723
35 | 2565023.5141 | 1184261.612
36 | 2564939.1822 | 1183890.5595
37 | 2565000.2762 | 1183864.3669
38 | 2564991.222 | 1183872.0802
39 | 2565105.2355 | 1183842.2585
40 | 2564971.7743 | 1183879.2785
41 | 2564676.3721 | 1183871.637
42 | 2565533.6014 | 1184046.5487
43 | 2565511.1606 | 1184027.226
44 | 2565676.8712 | 1184068.4452
45 | 2565509.4113 | 1184025.656
46 | 2565677.5542 | 1184027.511
47 | 2565678.8389 | 1184083.4301
48 | 2565506.1269 | 1184022.7081
49 | 2565680.1875 | 1184010.156
50 | 2565492.8508 | 1184010.7926
51 | 2565662.1968 | 1184146.2893
52 | 2565663.4144 | 1184147.8241
53 | 2565677.2074 | 1184165.2103
54 | 2565690.3797 | 1184181.8142
55 | 2565481.5602 | 1183999.4752
56 | 2565467.2416 | 1183983.4688
57 | 2565453.3046 | 1183967.8888
58 | 2565687.5946 | 1183958.3395
59 | 2565134.8768 | 1183603.5879
60 | 2565700.4681 | 1184382.5564
61 | 2565719.6303 | 1184362.0805
62 | 2565586.8038 | 1184487.2982
63 | 2565724.1721 | 1184358.8917
64 | 2565907.0782 | 1184151.8579
65 | 2565893.5437 | 1184146.5506
66 | 2565900.1584 | 1184159.1457
67 | 2566165.1259 | 1184027.4265
68 | 2565879.7018 | 1184150.4812
69 | 2566172.1679 | 1184031.8726
70 | 2565862.5344 | 1184161.6841
71 | 2565868.9556 | 1184178.6088
72 | 2565843.2934 | 1184108.7262
73 | 2565874.5424 | 1184193.3342
74 | 2565878.0502 | 1184202.5799
75 | 2565883.4407 | 1184219.687
76 | 2565885.0413 | 1184233.3631
77 | 2565877.9426 | 1184252.0107
78 | 2565867.6513 | 1184290.2066
79 | 2565860.8141 | 1184320.9608
80 | 2565838.5561 | 1184333.776
81 | 2565771.3635 | 1184289.9504
82 | 2565768.5782 | 1184286.0985
83 | 2565755.8407 | 1184269.6637
84 | 2565747.0087 | 1184258.268
85 | 2565720.9653 | 1184224.6728
86 | 2565700.0219 | 1184195.6919
87 | 2565696.632 | 1184190.8129
88 | 2565694.7445 | 1184188.0963
89 | 2565686.3699 | 1184141.0492
90 | 2565682.8595 | 1184113.8544
91 | 2565687.7235 | 1183956.8184
92 | 2565687.1653 | 1183931.9
93 | 2565682.4395 | 1183909.7088
94 | 2565641.0462 | 1183739.7852
95 | 2565650.4623 | 1183696.2359
96 | 2565600.1619 | 1183726.0432
97 | 2565658.4181 | 1183672.0367
98 | 2565703.0294 | 1183509.0003
99 | 2565705.9032 | 1183487.5456
100 | 2565127.5722 | 1183584.8906
101 | 2565714.8753 | 1183440.0578
102 | 2565698.5088 | 1183484.0528
103 | 2565770.7874 | 1183501.492
104 | 2565719.5089 | 1183412.0941
105 | 2565694.0158 | 1183469.1698
106 | 2566010.1134 | 1183489.8943
107 | 2565719.9113 | 1183409.57
108 | 2565691.241 | 1183453.6105
109 | 2565688.862 | 1183440.2705
110 | 2565731.9037 | 1183334.3417
111 | 2565713.47 | 1183238.2952
112 | 2566016.6337 | 1183498.3175
113 | 2565720.9653 | 1184224.6728

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97374 | -0.18479 | 0.00088206 | 0.00022106
1 | 0.97366 | -0.18538 | 0.0024396 | 0.00061143
2 | 0.97404 | -0.18264 | 0 | 0
3 | 0.971 | -0.20447 | 0 | 0
4 | 0.97409 | -0.18228 | 0.00025436 | 6.3748e-05
5 | 0.9701 | -0.21098 | 0.011577 | 0.0029014
6 | 0.97008 | -0.21112 | 0 | 0
7 | 0.97007 | -0.21124 | 0.00028814 | 7.2216e-05
8 | 0.9745 | -0.17935 | 0.00067904 | 0.00017018
9 | 0.97465 | -0.17823 | 0 | 0
10 | 0.97521 | -0.17423 | 0 | 0
11 | 0.97517 | -0.17448 | 0.00073852 | 0.00018509
12 | 0.97608 | -0.16802 | 0.0015221 | 0.00038146
13 | 0.97664 | -0.164 | 0.00058173 | 0.0001458
14 | 0.98031 | -0.13784 | 0.00060421 | 0.00015143
15 | 0.98228 | -0.12387 | 0.00022532 | 5.6471e-05
16 | 0.98291 | -0.11941 | 0.0020163 | 0.00050533
17 | 0.98364 | -0.11425 | 0.0041376 | 0.001037
18 | 0.98476 | -0.10638 | 0.0052536 | 0.0013167
19 | 0.98614 | -0.096579 | 0 | 0
20 | 0.98582 | -0.098857 | 0.0029958 | 0.00075082
21 | 0.99359 | -0.04439 | 0.0020636 | 0.0005172
22 | 0.98499 | -0.10477 | 0.0026932 | 0.00067498
23 | 0.97951 | -0.1437 | 0.001567 | 0.00039272
24 | 0.97972 | -0.14222 | 0.0010007 | 0.0002508
25 | 0.97316 | -0.19085 | 0.00083825 | 0.00021008
26 | 0.97363 | -0.18747 | 0 | 0
27 | 0.97297 | -0.19223 | 0 | 0
28 | 0.97336 | -0.18942 | 0.001638 | 0.00041051
29 | 0.97586 | -0.17135 | 0.0015498 | 0.00038842
30 | 0.97291 | -0.19266 | 0.00067686 | 0.00016964
31 | 0.97595 | -0.17073 | 0.00083874 | 0.00021021
32 | 0.97623 | -0.16867 | 0.0007812 | 0.00019579
33 | 0.97285 | -0.19308 | 0.0024886 | 0.00062369
34 | 0.9763 | -0.16817 | 0.00089314 | 0.00022384
35 | 0.97744 | -0.15997 | 0 | 0
36 | 0.98284 | -0.1213 | 0.0005187 | 0.00013
37 | 0.98397 | -0.11323 | 0.00084249 | 0.00021115
38 | 0.98376 | -0.11476 | 0.00039211 | 9.8273e-05
39 | 0.98615 | -0.097731 | 0.001045 | 0.0002619
40 | 0.98339 | -0.11736 | 0.0010088 | 0.00025282
41 | 0.98257 | -0.12329 | 0.00072034 | 0.00018054
42 | 0.99163 | -0.058783 | 0.0011788 | 0.00029542
43 | 0.99119 | -0.061929 | 0.00085047 | 0.00021315
44 | 0.99393 | -0.042563 | 0.00060061 | 0.00015053
45 | 0.99115 | -0.062168 | 0.00079795 | 0.00019999
46 | 0.99266 | -0.05148 | 0.0016894 | 0.00042341
47 | 0.99441 | -0.039189 | 0.00022381 | 5.6093e-05
48 | 0.99109 | -0.0626 | 0.00078627 | 0.00019706
49 | 0.99216 | -0.055 | 0.0003534 | 8.8569e-05
50 | 0.99086 | -0.064274 | 0.00030353 | 7.6072e-05
51 | 0.99754 | -0.017165 | 0.0015112 | 0.00037875
52 | 0.99755 | -0.017136 | 0.00051235 | 0.00012841
53 | 0.99761 | -0.016685 | 0.0012098 | 0.00030322
54 | 0.99771 | -0.015997 | 0 | 0
55 | 0.99065 | -0.065752 | 0.0020656 | 0.00051769
56 | 0.9904 | -0.06751 | 0.00092387 | 0.00023154
57 | 0.99017 | -0.069123 | 0 | 0
58 | 0.9907 | -0.065331 | 0.0019476 | 0.0004881
59 | 0.98591 | -0.099486 | 0.00027045 | 6.7781e-05
60 | 0.98478 | -0.10629 | 0.00067241 | 0.00016852
61 | 0.98487 | -0.10565 | 0.0045386 | 0.0011375
62 | 0.98444 | -0.10871 | 0.0015096 | 0.00037835
63 | 0.98492 | -0.10526 | 0.0030117 | 0.0007548
64 | 0.97664 | -0.16432 | 0.0015679 | 0.00039296
65 | 0.97675 | -0.16349 | 0.0015635 | 0.00039186
66 | 0.97662 | -0.16444 | 0.0010645 | 0.00026679
67 | 0.9756 | -0.17178 | 0.0019453 | 0.00048754
68 | 0.9769 | -0.16246 | 0.0024324 | 0.00060962
69 | 0.9756 | -0.17183 | 0.00052545 | 0.00013169
70 | 0.97717 | -0.1605 | 0 | 0
71 | 0.97746 | -0.15837 | 0.0018999 | 0.00047616
72 | 0.97699 | -0.16177 | 0.0021523 | 0.00053941
73 | 0.97777 | -0.1562 | 0.0051641 | 0.0012942
74 | 0.97803 | -0.1543 | 0.002965 | 0.00074311
75 | 0.97859 | -0.15031 | 0.0014543 | 0.00036449
76 | 0.97906 | -0.14697 | 0.0012175 | 0.00030514
77 | 0.97976 | -0.14191 | 0 | 0
78 | 0.98134 | -0.13068 | 0.0039963 | 0.0010016
79 | 0.98284 | -0.12 | 0.0019529 | 0.00048944
80 | 0.98405 | -0.11138 | 0.0018566 | 0.0004653
81 | 0.99458 | -0.037513 | 0.0010636 | 0.00026657
82 | 0.99487 | -0.035491 | 0.0018091 | 0.0004534
83 | 0.99617 | -0.026481 | 0.0031773 | 0.00079631
84 | 0.9971 | -0.020017 | 0.0048452 | 0.0012143
85 | 1 | 0 | -0.16016 | -0.04018
86 | 0.99838 | -0.011345 | 0.0041199 | 0.0010325
87 | 0.99812 | -0.01311 | 0.0062632 | 0.0015697
88 | 0.998 | -0.013989 | 0.00069775 | 0.00017487
89 | 0.99627 | -0.026103 | 0.00411 | 0.0010301
90 | 0.99538 | -0.032314 | 0.00057265 | 0.00014352
91 | 0.99067 | -0.065602 | 0.003551 | 0.00088997
92 | 0.99017 | -0.069149 | 0.0020117 | 0.00050418
93 | 0.98978 | -0.071902 | 0.0010165 | 0.00025476
94 | 0.98705 | -0.09136 | 0 | 0
95 | 0.98639 | -0.096077 | 0.0019051 | 0.00047747
96 | 0.98701 | -0.091603 | 0.00054818 | 0.00013739
97 | 0.98608 | -0.098284 | 0.00093261 | 0.00023373
98 | 0.98427 | -0.11128 | 0.0006709 | 0.00016814
99 | 0.98405 | -0.1128 | 0 | 0
100 | 0.98589 | -0.099574 | 0.00042688 | 0.00010699
101 | 0.98378 | -0.11477 | 0 | 0
102 | 0.98402 | -0.11304 | 0.00092816 | 0.00023262
103 | 0.9836 | -0.11607 | 0.00048772 | 0.00012224
104 | 0.98368 | -0.11549 | 0 | 0
105 | 0.98398 | -0.11334 | 0.00050487 | 0.00012653
106 | 0.98327 | -0.11846 | 0.00041451 | 0.00010388
107 | 0.98367 | -0.11556 | 0.0011962 | 0.0002998
108 | 0.98395 | -0.11357 | 0.00022033 | 5.522e-05
109 | 0.98392 | -0.11373 | 0.0011785 | 0.00029537
110 | 0.98353 | -0.11656 | 0.00073981 | 0.00018541
111 | 0.98345 | -0.11712 | 0.00052342 | 0.00013118
112 | 0.98326 | -0.11852 | 0.00054165 | 0.00013575
113 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0024398 | 0.00061122 | -0.0024396 | -0.00061143 | 1.9954e-07 | -2.0938e-07 | 0.0037283 | 0.0037284 | 0.0037284 | 0.97374 | -0.18479 | 0.97366 | -0.18538 | 1.3809
1 | -0.01523 | -0.0038189 | 0.015235 | 0.0038205 | 4.5468e-06 | 1.5814e-06 | 0.023274 | 0.023274 | 0.023274 | 0.97374 | -0.18479 | 0.97404 | -0.18264 | 8.6202
2 | 0.011908 | 0.0029866 | -0.011876 | -0.0029761 | 3.2417e-05 | 1.0522e-05 | 0.018198 | 0.018199 | 0.018199 | 0.97374 | -0.18479 | 0.971 | -0.20447 | 6.7403
3 | -0.015235 | -0.0038205 | 0.015235 | 0.0038208 | 7.6299e-07 | 2.6536e-07 | 0.023274 | 0.023274 | 0.023274 | 0.97404 | -0.18264 | 0.97409 | -0.18228 | 8.6201
4 | 0.011876 | 0.0029761 | -0.011865 | -0.0029726 | 1.0693e-05 | 3.4734e-06 | 0.018199 | 0.018199 | 0.018199 | 0.971 | -0.20447 | 0.9701 | -0.21098 | 6.7404
5 | -0.01549 | -0.0038845 | 0.015496 | 0.0038867 | 6.2946e-06 | 2.1966e-06 | 0.023663 | 0.023663 | 0.023663 | 0.97409 | -0.18228 | 0.9745 | -0.17935 | 8.764
6 | 0.00028815 | 7.1197e-05 | -0.00028815 | -7.1761e-05 | 5.5853e-09 | -5.642e-07 | 0.00044163 | 0.00044183 | 0.00044183 | 0.9701 | -0.21098 | 0.97008 | -0.21112 | 0.16364
7 | 0.00028815 | 7.1761e-05 | -0.00028814 | -7.2216e-05 | 4.5086e-09 | -4.5505e-07 | 0.00044183 | 0.00044199 | 0.00044199 | 0.97008 | -0.21112 | 0.97007 | -0.21124 | 0.1637
8 | -0.016175 | -0.0040569 | 0.016178 | 0.0040578 | 2.5005e-06 | 8.7989e-07 | 0.0247 | 0.0247 | 0.0247 | 0.9745 | -0.17935 | 0.97465 | -0.17823 | 9.148
9 | -0.016178 | -0.0040578 | 0.016187 | 0.0040609 | 8.984e-06 | 3.1611e-06 | 0.0247 | 0.0247 | 0.0247 | 0.97465 | -0.17823 | 0.97521 | -0.17423 | 9.148
10 | 0.00073855 | 0.00018469 | -0.00073852 | -0.00018509 | 2.615e-08 | -4.0172e-07 | 0.0011268 | 0.0011269 | 0.0011269 | 0.97521 | -0.17423 | 0.97517 | -0.17448 | 0.41737
11 | -0.016925 | -0.0042456 | 0.01694 | 0.0042508 | 1.4587e-05 | 5.1727e-06 | 0.025826 | 0.025826 | 0.025826 | 0.97521 | -0.17423 | 0.97608 | -0.16802 | 9.5653
12 | -0.018462 | -0.0046323 | 0.018472 | 0.004636 | 1.0306e-05 | 3.7032e-06 | 0.028147 | 0.028146 | 0.028147 | 0.97608 | -0.16802 | 0.97664 | -0.164 | 10.4246
13 | -0.019054 | -0.0047818 | 0.019123 | 0.0048068 | 6.9404e-05 | 2.5036e-05 | 0.029033 | 0.029032 | 0.029033 | 0.97664 | -0.164 | 0.98031 | -0.13784 | 10.7529
14 | -0.019727 | -0.0049582 | 0.019766 | 0.0049721 | 3.8463e-05 | 1.3925e-05 | 0.029949 | 0.029949 | 0.029949 | 0.98031 | -0.13784 | 0.98228 | -0.12387 | 11.0923
15 | -0.019991 | -0.0050286 | 0.020004 | 0.0050331 | 1.2444e-05 | 4.5109e-06 | 0.03029 | 0.03029 | 0.03029 | 0.98228 | -0.12387 | 0.98291 | -0.11941 | 11.2186
16 | -0.02202 | -0.0055385 | 0.022036 | 0.0055443 | 1.5854e-05 | 5.8078e-06 | 0.033343 | 0.033343 | 0.033343 | 0.98291 | -0.11941 | 0.98364 | -0.11425 | 12.3491
17 | -0.026173 | -0.0065812 | 0.026202 | 0.0065919 | 2.8729e-05 | 1.0676e-05 | 0.039602 | 0.039602 | 0.039602 | 0.98364 | -0.11425 | 0.98476 | -0.10638 | 14.6673
18 | -0.031456 | -0.0079086 | 0.031499 | 0.0079248 | 4.2995e-05 | 1.6148e-05 | 0.04754 | 0.04754 | 0.04754 | 0.98476 | -0.10638 | 0.98614 | -0.096579 | 17.6075
19 | 0.012742 | 0.0031918 | -0.012738 | -0.0031905 | 4.013e-06 | 1.3216e-06 | 0.019226 | 0.019226 | 0.019226 | 0.98614 | -0.096579 | 0.98582 | -0.098857 | 7.1207
20 | -0.081518 | -0.020484 | 0.082115 | 0.020713 | 0.00059653 | 0.00022862 | 0.12302 | 0.12302 | 0.12302 | 0.98614 | -0.096579 | 0.99359 | -0.04439 | 45.5644
21 | 0.037278 | 0.0093679 | -0.037235 | -0.0093518 | 4.2451e-05 | 1.6053e-05 | 0.056258 | 0.056258 | 0.056258 | 0.98614 | -0.096579 | 0.98499 | -0.10477 | 20.8364
22 | 0.009742 | 0.0024397 | -0.0097334 | -0.0024372 | 8.6206e-06 | 2.5017e-06 | 0.014704 | 0.014704 | 0.014704 | 0.98582 | -0.098857 | 0.98492 | -0.10526 | 5.4461
23 | -0.084178 | -0.02123 | 0.08426 | 0.021261 | 8.1241e-05 | 3.114e-05 | 0.12611 | 0.12611 | 0.12611 | 0.99359 | -0.04439 | 0.99458 | -0.037513 | 46.709
24 | 0.034542 | 0.0086768 | -0.03451 | -0.0086649 | 3.1721e-05 | 1.1963e-05 | 0.05219 | 0.05219 | 0.05219 | 0.98499 | -0.10477 | 0.98405 | -0.11138 | 19.3295
25 | -0.001567 | -0.00039272 | 0.0015673 | 0.00039171 | 3.1901e-07 | -1.0133e-06 | 0.0023805 | 0.0023801 | 0.0023805 | 0.97951 | -0.1437 | 0.97972 | -0.14222 | 0.88165
26 | -0.002568 | -0.00064251 | 0.0025681 | 0.0006424 | 1.0952e-07 | -1.032e-07 | 0.0038999 | 0.0038999 | 0.0038999 | 0.97972 | -0.14222 | 0.97976 | -0.14191 | 1.4444
27 | -0.0040046 | -0.0010029 | 0.0040065 | 0.0010026 | 1.8689e-06 | -2.7428e-07 | 0.006123 | 0.0061226 | 0.006123 | 0.97316 | -0.19085 | 0.97363 | -0.18747 | 2.2678
28 | 0.0031664 | 0.00079282 | -0.0031658 | -0.0007931 | 6.0469e-07 | -2.8101e-07 | 0.0048413 | 0.0048415 | 0.0048415 | 0.97316 | -0.19085 | 0.97297 | -0.19223 | 1.7931
29 | 0.0016384 | 0.00040929 | -0.001638 | -0.00041051 | 4.3967e-07 | -1.2283e-06 | 0.0025035 | 0.002504 | 0.002504 | 0.97363 | -0.18747 | 0.97336 | -0.18942 | 0.92742
30 | -0.0056449 | -0.0014119 | 0.0056574 | 0.0014134 | 1.2545e-05 | 1.4568e-06 | 0.0086262 | 0.008625 | 0.0086262 | 0.97363 | -0.18747 | 0.97586 | -0.17135 | 3.1949
31 | 0.0031658 | 0.0007931 | -0.0031656 | -0.00079319 | 1.8647e-07 | -8.6606e-08 | 0.0048415 | 0.0048415 | 0.0048415 | 0.97297 | -0.19223 | 0.97291 | -0.19266 | 1.7932
32 | -0.0072072 | -0.0018018 | 0.0072078 | 0.0018019 | 6.247e-07 | 1.3667e-07 | 0.010988 | 0.010988 | 0.010988 | 0.97586 | -0.17135 | 0.97595 | -0.17073 | 4.0697
33 | 0.0024887 | 0.00062355 | -0.0024886 | -0.00062369 | 1.4393e-07 | -1.4233e-07 | 0.0038063 | 0.0038064 | 0.0038064 | 0.97291 | -0.19266 | 0.97285 | -0.19308 | 1.4098
34 | -0.0080466 | -0.0020121 | 0.0080489 | 0.0020127 | 2.2771e-06 | 5.7269e-07 | 0.012267 | 0.012267 | 0.012267 | 0.97595 | -0.17073 | 0.97623 | -0.16867 | 4.5433
35 | -0.0088301 | -0.0022085 | 0.0088307 | 0.0022087 | 6.0697e-07 | 1.6629e-07 | 0.013458 | 0.013458 | 0.013458 | 0.97623 | -0.16867 | 0.9763 | -0.16817 | 4.9843
36 | -0.0097238 | -0.0024325 | 0.0097348 | 0.0024357 | 1.101e-05 | 3.2286e-06 | 0.014819 | 0.014818 | 0.014819 | 0.9763 | -0.16817 | 0.97744 | -0.15997 | 5.4884
37 | -0.0097348 | -0.0024357 | 0.009787 | 0.002451 | 5.2133e-05 | 1.5255e-05 | 0.014818 | 0.014817 | 0.014818 | 0.97744 | -0.15997 | 0.98284 | -0.1213 | 5.4883
38 | 0.00072054 | 0.00017727 | -0.00072034 | -0.00018054 | 1.9546e-07 | -3.2631e-06 | 0.0010897 | 0.0010909 | 0.0010909 | 0.98284 | -0.1213 | 0.98257 | -0.12329 | 0.40404
39 | -0.011026 | -0.0027583 | 0.011032 | 0.0027601 | 5.9961e-06 | 1.8689e-06 | 0.016692 | 0.016692 | 0.016692 | 0.98284 | -0.1213 | 0.98339 | -0.11736 | 6.1821
40 | 0.01244 | 0.0031135 | -0.012437 | -0.0031126 | 2.6263e-06 | 8.5907e-07 | 0.018811 | 0.018811 | 0.018811 | 0.98397 | -0.11323 | 0.98376 | -0.11476 | 6.967
41 | -0.013282 | -0.0033246 | 0.013311 | 0.0033341 | 2.8485e-05 | 9.5152e-06 | 0.020085 | 0.020084 | 0.020085 | 0.98397 | -0.11323 | 0.98615 | -0.097731 | 7.4389
42 | 0.012045 | 0.0030143 | -0.012041 | -0.0030129 | 4.3109e-06 | 1.3939e-06 | 0.018218 | 0.018218 | 0.018218 | 0.98376 | -0.11476 | 0.98339 | -0.11736 | 6.7474
43 | 0.0006975 | 0.00017151 | -0.00069733 | -0.00017451 | 1.6604e-07 | -3.0038e-06 | 0.0010513 | 0.0010524 | 0.0010524 | 0.98615 | -0.097731 | 0.98591 | -0.099486 | 0.38977
44 | -0.015053 | -0.0037675 | 0.015113 | 0.003781 | 5.955e-05 | 1.3423e-05 | 0.022713 | 0.022709 | 0.022713 | 0.98615 | -0.097731 | 0.99017 | -0.069123 | 4.206
45 | 0.020867 | 0.0052236 | -0.020858 | -0.0052209 | 9.0622e-06 | 2.7213e-06 | 0.03131 | 0.03131 | 0.03131 | 0.99163 | -0.058783 | 0.99119 | -0.061929 | 5.7982
46 | -0.022046 | -0.005519 | 0.022095 | 0.0055343 | 4.9477e-05 | 1.5282e-05 | 0.033079 | 0.033077 | 0.033079 | 0.99163 | -0.058783 | 0.99393 | -0.042563 | 6.1257
47 | 0.020007 | 0.0050077 | -0.020007 | -0.0050075 | 6.6152e-07 | 1.9384e-07 | 0.030033 | 0.030034 | 0.030034 | 0.99119 | -0.061929 | 0.99115 | -0.062168 | 5.5618
48 | 0.021493 | 0.0053877 | -0.021466 | -0.0053781 | 2.6512e-05 | 9.6657e-06 | 0.032177 | 0.032177 | 0.032177 | 0.99393 | -0.042563 | 0.99266 | -0.05148 | 11.9176
49 | -0.044188 | -0.011073 | 0.044209 | 0.01108 | 2.064e-05 | 7.5466e-06 | 0.066154 | 0.066154 | 0.066154 | 0.99393 | -0.042563 | 0.99441 | -0.039189 | 12.2507
50 | 0.019209 | 0.0048075 | -0.019208 | -0.0048072 | 1.1449e-06 | 3.266e-07 | 0.028836 | 0.028836 | 0.028836 | 0.99115 | -0.062168 | 0.99109 | -0.0626 | 5.3399
51 | 0.019777 | 0.0049546 | -0.019767 | -0.0049512 | 9.6262e-06 | 3.4756e-06 | 0.029645 | 0.029645 | 0.029645 | 0.99266 | -0.05148 | 0.99216 | -0.055 | 10.9796
52 | -0.044433 | -0.011136 | 0.044475 | 0.011152 | 4.2328e-05 | 1.5483e-05 | 0.066489 | 0.066488 | 0.066489 | 0.99441 | -0.039189 | 0.99538 | -0.032314 | 12.3127
53 | 0.018421 | 0.0046102 | -0.018417 | -0.004609 | 4.2568e-06 | 1.1776e-06 | 0.027655 | 0.027655 | 0.027655 | 0.99109 | -0.0626 | 0.99086 | -0.064274 | 5.1213
54 | 0.019414 | 0.0048626 | -0.019386 | -0.0048526 | 2.7696e-05 | 9.977e-06 | 0.029115 | 0.029115 | 0.029115 | 0.99216 | -0.055 | 0.9907 | -0.065331 | 10.7834
55 | 0.018113 | 0.0045329 | -0.01811 | -0.0045319 | 3.6955e-06 | 1.009e-06 | 0.027199 | 0.0272 | 0.0272 | 0.99086 | -0.064274 | 0.99065 | -0.065752 | 5.037
56 | -0.0015112 | -0.00037875 | 0.0015112 | 0.00037872 | 6.212e-09 | -2.3186e-08 | 0.0022543 | 0.0022542 | 0.0022543 | 0.99754 | -0.017165 | 0.99755 | -0.017136 | 0.83491
57 | -0.0020236 | -0.00050713 | 0.0020237 | 0.00050689 | 1.2617e-07 | -2.4122e-07 | 0.0030185 | 0.0030184 | 0.0030185 | 0.99755 | -0.017136 | 0.99761 | -0.016685 | 1.118
58 | -0.0032335 | -0.00081011 | 0.0032339 | 0.00080995 | 3.0763e-07 | -1.5844e-07 | 0.004823 | 0.0048229 | 0.004823 | 0.99761 | -0.016685 | 0.99771 | -0.015997 | 1.7863
59 | 0.049266 | 0.012365 | -0.049197 | -0.012339 | 6.9031e-05 | 2.5482e-05 | 0.073482 | 0.073483 | 0.073483 | 0.99771 | -0.015997 | 0.99627 | -0.026103 | 13.6079
60 | -0.052499 | -0.013175 | 0.052514 | 0.01318 | 1.4634e-05 | 5.4288e-06 | 0.078305 | 0.078305 | 0.078305 | 0.99771 | -0.015997 | 0.998 | -0.013989 | 14.501
61 | 0.016044 | 0.0040142 | -0.01604 | -0.0040133 | 3.8908e-06 | 9.4358e-07 | 0.024097 | 0.024097 | 0.024097 | 0.99065 | -0.065752 | 0.9904 | -0.06751 | 4.4624
62 | 0.015116 | 0.0037817 | -0.015113 | -0.003781 | 3.3634e-06 | 7.5575e-07 | 0.022709 | 0.022709 | 0.022709 | 0.9904 | -0.06751 | 0.99017 | -0.069123 | 4.2054
63 | 0.017438 | 0.0043645 | -0.017438 | -0.0043643 | 6.5339e-07 | 2.3165e-07 | 0.02619 | 0.02619 | 0.02619 | 0.9907 | -0.065331 | 0.99067 | -0.065602 | 9.7
64 | 0.00042688 | 0.00010673 | -0.00042688 | -0.00010699 | 5.1989e-09 | -2.5398e-07 | 0.0006442 | 0.00064429 | 0.00064429 | 0.98591 | -0.099486 | 0.98589 | -0.099574 | 0.23863
65 | -0.0021825 | -0.0005451 | 0.0021827 | 0.00054481 | 1.9326e-07 | -2.8818e-07 | 0.0032972 | 0.0032971 | 0.0032972 | 0.98478 | -0.10629 | 0.98487 | -0.10565 | 1.2212
66 | 0.0015101 | 0.00037658 | -0.0015096 | -0.00037835 | 5.0205e-07 | -1.7728e-06 | 0.0022812 | 0.0022819 | 0.0022819 | 0.98478 | -0.10629 | 0.98444 | -0.10871 | 0.84514
67 | -0.0067213 | -0.0016823 | 0.0067217 | 0.0016824 | 3.5706e-07 | 6.6707e-08 | 0.010154 | 0.010154 | 0.010154 | 0.98487 | -0.10565 | 0.98492 | -0.10526 | 3.7609
68 | -0.0051058 | -0.0012762 | 0.0051064 | 0.0012762 | 5.8494e-07 | 3.1058e-08 | 0.007778 | 0.0077779 | 0.007778 | 0.97664 | -0.16432 | 0.97675 | -0.16349 | 2.8807
69 | 0.0010645 | 0.00026667 | -0.0010645 | -0.00026679 | 1.7146e-08 | -1.2411e-07 | 0.0016219 | 0.0016219 | 0.0016219 | 0.97664 | -0.16432 | 0.97662 | -0.16444 | 0.60072
70 | 0.0024733 | 0.00061653 | -0.0024708 | -0.00061913 | 2.5378e-06 | -2.605e-06 | 0.0037672 | 0.0037685 | 0.0037685 | 0.97664 | -0.16432 | 0.9756 | -0.17178 | 1.3957
71 | -0.0066699 | -0.001668 | 0.0066709 | 0.0016682 | 9.4876e-07 | 1.8052e-07 | 0.01016 | 0.01016 | 0.01016 | 0.97675 | -0.16349 | 0.9769 | -0.16246 | 3.7629
72 | 0.00052546 | 0.00013159 | -0.00052545 | -0.00013169 | 3.3378e-09 | -1.0271e-07 | 0.0008014 | 0.00080144 | 0.00080144 | 0.9756 | -0.17178 | 0.9756 | -0.17183 | 0.29683
73 | -0.0091033 | -0.0022778 | 0.0091057 | 0.0022785 | 2.4593e-06 | 6.8912e-07 | 0.013865 | 0.013865 | 0.013865 | 0.9769 | -0.16246 | 0.97717 | -0.1605 | 5.1351
74 | -0.011258 | -0.0028174 | 0.011262 | 0.0028184 | 3.3194e-06 | 1.0499e-06 | 0.017143 | 0.017142 | 0.017143 | 0.97717 | -0.1605 | 0.97746 | -0.15837 | 6.3491
75 | 0.0021526 | 0.00053885 | -0.0021523 | -0.00053941 | 3.7807e-07 | -5.6085e-07 | 0.0032778 | 0.003278 | 0.003278 | 0.97717 | -0.1605 | 0.97699 | -0.16177 | 1.2141
76 | -0.013162 | -0.0032946 | 0.013166 | 0.0032959 | 3.9448e-06 | 1.3197e-06 | 0.020035 | 0.020035 | 0.020035 | 0.97746 | -0.15837 | 0.97777 | -0.1562 | 7.4203
77 | -0.01833 | -0.0045902 | 0.018334 | 0.0045919 | 4.8011e-06 | 1.7225e-06 | 0.027894 | 0.027894 | 0.027894 | 0.97777 | -0.1562 | 0.97803 | -0.1543 | 10.331
78 | -0.021299 | -0.005335 | 0.021311 | 0.0053393 | 1.1758e-05 | 4.2971e-06 | 0.032405 | 0.032405 | 0.032405 | 0.97803 | -0.1543 | 0.97859 | -0.15031 | 12.0018
79 | -0.022766 | -0.0057038 | 0.022776 | 0.0057077 | 1.0538e-05 | 3.8761e-06 | 0.034616 | 0.034616 | 0.034616 | 0.97859 | -0.15031 | 0.97906 | -0.14697 | 12.8208
80 | -0.023994 | -0.0060128 | 0.02401 | 0.006019 | 1.6791e-05 | 6.2036e-06 | 0.036466 | 0.036466 | 0.036466 | 0.97906 | -0.14697 | 0.97976 | -0.14191 | 13.5061
81 | -0.026579 | -0.0066614 | 0.02662 | 0.0066768 | 4.1387e-05 | 1.5405e-05 | 0.040366 | 0.040366 | 0.040366 | 0.97976 | -0.14191 | 0.98134 | -0.13068 | 14.9505
82 | -0.030616 | -0.0076784 | 0.030662 | 0.0076954 | 4.5405e-05 | 1.7036e-05 | 0.046426 | 0.046426 | 0.046426 | 0.98134 | -0.13068 | 0.98284 | -0.12 | 17.1947
83 | -0.032615 | -0.0081849 | 0.032654 | 0.0081996 | 3.9083e-05 | 1.4706e-05 | 0.049382 | 0.049382 | 0.049382 | 0.98284 | -0.12 | 0.98405 | -0.11138 | 18.2898
84 | -0.085323 | -0.021528 | 0.085347 | 0.021537 | 2.4212e-05 | 9.1887e-06 | 0.12771 | 0.12771 | 0.12771 | 0.99458 | -0.037513 | 0.99487 | -0.035491 | 23.6492
85 | -0.087156 | -0.021991 | 0.087267 | 0.022032 | 0.00011033 | 4.1895e-05 | 0.13041 | 0.13041 | 0.13041 | 0.99487 | -0.035491 | 0.99617 | -0.026481 | 24.1502
86 | -0.090444 | -0.022829 | 0.090526 | 0.02286 | 8.2172e-05 | 3.1229e-05 | 0.13516 | 0.13516 | 0.13516 | 0.99617 | -0.026481 | 0.9971 | -0.020017 | 25.0291
87 | -0.095371 | -0.024074 | 0.09564 | 0.024177 | 0.00026888 | 0.0001023 | 0.14239 | 0.14239 | 0.14239 | 0.9971 | -0.020017 | 1 | 0 | 26.3681
88 | 0.063716 | 0.016003 | -0.063616 | -0.015965 | 0.00010034 | 3.7655e-05 | 0.094823 | 0.094823 | 0.094823 | 1 | 0 | 0.99838 | -0.011345 | 17.5599
89 | 0.059496 | 0.014933 | -0.059482 | -0.014927 | 1.4578e-05 | 5.4517e-06 | 0.088683 | 0.088683 | 0.088683 | 0.99838 | -0.011345 | 0.99812 | -0.01311 | 16.4228
90 | 0.053218 | 0.013358 | -0.053212 | -0.013355 | 6.4976e-06 | 2.4126e-06 | 0.079346 | 0.079346 | 0.079346 | 0.99812 | -0.01311 | 0.998 | -0.013989 | 14.6936
91 | 0.045087 | 0.011309 | -0.045048 | -0.011295 | 3.88e-05 | 1.421e-05 | 0.067344 | 0.067344 | 0.067344 | 0.99627 | -0.026103 | 0.99538 | -0.032314 | 12.4712
92 | 0.013887 | 0.0034743 | -0.01388 | -0.003472 | 6.7914e-06 | 2.2901e-06 | 0.020856 | 0.020856 | 0.020856 | 0.99067 | -0.065602 | 0.99017 | -0.069149 | 7.7246
93 | 0.011868 | 0.0029679 | -0.011864 | -0.0029664 | 4.5026e-06 | 1.44e-06 | 0.017833 | 0.017833 | 0.017833 | 0.99017 | -0.069149 | 0.98978 | -0.071902 | 6.6049
94 | 0.010847 | 0.0027117 | -0.010818 | -0.0027027 | 2.9015e-05 | 8.9181e-06 | 0.016305 | 0.016306 | 0.016306 | 0.98978 | -0.071902 | 0.98705 | -0.09136 | 6.0392
95 | 0.01027 | 0.0025659 | -0.010263 | -0.0025639 | 6.6622e-06 | 1.9933e-06 | 0.01548 | 0.01548 | 0.01548 | 0.98705 | -0.09136 | 0.98639 | -0.096077 | 5.7333
96 | 0.0005482 | 0.00013684 | -0.00054818 | -0.00013739 | 1.8378e-08 | -5.4421e-07 | 0.00082624 | 0.00082643 | 0.00082643 | 0.98705 | -0.09136 | 0.98701 | -0.091603 | 0.30609
97 | 0.0083582 | 0.0020864 | -0.0083557 | -0.0020858 | 2.5332e-06 | 6.4833e-07 | 0.012606 | 0.012606 | 0.012606 | 0.98639 | -0.096077 | 0.98608 | -0.098284 | 4.6689
98 | 0.0074231 | 0.001852 | -0.0074099 | -0.0018491 | 1.3228e-05 | 2.9356e-06 | 0.011199 | 0.011199 | 0.011199 | 0.98608 | -0.098284 | 0.98427 | -0.11128 | 4.1479
99 | 0.006739 | 0.001681 | -0.0067376 | -0.0016807 | 1.4012e-06 | 2.6388e-07 | 0.010185 | 0.010185 | 0.010185 | 0.98427 | -0.11128 | 0.98405 | -0.1128 | 3.7723
100 | 0.0039054 | 0.00097154 | -0.0039044 | -0.00097175 | 1.0516e-06 | -2.0978e-07 | 0.0059029 | 0.0059031 | 0.0059031 | 0.98405 | -0.1128 | 0.98378 | -0.11477 | 2.1863
101 | 0.0028321 | 0.00070916 | -0.0028321 | -0.00070923 | 9.3581e-08 | -6.7897e-08 | 0.0042823 | 0.0042824 | 0.0042824 | 0.98405 | -0.1128 | 0.98402 | -0.11304 | 1.5861
102 | 0.0014445 | 0.00035783 | -0.0014442 | -0.00035882 | 2.5433e-07 | -9.8742e-07 | 0.0021833 | 0.0021837 | 0.0021837 | 0.98378 | -0.11477 | 0.9836 | -0.11607 | 0.80878
103 | 0.0024599 | 0.00061392 | -0.0024597 | -0.00061418 | 2.4478e-07 | -2.6577e-07 | 0.0037198 | 0.0037199 | 0.0037199 | 0.98378 | -0.11477 | 0.98368 | -0.11549 | 1.3778
104 | 0.0019039 | 0.00047661 | -0.0019038 | -0.00047678 | 8.056e-08 | -1.6689e-07 | 0.0028788 | 0.0028789 | 0.0028789 | 0.98402 | -0.11304 | 0.98398 | -0.11334 | 1.0663
105 | 0.00095648 | 0.00023658 | -0.00095617 | -0.0002395 | 3.128e-07 | -2.9199e-06 | 0.0014459 | 0.0014469 | 0.0014469 | 0.9836 | -0.11607 | 0.98327 | -0.11846 | 0.53591
106 | 0.0024597 | 0.00061418 | -0.0024597 | -0.00061421 | 2.2071e-08 | -2.3958e-08 | 0.0037199 | 0.00372 | 0.00372 | 0.98368 | -0.11549 | 0.98367 | -0.11556 | 1.3778
107 | 0.0013989 | 0.00035024 | -0.0013989 | -0.00035043 | 4.4135e-08 | -1.8377e-07 | 0.0021154 | 0.0021155 | 0.0021155 | 0.98398 | -0.11334 | 0.98395 | -0.11357 | 0.78351
108 | 0.00054166 | 0.00013562 | -0.00054165 | -0.00013575 | 4.4659e-09 | -1.3339e-07 | 0.00081966 | 0.00081971 | 0.00081971 | 0.98327 | -0.11846 | 0.98326 | -0.11852 | 0.3036
109 | 0.0012634 | 0.00031441 | -0.0012633 | -0.00031531 | 1.7352e-07 | -9.0016e-07 | 0.0019104 | 0.0019108 | 0.0019108 | 0.98367 | -0.11556 | 0.98353 | -0.11656 | 0.70769
110 | 0.0011786 | 0.00029521 | -0.0011785 | -0.00029537 | 2.686e-08 | -1.6178e-07 | 0.0017823 | 0.0017823 | 0.0017823 | 0.98395 | -0.11357 | 0.98392 | -0.11373 | 0.66013
111 | 0.00052346 | 0.00012989 | -0.00052342 | -0.00013118 | 4.0152e-08 | -1.2872e-06 | 0.0007915 | 0.00079196 | 0.00079196 | 0.98353 | -0.11656 | 0.98345 | -0.11712 | 0.29332

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16531 | 0.041472

## res_load
| p_mw | q_mvar
0 | 0.00088206 | 0.00022106
1 | 0.0024396 | 0.00061143
2 | 0.00025436 | 6.3748e-05
3 | 0.011577 | 0.0029014
4 | 0.00028814 | 7.2216e-05
5 | 0.00067904 | 0.00017018
6 | 0.00073852 | 0.00018509
7 | 0.0015221 | 0.00038146
8 | 0.00058173 | 0.0001458
9 | 0.00060421 | 0.00015143
10 | 0.00022532 | 5.6471e-05
11 | 0.0020163 | 0.00050533
12 | 0.0041376 | 0.001037
13 | 0.0052536 | 0.0013167
14 | 0.0029958 | 0.00075082
15 | 0.0020636 | 0.0005172
16 | 0.0026932 | 0.00067498
17 | 0.001567 | 0.00039272
18 | 0.0010007 | 0.0002508
19 | 0.00083825 | 0.00021008
20 | 0.001638 | 0.00041051
21 | 0.0015498 | 0.00038842
22 | 0.00067686 | 0.00016964
23 | 0.00083874 | 0.00021021
24 | 0.0007812 | 0.00019579
25 | 0.0024886 | 0.00062369
26 | 0.00089314 | 0.00022384
27 | 0.0005187 | 0.00013
28 | 0.00084249 | 0.00021115
29 | 0.00039211 | 9.8273e-05
30 | 0.001045 | 0.0002619
31 | 0.0010088 | 0.00025282
32 | 0.00072034 | 0.00018054
33 | 0.0011788 | 0.00029542
34 | 0.00085047 | 0.00021315
35 | 0.00060061 | 0.00015053
36 | 0.00079795 | 0.00019999
37 | 0.0016894 | 0.00042341
38 | 0.00022381 | 5.6093e-05
39 | 0.00078627 | 0.00019706
40 | 0.0003534 | 8.8569e-05
41 | 0.00030353 | 7.6072e-05
42 | 0.0015112 | 0.00037875
43 | 0.00051235 | 0.00012841
44 | 0.0012098 | 0.00030322
45 | 0.0020656 | 0.00051769
46 | 0.00092387 | 0.00023154
47 | 0.0019476 | 0.0004881
48 | 0.00027045 | 6.7781e-05
49 | 0.00067241 | 0.00016852
50 | 0.0045386 | 0.0011375
51 | 0.0015096 | 0.00037835
52 | 0.0030117 | 0.0007548
53 | 0.0015679 | 0.00039296
54 | 0.0015635 | 0.00039186
55 | 0.0010645 | 0.00026679
56 | 0.0019453 | 0.00048754
57 | 0.0024324 | 0.00060962
58 | 0.00052545 | 0.00013169
59 | 0.0018999 | 0.00047616
60 | 0.0021523 | 0.00053941
61 | 0.0051641 | 0.0012942
62 | 0.002965 | 0.00074311
63 | 0.0014543 | 0.00036449
64 | 0.0012175 | 0.00030514
65 | 0.0039963 | 0.0010016
66 | 0.0019529 | 0.00048944
67 | 0.0018566 | 0.0004653
68 | 0.0010636 | 0.00026657
69 | 0.0018091 | 0.0004534
70 | 0.0031773 | 0.00079631
71 | 0.0048452 | 0.0012143
72 | 0.0051567 | 0.0012924
73 | 0.0041199 | 0.0010325
74 | 0.0062632 | 0.0015697
75 | 0.00069775 | 0.00017487
76 | 0.00411 | 0.0010301
77 | 0.00057265 | 0.00014352
78 | 0.003551 | 0.00088997
79 | 0.0020117 | 0.00050418
80 | 0.0010165 | 0.00025476
81 | 0.0019051 | 0.00047747
82 | 0.00054818 | 0.00013739
83 | 0.00093261 | 0.00023373
84 | 0.0006709 | 0.00016814
85 | 0.00042688 | 0.00010699
86 | 0.00092816 | 0.00023262
87 | 0.00048772 | 0.00012224
88 | 0.00050487 | 0.00012653
89 | 0.00041451 | 0.00010388
90 | 0.0011962 | 0.0002998
91 | 0.00022033 | 5.522e-05
92 | 0.0011785 | 0.00029537
93 | 0.00073981 | 0.00018541
94 | 0.00052342 | 0.00013118
95 | 0.00054165 | 0.00013575

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1