## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2029-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2029-2_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2029-2_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2029-2_0_3_node_72 | 0.4 | n |  | TRUE
4 | bus_LV_2029-2_0_3_node_70 | 0.4 | n |  | TRUE
5 | bus_LV_2029-2_0_3_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_2029-2_0_3_node_42 | 0.4 | n |  | TRUE
7 | bus_LV_2029-2_0_3_node_39 | 0.4 | n |  | TRUE
8 | bus_LV_2029-2_0_3_node_46 | 0.4 | n |  | TRUE
9 | bus_LV_2029-2_0_3_node_45 | 0.4 | n |  | TRUE
10 | bus_LV_2029-2_0_3_node_52 | 0.4 | n |  | TRUE
11 | bus_LV_2029-2_0_3_node_51 | 0.4 | n |  | TRUE
12 | bus_LV_2029-2_0_3_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_2029-2_0_3_node_49 | 0.4 | n |  | TRUE
14 | bus_LV_2029-2_0_3_node_50 | 0.4 | n |  | TRUE
15 | bus_LV_2029-2_0_3_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_2029-2_0_3_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_2029-2_0_3_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_2029-2_0_3_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_2029-2_0_3_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_2029-2_0_3_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_2029-2_0_3_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_2029-2_0_3_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_2029-2_0_3_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_2029-2_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_2029-2_0_3_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_2029-2_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_2029-2_0_3_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_2029-2_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_2029-2_0_3_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_2029-2_0_3_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_2029-2_0_3_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_2029-2_0_3_node_67 | 0.4 | n |  | TRUE
33 | bus_LV_2029-2_0_3_node_66 | 0.4 | n |  | TRUE
34 | bus_LV_2029-2_0_3_node_68 | 0.4 | n |  | TRUE
35 | bus_LV_2029-2_0_3_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_2029-2_0_3_node_43 | 0.4 | n |  | TRUE
37 | bus_LV_2029-2_0_3_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_2029-2_0_3_node_41 | 0.4 | n |  | TRUE
39 | bus_LV_2029-2_0_3_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_2029-2_0_3_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_2029-2_0_3_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_2029-2_0_3_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_2029-2_0_3_node_61 | 0.4 | n |  | TRUE
44 | bus_LV_2029-2_0_3_node_62 | 0.4 | n |  | TRUE
45 | bus_LV_2029-2_0_3_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_2029-2_0_3_node_80 | 0.4 | n |  | TRUE
47 | bus_LV_2029-2_0_3_node_55 | 0.4 | n |  | TRUE
48 | bus_LV_2029-2_0_3_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_2029-2_0_3_node_64 | 0.4 | n |  | TRUE
50 | bus_LV_2029-2_0_3_node_79 | 0.4 | n |  | TRUE
51 | bus_LV_2029-2_0_3_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_2029-2_0_3_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_2029-2_0_3_node_76 | 0.4 | n |  | TRUE
54 | bus_LV_2029-2_0_3_node_78 | 0.4 | n |  | TRUE
55 | bus_LV_2029-2_0_3_node_75 | 0.4 | n |  | TRUE
56 | bus_LV_2029-2_0_3_node_77 | 0.4 | n |  | TRUE
57 | bus_LV_2029-2_0_3_node_56 | 0.4 | n |  | TRUE
58 | bus_LV_2029-2_0_3_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_2029-2_0_3_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_2029-2_0_3_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_2029-2_0_3_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_2029-2_0_3_node_60 | 0.4 | n |  | TRUE
63 | bus_LV_2029-2_0_3_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_2029-2_0_3_node_69 | 0.4 | n |  | TRUE
65 | bus_LV_2029-2_0_3_node_71 | 0.4 | n |  | TRUE
66 | bus_LV_2029-2_0_3_node_73 | 0.4 | n |  | TRUE
67 | bus_LV_2029-2_0_3_node_74 | 0.4 | n |  | TRUE
68 | bus_MV_477_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2029-2_0_3_load_0 | 0 | 0.0035894 | 0.00089958 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2029-2_0_3_load_3 | 2 | 0.0010743 | 0.00026924 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2029-2_0_3_load_72 | 3 | 0.0071502 | 0.001792 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2029-2_0_3_load_70 | 4 | 0.0035015 | 0.00087756 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2029-2_0_3_load_39 | 7 | 0.00082421 | 0.00020657 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2029-2_0_3_load_46 | 8 | 0.0024869 | 0.00062328 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2029-2_0_3_load_45 | 9 | 0.001795 | 0.00044987 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2029-2_0_3_load_51 | 11 | 0.0008908 | 0.00022325 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2029-2_0_3_load_16 | 12 | 0.00047362 | 0.0001187 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2029-2_0_3_load_49 | 13 | 0.0032404 | 0.00081213 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2029-2_0_3_load_50 | 14 | 0.00013648 | 3.4205e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2029-2_0_3_load_17 | 15 | 0.0023722 | 0.00059454 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2029-2_0_3_load_18 | 16 | 0.00080144 | 0.00020086 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2029-2_0_3_load_19 | 17 | 0.0021557 | 0.00054027 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2029-2_0_3_load_20 | 18 | 0.010217 | 0.0025606 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2029-2_0_3_load_21 | 19 | 0.002889 | 0.00072404 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2029-2_0_3_load_22 | 20 | 0.0038867 | 0.00097409 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2029-2_0_3_load_24 | 22 | 0.0014115 | 0.00035375 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2029-2_0_3_load_25 | 23 | 0.0043651 | 0.001094 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2029-2_0_3_load_30 | 25 | 0.001247 | 0.00031252 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2029-2_0_3_load_27 | 26 | 0.0004052 | 0.00010155 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2029-2_0_3_load_28 | 28 | 0.037921 | 0.009504 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2029-2_0_3_load_29 | 29 | 0.063786 | 0.015986 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2029-2_0_3_load_36 | 31 | 0.001212 | 0.00030375 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2029-2_0_3_load_67 | 32 | 0.0014104 | 0.00035347 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2029-2_0_3_load_66 | 33 | 0.0016367 | 0.00041021 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2029-2_0_3_load_68 | 34 | 0.0026494 | 0.00066399 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2029-2_0_3_load_34 | 35 | 0.0028371 | 0.00071105 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2029-2_0_3_load_63 | 37 | 0.0023683 | 0.00059356 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2029-2_0_3_load_33 | 39 | 0.0013475 | 0.00033771 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2029-2_0_3_load_37 | 41 | 0.00034175 | 8.5651e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2029-2_0_3_load_38 | 42 | 0.0026027 | 0.0006523 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2029-2_0_3_load_61 | 43 | 0.00039174 | 9.8179e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2029-2_0_3_load_62 | 44 | 0.00037282 | 9.3437e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2029-2_0_3_load_44 | 45 | 0.0054536 | 0.0013668 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2029-2_0_3_load_80 | 46 | 0.00061192 | 0.00015336 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2029-2_0_3_load_55 | 47 | 0.00055817 | 0.00013989 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2029-2_0_3_load_53 | 48 | 0.00038816 | 9.7283e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2029-2_0_3_load_64 | 49 | 0.0021335 | 0.00053471 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2029-2_0_3_load_79 | 50 | 0.00046517 | 0.00011658 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2029-2_0_3_load_47 | 51 | 0.0013442 | 0.00033688 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2029-2_0_3_load_48 | 52 | 0.0015428 | 0.00038667 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2029-2_0_3_load_76 | 53 | 0.00061958 | 0.00015528 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2029-2_0_3_load_78 | 54 | 0.0016706 | 0.0004187 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2029-2_0_3_load_75 | 55 | 0.0010299 | 0.00025811 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2029-2_0_3_load_77 | 56 | 0.00055591 | 0.00013932 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2029-2_0_3_load_56 | 57 | 0.00040441 | 0.00010136 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2029-2_0_3_load_54 | 58 | 0.00028497 | 7.1421e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2029-2_0_3_load_57 | 59 | 0.00046473 | 0.00011647 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2029-2_0_3_load_58 | 60 | 0.00042091 | 0.00010549 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2029-2_0_3_load_59 | 61 | 0.00033902 | 8.4967e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2029-2_0_3_load_60 | 62 | 0.00040822 | 0.00010231 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2029-2_0_3_load_65 | 63 | 0.0050691 | 0.0012704 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2029-2_0_3_load_71 | 65 | 0.0040822 | 0.0010231 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2029-2_0_3_load_74 | 67 | 0.001413 | 0.00035412 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2029-2_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.036285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2029-2_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.050945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2029-2_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.038471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2029-2_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.0002541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2029-2_0_3_line_4 | NAYY 4x150 SE | 4 | 64 | 0.021957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2029-2_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.007707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2029-2_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.059281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2029-2_0_3_line_7 | NAYY 4x150 SE | 6 | 10 | 0.045624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2029-2_0_3_line_8 | NAYY 4x150 SE | 6 | 11 | 0.082114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2029-2_0_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.064234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2029-2_0_3_line_10 | NAYY 4x150 SE | 9 | 45 | 0.0095382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_2029-2_0_3_line_11 | NAYY 4x150 SE | 10 | 47 | 0.023116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2029-2_0_3_line_12 | NAYY 4x150 SE | 10 | 48 | 0.014507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2029-2_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.018086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2029-2_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.30506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2029-2_0_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.024964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2029-2_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.045402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2029-2_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.010004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2029-2_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.006607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2029-2_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.026703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2029-2_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.0033319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2029-2_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.0062016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2029-2_0_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.051287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_2029-2_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.13274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_2029-2_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.025224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_2029-2_0_3_line_25 | NAYY 4x150 SE | 23 | 25 | 0.13265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_2029-2_0_3_line_26 | NAYY 4x150 SE | 24 | 26 | 0.012085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_2029-2_0_3_line_27 | NAYY 4x150 SE | 25 | 27 | 0.043968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_2029-2_0_3_line_28 | NAYY 4x150 SE | 26 | 28 | 0.032802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_2029-2_0_3_line_29 | NAYY 4x150 SE | 27 | 32 | 0.036863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_2029-2_0_3_line_30 | NAYY 4x150 SE | 27 | 33 | 0.012255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2029-2_0_3_line_31 | NAYY 4x150 SE | 28 | 29 | 0.039749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_2029-2_0_3_line_32 | NAYY 4x150 SE | 29 | 30 | 0.011631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2029-2_0_3_line_33 | NAYY 4x150 SE | 30 | 31 | 0.091817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2029-2_0_3_line_34 | NAYY 4x150 SE | 31 | 35 | 0.014756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2029-2_0_3_line_35 | NAYY 4x150 SE | 32 | 34 | 0.013859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_2029-2_0_3_line_36 | NAYY 4x150 SE | 34 | 64 | 0.045792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_2029-2_0_3_line_37 | NAYY 4x150 SE | 35 | 39 | 0.029663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2029-2_0_3_line_38 | NAYY 4x150 SE | 36 | 37 | 0.01601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2029-2_0_3_line_39 | NAYY 4x150 SE | 36 | 38 | 0.066341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2029-2_0_3_line_40 | NAYY 4x150 SE | 37 | 49 | 0.01831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2029-2_0_3_line_41 | NAYY 4x150 SE | 38 | 42 | 0.034326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2029-2_0_3_line_42 | NAYY 4x150 SE | 39 | 40 | 0.041375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2029-2_0_3_line_43 | NAYY 4x150 SE | 40 | 41 | 0.019615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2029-2_0_3_line_44 | NAYY 4x150 SE | 40 | 42 | 0.0037221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2029-2_0_3_line_45 | NAYY 4x150 SE | 41 | 43 | 0.023884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2029-2_0_3_line_46 | NAYY 4x150 SE | 43 | 44 | 0.0072626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2029-2_0_3_line_47 | NAYY 4x150 SE | 44 | 62 | 0.024926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2029-2_0_3_line_48 | NAYY 4x150 SE | 45 | 46 | 0.19129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_2029-2_0_3_line_49 | NAYY 4x150 SE | 46 | 50 | 0.20128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_2029-2_0_3_line_50 | NAYY 4x150 SE | 47 | 57 | 0.020118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2029-2_0_3_line_51 | NAYY 4x150 SE | 48 | 58 | 0.049761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2029-2_0_3_line_52 | NAYY 4x150 SE | 49 | 63 | 0.058548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2029-2_0_3_line_53 | NAYY 4x150 SE | 50 | 56 | 0.006274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_2029-2_0_3_line_54 | NAYY 4x150 SE | 51 | 52 | 0.02585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2029-2_0_3_line_55 | NAYY 4x150 SE | 52 | 53 | 0.026253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_2029-2_0_3_line_56 | NAYY 4x150 SE | 52 | 54 | 0.1312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_2029-2_0_3_line_57 | NAYY 4x150 SE | 53 | 55 | 0.042564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_2029-2_0_3_line_58 | NAYY 4x150 SE | 54 | 56 | 0.0054965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_2029-2_0_3_line_59 | NAYY 4x150 SE | 55 | 67 | 0.021313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_2029-2_0_3_line_60 | NAYY 4x150 SE | 57 | 59 | 0.016526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2029-2_0_3_line_61 | NAYY 4x150 SE | 59 | 60 | 0.01466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2029-2_0_3_line_62 | NAYY 4x150 SE | 60 | 61 | 0.025331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2029-2_0_3_line_63 | NAYY 4x150 SE | 61 | 62 | 0.0058243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2029-2_0_3_line_64 | NAYY 4x150 SE | 64 | 65 | 0.036942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
65 | LV_2029-2_0_3_line_65 | NAYY 4x150 SE | 65 | 66 | 0.0048405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
66 | LV_2029-2_0_3_line_66 | NAYY 4x150 SE | 66 | 67 | 0.039569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2029-2_0_3_trafo_29 | 0.25 MVA 20/0.4 kV | 68 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2565939.6945 | 1184655.0502 | 2565940.8339 | 1184654.0987 | 2565947.7633 | 1184651.28 | 2565954.9804 | 1184649.3823 | 2565974.5504 | 1184646.0187
1 | 2565939.6945 | 1184655.0502 | 2565938.0622 | 1184656.5825 | 2565927.41 | 1184666.4041 | 2565925.0305 | 1184668.0518 | 2565915.8824 | 1184672.6176 | 2565906.1084 | 1184675.8417 | 2565895.5099 | 1184677.9521
2 | 2565895.5099 | 1184677.9521 | 2565880.7596 | 1184680.8891 | 2565871.2577 | 1184684.9789 | 2565863.1254 | 1184692.3181 | 2565861.6528 | 1184693.8602
3 | 2565861.4773 | 1184694.044 | 2565861.6528 | 1184693.8602
4 | 2565846.3128 | 1184709.9236 | 2565861.4773 | 1184694.044
5 | 2565527.4541 | 1185166.9981 | 2565531.4759 | 1185173.5784
6 | 2565527.4541 | 1185166.9981 | 2565564.576 | 1185120.7792
7 | 2565562.2282 | 1185207.3413 | 2565542.9007 | 1185185.4855 | 2565531.4759 | 1185173.5784
8 | 2565531.4759 | 1185173.5784 | 2565541.5882 | 1185202.7134 | 2565570.8209 | 1185244.8376
9 | 2565457.063 | 1184936.5264 | 2565410.2062 | 1184980.4639
10 | 2565463.887 | 1184929.8688 | 2565462.0254 | 1184931.8731 | 2565457.063 | 1184936.5264
11 | 2565562.2282 | 1185207.3413 | 2565576.0333 | 1185188.8002
12 | 2565562.2282 | 1185207.3413 | 2565571.2657 | 1185218.6899
13 | 2565582.2803 | 1185258.6926 | 2565577.2268 | 1185254.0686 | 2565570.8209 | 1185244.8376
14 | 2565600.8081 | 1185275.411 | 2565669.0075 | 1185572.7541
15 | 2565600.8081 | 1185275.411 | 2565599.4299 | 1185274.3848 | 2565582.2803 | 1185258.6926
16 | 2566031.2006 | 1185117.8166 | 2566010.7944 | 1185083.4397 | 2566007.5091 | 1185079.1224
17 | 2566001.4509 | 1185071.1611 | 2566007.5091 | 1185079.1224
18 | 2566001.4509 | 1185071.1611 | 2565997.45 | 1185065.9033
19 | 2565977.6895 | 1185048.2028 | 2565980.8322 | 1185050.048 | 2565994.1083 | 1185061.5118 | 2565997.45 | 1185065.9033
20 | 2565977.6895 | 1185048.2028 | 2565974.8163 | 1185046.5158
21 | 2565969.4684 | 1185043.3758 | 2565974.8163 | 1185046.5158
22 | 2565969.4684 | 1185043.3758 | 2565955.6357 | 1185038.7189 | 2565930.7258 | 1185029.4893 | 2565921.0459 | 1185026.5161
23 | 2565969.4684 | 1185043.3758 | 2565964.3299 | 1185034.9451 | 2565932.0124 | 1185016.8864 | 2565927.1899 | 1185011.6889 | 2565926.2036 | 1185006.0248 | 2565918.2317 | 1184971.8744 | 2565913.961 | 1184963.0829 | 2565897.2785 | 1184941.9002 | 2565896.5615 | 1184940.9376
24 | 2565896.9334 | 1185019.1099 | 2565921.0459 | 1185026.5161
25 | 2565896.5615 | 1184940.9376 | 2565883.5423 | 1184923.4577 | 2565873.0028 | 1184902.1733 | 2565867.3366 | 1184885.5968 | 2565864.8122 | 1184857.8743 | 2565864.1055 | 1184833.054 | 2565862.3686 | 1184825.6044 | 2565860.2175 | 1184823.1376 | 2565855.1682 | 1184819.9089
26 | 2565896.9334 | 1185019.1099 | 2565887.4544 | 1185017.7633 | 2565884.9683 | 1185017.4103
27 | 2565820.5193 | 1184799.9412 | 2565822.0419 | 1184803.2676 | 2565824.7122 | 1184808.4328 | 2565826.5816 | 1184811.0124 | 2565828.3691 | 1184812.6141 | 2565831.6612 | 1184813.0622 | 2565839.54 | 1184813.4729 | 2565849.9447 | 1184815.1699 | 2565852.1359 | 1184817.97 | 2565855.1682 | 1184819.9089
28 | 2565884.9683 | 1185017.4103 | 2565872.9267 | 1185015.7007 | 2565856.6652 | 1185016.0939 | 2565852.3319 | 1185016.6817
29 | 2565820.5193 | 1184799.9412 | 2565822.0403 | 1184798.9875 | 2565829.8353 | 1184790.0826 | 2565834.4012 | 1184782.3969 | 2565838.3089 | 1184774.3925 | 2565839.4482 | 1184769.1283
30 | 2565820.5193 | 1184799.9412 | 2565809.9221 | 1184806.0952
31 | 2565852.3319 | 1185016.6817 | 2565842.2062 | 1185018.0553 | 2565813.5505 | 1185025.1901
32 | 2565802.2641 | 1185028.0003 | 2565813.5505 | 1185025.1901
33 | 2565802.2641 | 1185028.0003 | 2565760.4147 | 1185081.9576 | 2565754.704 | 1185085.6033 | 2565748.8448 | 1185084.6364 | 2565740.4081 | 1185077.8642
34 | 2565728.4256 | 1185069.312 | 2565728.4256 | 1185069.312 | 2565733.5948 | 1185072.3951 | 2565740.4081 | 1185077.8642
35 | 2565841.6129 | 1184755.4434 | 2565839.9373 | 1184766.8681 | 2565839.4482 | 1184769.1283
36 | 2565846.3128 | 1184709.9236 | 2565844.3119 | 1184723.0531 | 2565842.1337 | 1184751.892 | 2565841.6129 | 1184755.4434
37 | 2565705.3975 | 1185083.9287 | 2565709.9849 | 1185084.915 | 2565714.7625 | 1185083.5869 | 2565725.1078 | 1185071.0098 | 2565728.4256 | 1185069.312
38 | 2565687.5102 | 1185000.1101 | 2565681.4602 | 1184985.2877
39 | 2565687.5102 | 1185000.1101 | 2565676.7927 | 1185003.7069 | 2565669.8298 | 1185008.5828 | 2565659.2351 | 1185018.927 | 2565637.8026 | 1185042.4628
40 | 2565681.4602 | 1184985.2877 | 2565674.5409 | 1184968.3354
41 | 2565637.8026 | 1185042.4628 | 2565667.2833 | 1185060.0454
42 | 2565670.4801 | 1185061.9519 | 2565703.5892 | 1185083.5399 | 2565705.3975 | 1185083.9287
43 | 2565670.4801 | 1185061.9519 | 2565658.7659 | 1185077.6848
44 | 2565670.4801 | 1185061.9519 | 2565667.2833 | 1185060.0454
45 | 2565644.5022 | 1185096.8419 | 2565658.7659 | 1185077.6848
46 | 2565644.5022 | 1185096.8419 | 2565640.165 | 1185102.6671
47 | 2565625.279 | 1185122.66 | 2565640.165 | 1185102.6671
48 | 2565463.887 | 1184929.8688 | 2565429.3552 | 1184741.7248
49 | 2565616.7783 | 1184668.3334 | 2565429.3552 | 1184741.7248
50 | 2565576.0333 | 1185188.8002 | 2565588.048 | 1185172.6636
51 | 2565603.1656 | 1185245.9037 | 2565597.2671 | 1185251.3406 | 2565571.2657 | 1185218.6899
52 | 2565674.5409 | 1184968.3354 | 2565673.8705 | 1184966.6929 | 2565668.8775 | 1184947.8226 | 2565668.3886 | 1184934.4628 | 2565669.4129 | 1184922.7951 | 2565672.6284 | 1184911.0548
53 | 2565619.9124 | 1184673.6775 | 2565619.3585 | 1184673.039 | 2565617.6959 | 1184669.2799 | 2565616.7783 | 1184668.3334
54 | 2565694.0354 | 1184788.4205 | 2565672.0642 | 1184802.0392
55 | 2565717.6434 | 1184777.0316 | 2565699.0218 | 1184785.3297 | 2565694.0354 | 1184788.4205
56 | 2565694.0354 | 1184788.4205 | 2565623.6615 | 1184677.6912
57 | 2565756.3115 | 1184759.2578 | 2565745.1705 | 1184764.7651 | 2565717.6434 | 1184777.0316
58 | 2565619.9124 | 1184673.6775 | 2565621.8249 | 1184675.8819 | 2565623.6615 | 1184677.6912
59 | 2565775.4172 | 1184749.8134 | 2565756.3115 | 1184759.2578
60 | 2565597.9172 | 1185159.4086 | 2565588.048 | 1185172.6636
61 | 2565597.9172 | 1185159.4086 | 2565606.6725 | 1185147.6496
62 | 2565606.6725 | 1185147.6496 | 2565621.8006 | 1185127.3316
63 | 2565625.279 | 1185122.66 | 2565621.8006 | 1185127.3316
64 | 2565846.3128 | 1184709.9236 | 2565829.5358 | 1184719.0688 | 2565813.9535 | 1184727.7445
65 | 2565809.7243 | 1184730.0991 | 2565813.9535 | 1184727.7445
66 | 2565809.7243 | 1184730.0991 | 2565775.8417 | 1184749.6035 | 2565775.4172 | 1184749.8134

## bus_geodata
| x | y | coords
0 | 2565974.5504 | 1184646.0187
1 | 2565939.6945 | 1184655.0502
2 | 2565895.5099 | 1184677.9521
3 | 2565861.6528 | 1184693.8602
4 | 2565861.4773 | 1184694.044
5 | 2565527.4541 | 1185166.9981
6 | 2565531.4759 | 1185173.5784
7 | 2565564.576 | 1185120.7792
8 | 2565410.2062 | 1184980.4639
9 | 2565457.063 | 1184936.5264
10 | 2565562.2282 | 1185207.3413
11 | 2565570.8209 | 1185244.8376
12 | 2565669.0075 | 1185572.7541
13 | 2565600.8081 | 1185275.411
14 | 2565582.2803 | 1185258.6926
15 | 2566031.2006 | 1185117.8166
16 | 2566007.5091 | 1185079.1224
17 | 2566001.4509 | 1185071.1611
18 | 2565997.45 | 1185065.9033
19 | 2565977.6895 | 1185048.2028
20 | 2565974.8163 | 1185046.5158
21 | 2565969.4684 | 1185043.3758
22 | 2565921.0459 | 1185026.5161
23 | 2565896.5615 | 1184940.9376
24 | 2565896.9334 | 1185019.1099
25 | 2565855.1682 | 1184819.9089
26 | 2565884.9683 | 1185017.4103
27 | 2565820.5193 | 1184799.9412
28 | 2565852.3319 | 1185016.6817
29 | 2565813.5505 | 1185025.1901
30 | 2565802.2641 | 1185028.0003
31 | 2565740.4081 | 1185077.8642
32 | 2565839.4482 | 1184769.1283
33 | 2565809.9221 | 1184806.0952
34 | 2565841.6129 | 1184755.4434
35 | 2565728.4256 | 1185069.312
36 | 2565687.5102 | 1185000.1101
37 | 2565681.4602 | 1184985.2877
38 | 2565637.8026 | 1185042.4628
39 | 2565705.3975 | 1185083.9287
40 | 2565670.4801 | 1185061.9519
41 | 2565658.7659 | 1185077.6848
42 | 2565667.2833 | 1185060.0454
43 | 2565644.5022 | 1185096.8419
44 | 2565640.165 | 1185102.6671
45 | 2565463.887 | 1184929.8688
46 | 2565429.3552 | 1184741.7248
47 | 2565576.0333 | 1185188.8002
48 | 2565571.2657 | 1185218.6899
49 | 2565674.5409 | 1184968.3354
50 | 2565616.7783 | 1184668.3334
51 | 2565672.0642 | 1184802.0392
52 | 2565694.0354 | 1184788.4205
53 | 2565717.6434 | 1184777.0316
54 | 2565623.6615 | 1184677.6912
55 | 2565756.3115 | 1184759.2578
56 | 2565619.9124 | 1184673.6775
57 | 2565588.048 | 1185172.6636
58 | 2565603.1656 | 1185245.9037
59 | 2565597.9172 | 1185159.4086
60 | 2565606.6725 | 1185147.6496
61 | 2565621.8006 | 1185127.3316
62 | 2565625.279 | 1185122.66
63 | 2565672.6284 | 1184911.0548
64 | 2565846.3128 | 1184709.9236
65 | 2565813.9535 | 1184727.7445
66 | 2565809.7243 | 1184730.0991
67 | 2565775.4172 | 1184749.8134
68 | 2565802.2641 | 1185028.0003

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97566 | -0.17144 | 0.0035894 | 0.00089958
1 | 0.97585 | -0.17008 | 0 | 0
2 | 0.97612 | -0.16816 | 0.0010743 | 0.00026924
3 | 0.97638 | -0.16628 | 0.0071502 | 0.001792
4 | 0.97639 | -0.16624 | 0.0035015 | 0.00087756
5 | 0.99054 | -0.06667 | 0 | 0
6 | 0.99055 | -0.066605 | 0 | 0
7 | 0.99047 | -0.067169 | 0.00082421 | 0.00020657
8 | 0.97002 | -0.21218 | 0.0024869 | 0.00062328
9 | 0.97026 | -0.21048 | 0.001795 | 0.00044987
10 | 0.99091 | -0.064 | 0 | 0
11 | 0.98999 | -0.070598 | 0.0008908 | 0.00022325
12 | 0.98954 | -0.073783 | 0.00047362 | 0.0001187
13 | 0.98975 | -0.072266 | 0.0032404 | 0.00081213
14 | 0.98989 | -0.071313 | 0.00013648 | 3.4205e-05
15 | 0.98921 | -0.075259 | 0.0023722 | 0.00059454
16 | 0.98937 | -0.074159 | 0.00080144 | 0.00020086
17 | 0.98941 | -0.073835 | 0.0021557 | 0.00054027
18 | 0.98947 | -0.073476 | 0.010217 | 0.0025606
19 | 0.99006 | -0.069245 | 0.002889 | 0.00072404
20 | 0.99015 | -0.068619 | 0.0038867 | 0.00097409
21 | 0.99035 | -0.067209 | 0 | 0
22 | 0.99304 | -0.048404 | 0.0014115 | 0.00035375
23 | 0.98553 | -0.10108 | 0.0043651 | 0.001094
24 | 0.99438 | -0.039011 | 0 | 0
25 | 0.98114 | -0.13225 | 0.001247 | 0.00031252
26 | 0.99503 | -0.03452 | 0.0004052 | 0.00010155
27 | 0.97972 | -0.14235 | 0 | 0
28 | 0.99679 | -0.022292 | 0.037921 | 0.009504
29 | 1 | 0 | -0.14183 | -0.03553
30 | 0.99954 | -0.003208 | 0 | 0
31 | 0.99591 | -0.028632 | 0.001212 | 0.00030375
32 | 0.97858 | -0.15053 | 0.0014104 | 0.00035347
33 | 0.97969 | -0.14256 | 0.0016367 | 0.00041021
34 | 0.97816 | -0.15351 | 0.0026494 | 0.00066399
35 | 0.99535 | -0.032554 | 0.0028371 | 0.00071105
36 | 0.99159 | -0.05913 | 0 | 0
37 | 0.99137 | -0.060687 | 0.0023683 | 0.00059356
38 | 0.9925 | -0.052682 | 0 | 0
39 | 0.99435 | -0.039602 | 0.0013475 | 0.00033771
40 | 0.99304 | -0.04889 | 0 | 0
41 | 0.99276 | -0.050879 | 0.00034175 | 8.5651e-05
42 | 0.99297 | -0.04935 | 0.0026027 | 0.0006523
43 | 0.99243 | -0.053219 | 0.00039174 | 9.8179e-05
44 | 0.99233 | -0.053902 | 0.00037282 | 9.3437e-05
45 | 0.97029 | -0.21027 | 0.0054536 | 0.0013668
46 | 0.97166 | -0.20038 | 0.00061192 | 0.00015336
47 | 0.99112 | -0.06252 | 0.00055817 | 0.00013989
48 | 0.9909 | -0.0641 | 0.00038816 | 9.7283e-05
49 | 0.99118 | -0.062027 | 0.0021335 | 0.00053471
50 | 0.97319 | -0.18933 | 0.00046517 | 0.00011658
51 | 0.97449 | -0.17994 | 0.0013442 | 0.00033688
52 | 0.97454 | -0.17957 | 0.0015428 | 0.00038667
53 | 0.97484 | -0.17736 | 0.00061958 | 0.00015528
54 | 0.97328 | -0.18864 | 0.0016706 | 0.0004187
55 | 0.97536 | -0.17364 | 0.0010299 | 0.00025811
56 | 0.97324 | -0.18897 | 0.00055591 | 0.00013932
57 | 0.99132 | -0.061119 | 0.00040441 | 0.00010136
58 | 0.99088 | -0.064245 | 0.00028497 | 7.1421e-05
59 | 0.99149 | -0.0599 | 0.00046473 | 0.00011647
60 | 0.99165 | -0.058749 | 0.00042091 | 0.00010549
61 | 0.99194 | -0.056654 | 0.00033902 | 8.4967e-05
62 | 0.99201 | -0.056152 | 0.00040822 | 0.00010231
63 | 0.99075 | -0.065045 | 0.0050691 | 0.0012704
64 | 0.97688 | -0.16272 | 0 | 0
65 | 0.97625 | -0.16721 | 0.0040822 | 0.0010231
66 | 0.97619 | -0.16769 | 0 | 0
67 | 0.97563 | -0.17166 | 0.001413 | 0.00035412
68 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0035894 | -0.00089958 | 0.00359 | 0.00089939 | 6.7849e-07 | -1.9227e-07 | 0.0054743 | 0.0054741 | 0.0054743 | 0.97566 | -0.17144 | 0.97585 | -0.17008 | 2.0275
1 | -0.00359 | -0.00089939 | 0.003591 | 0.00089912 | 9.5256e-07 | -2.7028e-07 | 0.0054741 | 0.0054739 | 0.0054741 | 0.97585 | -0.17008 | 0.97612 | -0.16816 | 2.0274
2 | -0.0046653 | -0.0011684 | 0.0046665 | 0.0011683 | 1.214e-06 | -1.4086e-08 | 0.0071115 | 0.0071113 | 0.0071115 | 0.97612 | -0.16816 | 0.97638 | -0.16628 | 2.6339
3 | -0.011817 | -0.0029604 | 0.011817 | 0.0029604 | 5.1422e-08 | 1.6599e-08 | 0.018008 | 0.018008 | 0.018008 | 0.97638 | -0.16628 | 0.97639 | -0.16624 | 6.6698
4 | -0.015318 | -0.0038379 | 0.015326 | 0.0038405 | 7.4669e-06 | 2.5971e-06 | 0.023345 | 0.023345 | 0.023345 | 0.97639 | -0.16624 | 0.97688 | -0.16272 | 8.6462
5 | -0.00082427 | -0.00020583 | 0.00082428 | 0.00020573 | 7.3703e-09 | -9.6372e-08 | 0.001238 | 0.0012379 | 0.001238 | 0.99054 | -0.06667 | 0.99055 | -0.066605 | 0.45851
6 | 0.00082427 | 0.00020583 | -0.00082421 | -0.00020657 | 5.6705e-08 | -7.4121e-07 | 0.001238 | 0.0012382 | 0.0012382 | 0.99054 | -0.06667 | 0.99047 | -0.067169 | 0.45861
7 | -0.0055692 | -0.0013899 | 0.0055711 | 0.00139 | 1.9916e-06 | 1.7848e-07 | 0.008364 | 0.0083638 | 0.008364 | 0.99055 | -0.066605 | 0.99091 | -0.064 | 3.0978
8 | 0.0047449 | 0.0011841 | -0.0047423 | -0.0011842 | 2.6021e-06 | -5.56e-08 | 0.0071261 | 0.0071264 | 0.0071264 | 0.99055 | -0.066605 | 0.98999 | -0.070598 | 2.6394
9 | -0.0024869 | -0.00062328 | 0.0024875 | 0.00062271 | 5.833e-07 | -5.6879e-07 | 0.0038149 | 0.0038146 | 0.0038149 | 0.97002 | -0.21218 | 0.97026 | -0.21048 | 1.4129
10 | -0.0042825 | -0.0010726 | 0.0042826 | 0.0010724 | 1.2836e-07 | -1.8624e-07 | 0.0065675 | 0.0065674 | 0.0065675 | 0.97026 | -0.21048 | 0.97029 | -0.21027 | 1.2162
11 | -0.0062443 | -0.0015579 | 0.0062456 | 0.0015581 | 1.2676e-06 | 1.8969e-07 | 0.0093743 | 0.0093742 | 0.0093743 | 0.99091 | -0.064 | 0.99112 | -0.06252 | 3.472
12 | 0.00067315 | 0.00016788 | -0.00067314 | -0.00016806 | 9.2454e-09 | -1.8333e-07 | 0.0010106 | 0.0010106 | 0.0010106 | 0.99091 | -0.064 | 0.9909 | -0.0641 | 0.3743
13 | 0.0038515 | 0.00096093 | -0.0038511 | -0.00096101 | 3.7802e-07 | -8.713e-08 | 0.0057875 | 0.0057876 | 0.0057876 | 0.98999 | -0.070598 | 0.98989 | -0.071313 | 2.1435
14 | -0.00047362 | -0.0001187 | 0.00047371 | 0.00011482 | 9.6368e-08 | -3.8827e-06 | 0.0007122 | 0.00071083 | 0.0007122 | 0.98954 | -0.073783 | 0.98975 | -0.072266 | 0.26378
15 | -0.0037141 | -0.00092694 | 0.0037146 | 0.00092681 | 4.8546e-07 | -1.3416e-07 | 0.0055825 | 0.0055824 | 0.0055825 | 0.98975 | -0.072266 | 0.98989 | -0.071313 | 2.0676
16 | -0.0023722 | -0.00059454 | 0.0023726 | 0.0005941 | 3.6074e-07 | -4.4421e-07 | 0.0035684 | 0.0035682 | 0.0035684 | 0.98921 | -0.075259 | 0.98937 | -0.074159 | 1.3216
17 | -0.003174 | -0.00079496 | 0.0031742 | 0.00079488 | 1.4225e-07 | -7.3766e-08 | 0.0047736 | 0.0047735 | 0.0047736 | 0.98937 | -0.074159 | 0.98941 | -0.073835 | 1.768
18 | -0.0053299 | -0.0013352 | 0.0053302 | 0.0013352 | 2.6489e-07 | 1.7021e-08 | 0.0080156 | 0.0080156 | 0.0080156 | 0.98941 | -0.073835 | 0.98947 | -0.073476 | 2.9687
19 | -0.015547 | -0.0038958 | 0.015556 | 0.0038989 | 9.1085e-06 | 3.1601e-06 | 0.02338 | 0.02338 | 0.02338 | 0.98947 | -0.073476 | 0.99006 | -0.069245 | 8.6594
20 | -0.018445 | -0.004623 | 0.018447 | 0.0046235 | 1.5978e-06 | 5.717e-07 | 0.027722 | 0.027722 | 0.027722 | 0.99006 | -0.069245 | 0.99015 | -0.068619 | 10.2674
21 | -0.022333 | -0.0055976 | 0.022338 | 0.0055992 | 4.3592e-06 | 1.5968e-06 | 0.033563 | 0.033563 | 0.033563 | 0.99015 | -0.068619 | 0.99035 | -0.067209 | 12.4308
22 | -0.072747 | -0.018297 | 0.072938 | 0.01837 | 0.00019125 | 7.2234e-05 | 0.10933 | 0.10933 | 0.10933 | 0.99035 | -0.067209 | 0.99304 | -0.048404 | 20.2455
23 | 0.050409 | 0.012698 | -0.050171 | -0.01261 | 0.00023772 | 8.8033e-05 | 0.075763 | 0.075764 | 0.075764 | 0.99035 | -0.067209 | 0.98553 | -0.10108 | 14.0304
24 | -0.074349 | -0.018723 | 0.074447 | 0.01876 | 9.7737e-05 | 3.6937e-05 | 0.11144 | 0.11144 | 0.11144 | 0.99304 | -0.048404 | 0.99438 | -0.039011 | 20.6371
25 | 0.045806 | 0.011516 | -0.045608 | -0.011443 | 0.00019803 | 7.2802e-05 | 0.069173 | 0.069175 | 0.069175 | 0.98553 | -0.10108 | 0.98114 | -0.13225 | 12.8101
26 | -0.074447 | -0.01876 | 0.074494 | 0.018778 | 4.6826e-05 | 1.7696e-05 | 0.11144 | 0.11144 | 0.11144 | 0.99438 | -0.039011 | 0.99503 | -0.03452 | 20.6371
27 | 0.044361 | 0.011131 | -0.044299 | -0.011108 | 6.2102e-05 | 2.2777e-05 | 0.067283 | 0.067284 | 0.067284 | 0.98114 | -0.13225 | 0.97972 | -0.14235 | 12.46
28 | -0.074899 | -0.01888 | 0.075027 | 0.018928 | 0.00012848 | 4.8562e-05 | 0.11205 | 0.11205 | 0.11205 | 0.99503 | -0.03452 | 0.99679 | -0.022292 | 20.7493
29 | 0.042662 | 0.010698 | -0.042614 | -0.01068 | 4.8291e-05 | 1.7646e-05 | 0.064798 | 0.064798 | 0.064798 | 0.97972 | -0.14235 | 0.97858 | -0.15053 | 11.9997
30 | 0.0016368 | 0.00041007 | -0.0016367 | -0.00041021 | 4.7257e-08 | -1.3614e-07 | 0.0024859 | 0.002486 | 0.002486 | 0.97972 | -0.14235 | 0.97969 | -0.14256 | 0.92074
31 | -0.11295 | -0.028432 | 0.1133 | 0.028567 | 0.00035276 | 0.00013464 | 0.16866 | 0.16865 | 0.16866 | 0.99679 | -0.022292 | 1 | 0 | 31.2324
32 | 0.027729 | 0.0069635 | -0.027716 | -0.0069589 | 1.2359e-05 | 4.6009e-06 | 0.041266 | 0.041266 | 0.041266 | 1 | 0 | 0.99954 | -0.003208 | 15.2836
33 | 0.027716 | 0.0069589 | -0.027619 | -0.0069226 | 9.7564e-05 | 3.6325e-05 | 0.041266 | 0.041266 | 0.041266 | 0.99954 | -0.003208 | 0.99591 | -0.028632 | 15.2837
34 | 0.026407 | 0.0066188 | -0.026392 | -0.0066135 | 1.4334e-05 | 5.321e-06 | 0.039455 | 0.039455 | 0.039455 | 0.99591 | -0.028632 | 0.99535 | -0.032554 | 14.6131
35 | 0.041203 | 0.010327 | -0.041186 | -0.010321 | 1.6974e-05 | 6.1805e-06 | 0.062654 | 0.062654 | 0.062654 | 0.97858 | -0.15053 | 0.97816 | -0.15351 | 11.6026
36 | 0.038537 | 0.0096566 | -0.038488 | -0.0096389 | 4.9101e-05 | 1.7737e-05 | 0.058623 | 0.058624 | 0.058624 | 0.97816 | -0.15351 | 0.97688 | -0.16272 | 10.8563
37 | 0.023555 | 0.0059025 | -0.023532 | -0.005894 | 2.2953e-05 | 8.4428e-06 | 0.035214 | 0.035214 | 0.035214 | 0.99535 | -0.032554 | 0.99435 | -0.039602 | 13.0422
38 | 0.0095765 | 0.0023996 | -0.0095745 | -0.0023991 | 2.0631e-06 | 5.8704e-07 | 0.014371 | 0.014371 | 0.014371 | 0.99159 | -0.05913 | 0.99137 | -0.060687 | 5.3225
39 | -0.0095765 | -0.0023996 | 0.0095851 | 0.0024021 | 8.5491e-06 | 2.4316e-06 | 0.014371 | 0.01437 | 0.014371 | 0.99159 | -0.05913 | 0.9925 | -0.052682 | 5.3225
40 | 0.0072061 | 0.0018055 | -0.0072048 | -0.0018052 | 1.3366e-06 | 2.7805e-07 | 0.010816 | 0.010816 | 0.010816 | 0.99137 | -0.060687 | 0.99118 | -0.062027 | 4.006
41 | -0.0095851 | -0.0024021 | 0.0095895 | 0.0024033 | 4.4233e-06 | 1.2574e-06 | 0.01437 | 0.01437 | 0.01437 | 0.9925 | -0.052682 | 0.99297 | -0.04935 | 5.3224
42 | 0.022185 | 0.0055563 | -0.022156 | -0.0055459 | 2.8454e-05 | 1.0408e-05 | 0.033198 | 0.033198 | 0.033198 | 0.99435 | -0.039602 | 0.99304 | -0.04889 | 12.2955
43 | 0.0099634 | 0.00249 | -0.0099607 | -0.0024892 | 2.7273e-06 | 7.9526e-07 | 0.014927 | 0.014927 | 0.014927 | 0.99304 | -0.04889 | 0.99276 | -0.050879 | 5.5286
44 | 0.012193 | 0.0030559 | -0.012192 | -0.0030556 | 7.7533e-07 | 2.5005e-07 | 0.018271 | 0.018271 | 0.018271 | 0.99304 | -0.04889 | 0.99297 | -0.04935 | 6.7669
45 | 0.0096189 | 0.0024035 | -0.0096158 | -0.0024027 | 3.0969e-06 | 8.8239e-07 | 0.014415 | 0.014415 | 0.014415 | 0.99276 | -0.050879 | 0.99243 | -0.053219 | 5.3389
46 | 0.0092241 | 0.0023045 | -0.0092232 | -0.0023042 | 8.6652e-07 | 2.3944e-07 | 0.013828 | 0.013828 | 0.013828 | 0.99243 | -0.053219 | 0.99233 | -0.053902 | 5.1214
47 | 0.0088504 | 0.0022108 | -0.0088477 | -0.0022101 | 2.7384e-06 | 7.3133e-07 | 0.013269 | 0.013269 | 0.013269 | 0.99233 | -0.053902 | 0.99201 | -0.056152 | 4.9144
48 | -0.0097362 | -0.0024392 | 0.0097495 | 0.0024396 | 1.3303e-05 | 3.8478e-07 | 0.014931 | 0.014929 | 0.014931 | 0.97029 | -0.21027 | 0.97166 | -0.20038 | 2.765
49 | -0.010361 | -0.0025929 | 0.010377 | 0.002594 | 1.5807e-05 | 1.0857e-06 | 0.015866 | 0.015865 | 0.015866 | 0.97166 | -0.20038 | 0.97319 | -0.18933 | 2.9382
50 | -0.0068037 | -0.001698 | 0.006805 | 0.0016982 | 1.3092e-06 | 2.4423e-07 | 0.010212 | 0.010212 | 0.010212 | 0.99112 | -0.06252 | 0.99132 | -0.061119 | 3.7823
51 | 0.00028498 | 7.0782e-05 | -0.00028497 | -7.1421e-05 | 5.6836e-09 | -6.388e-07 | 0.00042772 | 0.00042795 | 0.00042795 | 0.9909 | -0.0641 | 0.99088 | -0.064245 | 0.1585
52 | 0.0050713 | 0.0012705 | -0.0050691 | -0.0012704 | 2.1176e-06 | 6.0165e-08 | 0.0076131 | 0.0076134 | 0.0076134 | 0.99118 | -0.062027 | 0.99075 | -0.065045 | 2.8198
53 | -0.010842 | -0.0027106 | 0.010843 | 0.0027107 | 5.3783e-07 | 5.094e-08 | 0.016576 | 0.016576 | 0.016576 | 0.97319 | -0.18933 | 0.97324 | -0.18897 | 3.0696
54 | -0.0013442 | -0.00033688 | 0.0013442 | 0.00033658 | 6.7948e-08 | -2.9593e-07 | 0.0020525 | 0.0020524 | 0.0020525 | 0.97449 | -0.17994 | 0.97454 | -0.17957 | 0.76018
55 | -0.015973 | -0.003995 | 0.015978 | 0.0039962 | 4.8713e-06 | 1.2192e-06 | 0.024387 | 0.024387 | 0.024387 | 0.97454 | -0.17957 | 0.97484 | -0.17736 | 4.5161
56 | 0.013086 | 0.0032718 | -0.01307 | -0.0032687 | 1.634e-05 | 3.0193e-06 | 0.019979 | 0.01998 | 0.01998 | 0.97454 | -0.17957 | 0.97328 | -0.18864 | 3.7
57 | -0.016598 | -0.0041515 | 0.016606 | 0.0041537 | 8.522e-06 | 2.2158e-06 | 0.025332 | 0.025332 | 0.025332 | 0.97484 | -0.17736 | 0.97536 | -0.17364 | 4.6912
58 | 0.011399 | 0.00285 | -0.011399 | -0.00285 | 5.2074e-07 | 6.3673e-08 | 0.017426 | 0.017426 | 0.017426 | 0.97328 | -0.18864 | 0.97324 | -0.18897 | 3.227
59 | -0.017636 | -0.0044118 | 0.017641 | 0.0044132 | 4.8127e-06 | 1.3189e-06 | 0.026903 | 0.026903 | 0.026903 | 0.97536 | -0.17364 | 0.97563 | -0.17166 | 4.9821
60 | -0.0072095 | -0.0017996 | 0.0072107 | 0.0017998 | 1.2071e-06 | 2.5116e-07 | 0.010819 | 0.010819 | 0.010819 | 0.99132 | -0.061119 | 0.99149 | -0.0599 | 4.0071
61 | -0.0076754 | -0.0019163 | 0.0076766 | 0.0019166 | 1.2133e-06 | 2.7756e-07 | 0.011517 | 0.011517 | 0.011517 | 0.99149 | -0.0599 | 0.99165 | -0.058749 | 4.2654
62 | -0.0080975 | -0.0020221 | 0.0080998 | 0.0020227 | 2.3327e-06 | 5.7029e-07 | 0.012148 | 0.012148 | 0.012148 | 0.99165 | -0.058749 | 0.99194 | -0.056654 | 4.4993
63 | -0.0084389 | -0.0021076 | 0.0084394 | 0.0021078 | 5.8218e-07 | 1.4873e-07 | 0.012657 | 0.012657 | 0.012657 | 0.99194 | -0.056654 | 0.99201 | -0.056152 | 4.6876
64 | 0.023162 | 0.0057984 | -0.023148 | -0.0057938 | 1.4346e-05 | 4.5932e-06 | 0.035279 | 0.03528 | 0.03528 | 0.97688 | -0.16272 | 0.97625 | -0.16721 | 6.5333
65 | 0.019066 | 0.0047707 | -0.019064 | -0.0047703 | 1.2752e-06 | 3.694e-07 | 0.029058 | 0.029058 | 0.029058 | 0.97625 | -0.16721 | 0.97619 | -0.16769 | 5.381
66 | 0.019064 | 0.0047703 | -0.019054 | -0.0047673 | 1.0424e-05 | 3.0204e-06 | 0.029058 | 0.029058 | 0.029058 | 0.97619 | -0.16769 | 0.97563 | -0.17166 | 5.3811

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20562 | 0.051517

## res_load
| p_mw | q_mvar
0 | 0.0035894 | 0.00089958
1 | 0.0010743 | 0.00026924
2 | 0.0071502 | 0.001792
3 | 0.0035015 | 0.00087756
4 | 0.00082421 | 0.00020657
5 | 0.0024869 | 0.00062328
6 | 0.001795 | 0.00044987
7 | 0.0008908 | 0.00022325
8 | 0.00047362 | 0.0001187
9 | 0.0032404 | 0.00081213
10 | 0.00013648 | 3.4205e-05
11 | 0.0023722 | 0.00059454
12 | 0.00080144 | 0.00020086
13 | 0.0021557 | 0.00054027
14 | 0.010217 | 0.0025606
15 | 0.002889 | 0.00072404
16 | 0.0038867 | 0.00097409
17 | 0.0014115 | 0.00035375
18 | 0.0043651 | 0.001094
19 | 0.001247 | 0.00031252
20 | 0.0004052 | 0.00010155
21 | 0.037921 | 0.009504
22 | 0.063786 | 0.015986
23 | 0.001212 | 0.00030375
24 | 0.0014104 | 0.00035347
25 | 0.0016367 | 0.00041021
26 | 0.0026494 | 0.00066399
27 | 0.0028371 | 0.00071105
28 | 0.0023683 | 0.00059356
29 | 0.0013475 | 0.00033771
30 | 0.00034175 | 8.5651e-05
31 | 0.0026027 | 0.0006523
32 | 0.00039174 | 9.8179e-05
33 | 0.00037282 | 9.3437e-05
34 | 0.0054536 | 0.0013668
35 | 0.00061192 | 0.00015336
36 | 0.00055817 | 0.00013989
37 | 0.00038816 | 9.7283e-05
38 | 0.0021335 | 0.00053471
39 | 0.00046517 | 0.00011658
40 | 0.0013442 | 0.00033688
41 | 0.0015428 | 0.00038667
42 | 0.00061958 | 0.00015528
43 | 0.0016706 | 0.0004187
44 | 0.0010299 | 0.00025811
45 | 0.00055591 | 0.00013932
46 | 0.00040441 | 0.00010136
47 | 0.00028497 | 7.1421e-05
48 | 0.00046473 | 0.00011647
49 | 0.00042091 | 0.00010549
50 | 0.00033902 | 8.4967e-05
51 | 0.00040822 | 0.00010231
52 | 0.0050691 | 0.0012704
53 | 0.0040822 | 0.0010231
54 | 0.001413 | 0.00035412

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1