## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2029-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2029-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2029-4_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2029-4_0_3_node_14 | 0.4 | n |  | TRUE
4 | bus_LV_2029-4_0_3_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_2029-4_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2029-4_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2029-4_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2029-4_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2029-4_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2029-4_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_2029-4_0_3_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_2029-4_0_3_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_2029-4_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2029-4_0_3_node_43 | 0.4 | n |  | TRUE
15 | bus_LV_2029-4_0_3_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_2029-4_0_3_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_2029-4_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2029-4_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2029-4_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2029-4_0_3_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_2029-4_0_3_node_45 | 0.4 | n |  | TRUE
22 | bus_LV_2029-4_0_3_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_2029-4_0_3_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_2029-4_0_3_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_2029-4_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2029-4_0_3_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_2029-4_0_3_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_2029-4_0_3_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_2029-4_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_2029-4_0_3_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_2029-4_0_3_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2029-4_0_3_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_2029-4_0_3_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_2029-4_0_3_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_2029-4_0_3_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_2029-4_0_3_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_2029-4_0_3_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_2029-4_0_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2029-4_0_3_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_2029-4_0_3_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_2029-4_0_3_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_2029-4_0_3_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_2029-4_0_3_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_2029-4_0_3_node_47 | 0.4 | n |  | TRUE
45 | bus_MV_477_0_node_188 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2029-4_0_3_load_0 | 0 | 0.0071252 | 0.0017857 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2029-4_0_3_load_14 | 3 | 0.0038178 | 0.00095682 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2029-4_0_3_load_11 | 4 | 0.0021584 | 0.00054095 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2029-4_0_3_load_4 | 5 | 0.003396 | 0.00085111 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2029-4_0_3_load_6 | 7 | 0.0028825 | 0.00072242 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2029-4_0_3_load_9 | 10 | 0.00664 | 0.0016641 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2029-4_0_3_load_19 | 12 | 0.010288 | 0.0025784 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2029-4_0_3_load_43 | 14 | 0.0054855 | 0.0013748 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2029-4_0_3_load_20 | 16 | 0.0040391 | 0.0010123 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2029-4_0_3_load_15 | 18 | 0.020259 | 0.0050774 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2029-4_0_3_load_16 | 19 | 0.017375 | 0.0043546 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2029-4_0_3_load_44 | 22 | 0.041608 | 0.010428 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2029-4_0_3_load_23 | 23 | 0.0061186 | 0.0015335 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2029-4_0_3_load_26 | 26 | 0.026191 | 0.006564 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2029-4_0_3_load_27 | 29 | 0.015951 | 0.0039976 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2029-4_0_3_load_28 | 30 | 0.011273 | 0.0028252 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2029-4_0_3_load_21 | 31 | 0.0014242 | 0.00035694 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2029-4_0_3_load_35 | 32 | 0.0030973 | 0.00077625 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2029-4_0_3_load_42 | 34 | 0.0017602 | 0.00044114 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2029-4_0_3_load_46 | 35 | 0.0087845 | 0.0022016 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2029-4_0_3_load_31 | 37 | 0.0054372 | 0.0013627 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2029-4_0_3_load_33 | 39 | 0.00061819 | 0.00015493 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2029-4_0_3_load_34 | 40 | 0.0040816 | 0.0010229 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2029-4_0_3_load_38 | 42 | 0.0012083 | 0.00030283 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2029-4_0_3_load_47 | 44 | 0.0087796 | 0.0022004 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2029-4_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.098391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2029-4_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.013389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2029-4_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.017101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2029-4_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.026507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2029-4_0_3_line_4 | NAYY 4x150 SE | 4 | 13 | 0.018343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2029-4_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.009622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2029-4_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.0087884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2029-4_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.019125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2029-4_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.038135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2029-4_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.015971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2029-4_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.00553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2029-4_0_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.0058067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2029-4_0_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.014453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2029-4_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.023129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2029-4_0_3_line_14 | NAYY 4x150 SE | 11 | 15 | 0.011902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2029-4_0_3_line_15 | NAYY 4x150 SE | 12 | 16 | 0.031139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2029-4_0_3_line_16 | NAYY 4x150 SE | 14 | 34 | 0.013091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2029-4_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.022735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2029-4_0_3_line_18 | NAYY 4x150 SE | 16 | 31 | 0.0014153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2029-4_0_3_line_19 | NAYY 4x150 SE | 17 | 18 | 0.0137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2029-4_0_3_line_20 | NAYY 4x150 SE | 18 | 19 | 0.0020325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2029-4_0_3_line_21 | NAYY 4x150 SE | 19 | 25 | 0.0093404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2029-4_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.02449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2029-4_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.036045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2029-4_0_3_line_24 | NAYY 4x150 SE | 21 | 35 | 0.019859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2029-4_0_3_line_25 | NAYY 4x150 SE | 22 | 36 | 0.00074867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2029-4_0_3_line_26 | NAYY 4x150 SE | 23 | 24 | 0.011354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2029-4_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.013695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_2029-4_0_3_line_28 | NAYY 4x150 SE | 24 | 25 | 0.004836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2029-4_0_3_line_29 | NAYY 4x150 SE | 26 | 28 | 0.010081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_2029-4_0_3_line_30 | NAYY 4x150 SE | 27 | 28 | 0.003202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_2029-4_0_3_line_31 | NAYY 4x150 SE | 27 | 29 | 0.015333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2029-4_0_3_line_32 | NAYY 4x150 SE | 28 | 36 | 0.031006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2029-4_0_3_line_33 | NAYY 4x150 SE | 29 | 30 | 0.0016161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2029-4_0_3_line_34 | NAYY 4x150 SE | 31 | 32 | 0.029342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2029-4_0_3_line_35 | NAYY 4x150 SE | 32 | 33 | 0.0018676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2029-4_0_3_line_36 | NAYY 4x150 SE | 33 | 41 | 0.052815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2029-4_0_3_line_37 | NAYY 4x150 SE | 34 | 43 | 0.021157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2029-4_0_3_line_38 | NAYY 4x150 SE | 35 | 44 | 0.023244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2029-4_0_3_line_39 | NAYY 4x150 SE | 37 | 38 | 0.028999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2029-4_0_3_line_40 | NAYY 4x150 SE | 38 | 39 | 0.017088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2029-4_0_3_line_41 | NAYY 4x150 SE | 38 | 40 | 0.094218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2029-4_0_3_line_42 | NAYY 4x150 SE | 39 | 41 | 0.040031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2029-4_0_3_line_43 | NAYY 4x150 SE | 42 | 43 | 0.013887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2029-4_0_3_trafo_29 | 0.25 MVA 20/0.4 kV | 45 | 27 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2564890.4018 | 1185299.8122 | 2564888.1962 | 1185284.228 | 2564825.1413 | 1185230.792
1 | 2564879.939 | 1185307.6334 | 2564883.1878 | 1185303.3454 | 2564890.4018 | 1185299.8122
2 | 2564879.939 | 1185307.6334 | 2564869.7267 | 1185310.0059 | 2564863.7479 | 1185312.8394
3 | 2564863.7479 | 1185312.8394 | 2564839.7952 | 1185324.1913
4 | 2564823.2198 | 1185332.0468 | 2564839.7952 | 1185324.1913
5 | 2564795.7505 | 1185367.7277 | 2564799.9592 | 1185376.3804
6 | 2564795.7505 | 1185367.7277 | 2564803.5103 | 1185363.602
7 | 2564796.1563 | 1185345.947 | 2564803.5103 | 1185363.602
8 | 2564761.4417 | 1185361.6934 | 2564787.2543 | 1185350.5241 | 2564793.227 | 1185347.4539 | 2564796.1563 | 1185345.947
9 | 2564796.1563 | 1185345.947 | 2564810.3631 | 1185338.6502
10 | 2564761.4417 | 1185361.6934 | 2564757.3824 | 1185357.9264
11 | 2564761.4417 | 1185361.6934 | 2564756.3198 | 1185364.429
12 | 2564823.2198 | 1185332.0468 | 2564810.3631 | 1185338.6502
13 | 2564757.3824 | 1185357.9264 | 2564740.4156 | 1185342.2073
14 | 2564757.3824 | 1185357.9264 | 2564768.1352 | 1185352.7603
15 | 2564728.852 | 1185379.0972 | 2564738.9842 | 1185373.6878 | 2564756.3198 | 1185364.429
16 | 2564730.8127 | 1185333.3105 | 2564740.4156 | 1185342.2073
17 | 2564788.6746 | 1185342.8894 | 2564768.1352 | 1185352.7603
18 | 2564727.6035 | 1185379.7637 | 2564728.852 | 1185379.0972
19 | 2564788.6746 | 1185342.8894 | 2564782.7845 | 1185330.5202
20 | 2564781.9107 | 1185328.6851 | 2564782.7845 | 1185330.5202
21 | 2564777.895 | 1185320.252 | 2564781.9107 | 1185328.6851
22 | 2564740.0144 | 1185249.6156 | 2564758.9567 | 1185265.201
23 | 2564758.9567 | 1185265.201 | 2564736.2217 | 1185293.1722
24 | 2564740.0144 | 1185249.6156 | 2564724.8059 | 1185236.846
25 | 2564735.7495 | 1185293.7532 | 2564736.2217 | 1185293.1722
26 | 2564775.8163 | 1185315.8842 | 2564783.3564 | 1185307.3947
27 | 2564775.8163 | 1185315.8842 | 2564765.7034 | 1185306.65
28 | 2564777.895 | 1185320.252 | 2564777.4932 | 1185319.4095 | 2564775.8163 | 1185315.8842
29 | 2564759.0782 | 1185314.2487 | 2564765.7034 | 1185306.65
30 | 2564759.0782 | 1185314.2487 | 2564761.5325 | 1185316.3131
31 | 2564761.5325 | 1185316.3131 | 2564751.3811 | 1185327.805
32 | 2564759.0782 | 1185314.2487 | 2564735.7495 | 1185293.7532
33 | 2564750.3111 | 1185329.0162 | 2564751.3811 | 1185327.805
34 | 2564727.6035 | 1185379.7637 | 2564701.7194 | 1185393.5825
35 | 2564700.0718 | 1185394.4621 | 2564701.7194 | 1185393.5825
36 | 2564663.5015 | 1185425.3725 | 2564668.0244 | 1185424.9456 | 2564671.9564 | 1185422.6766 | 2564674.5751 | 1185418.9814 | 2564675.4187 | 1185414.5296 | 2564674.3243 | 1185410.1337 | 2564700.0718 | 1185394.4621
37 | 2564715.2929 | 1185318.9319 | 2564730.8127 | 1185333.3105
38 | 2564724.8059 | 1185236.846 | 2564707.0044 | 1185221.8992
39 | 2564703.9717 | 1185465.4991 | 2564724.482 | 1185485.9997
40 | 2564703.9717 | 1185465.4991 | 2564692.5391 | 1185453.7493 | 2564692.0129 | 1185453.2968
41 | 2564703.9717 | 1185465.4991 | 2564709.9479 | 1185463.0514 | 2564714.2456 | 1185460.6803 | 2564785.2089 | 1185417.919
42 | 2564663.5015 | 1185425.3725 | 2564673.9766 | 1185437.7839 | 2564692.0129 | 1185453.2968
43 | 2564715.2929 | 1185318.9319 | 2564704.6711 | 1185309.986

## bus_geodata
| x | y | coords
0 | 2564825.1413 | 1185230.792
1 | 2564890.4018 | 1185299.8122
2 | 2564879.939 | 1185307.6334
3 | 2564863.7479 | 1185312.8394
4 | 2564839.7952 | 1185324.1913
5 | 2564799.9592 | 1185376.3804
6 | 2564795.7505 | 1185367.7277
7 | 2564803.5103 | 1185363.602
8 | 2564796.1563 | 1185345.947
9 | 2564761.4417 | 1185361.6934
10 | 2564810.3631 | 1185338.6502
11 | 2564757.3824 | 1185357.9264
12 | 2564756.3198 | 1185364.429
13 | 2564823.2198 | 1185332.0468
14 | 2564740.4156 | 1185342.2073
15 | 2564768.1352 | 1185352.7603
16 | 2564728.852 | 1185379.0972
17 | 2564788.6746 | 1185342.8894
18 | 2564782.7846 | 1185330.5202
19 | 2564781.9107 | 1185328.6851
20 | 2564758.9567 | 1185265.201
21 | 2564740.0144 | 1185249.6156
22 | 2564736.2217 | 1185293.1722
23 | 2564783.3564 | 1185307.3947
24 | 2564775.8164 | 1185315.8842
25 | 2564777.895 | 1185320.252
26 | 2564765.7034 | 1185306.65
27 | 2564761.5325 | 1185316.3131
28 | 2564759.0782 | 1185314.2487
29 | 2564751.3811 | 1185327.805
30 | 2564750.3111 | 1185329.0162
31 | 2564727.6035 | 1185379.7637
32 | 2564701.7194 | 1185393.5825
33 | 2564700.0718 | 1185394.4621
34 | 2564730.8127 | 1185333.3105
35 | 2564724.8059 | 1185236.846
36 | 2564735.7495 | 1185293.7532
37 | 2564724.482 | 1185485.9997
38 | 2564703.9717 | 1185465.4991
39 | 2564692.0129 | 1185453.2968
40 | 2564785.2089 | 1185417.919
41 | 2564663.5015 | 1185425.3725
42 | 2564704.6711 | 1185309.986
43 | 2564715.2929 | 1185318.9319
44 | 2564707.0044 | 1185221.8992
45 | 2564759.0782 | 1185314.2487

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98611 | -0.097603 | 0.0071252 | 0.0017857
1 | 0.98713 | -0.09041 | 0 | 0
2 | 0.98727 | -0.089432 | 0 | 0
3 | 0.98744 | -0.088183 | 0.0038178 | 0.00095682
4 | 0.98786 | -0.085211 | 0.0021584 | 0.00054095
5 | 0.98867 | -0.079457 | 0.003396 | 0.00085111
6 | 0.98872 | -0.079123 | 0 | 0
7 | 0.98876 | -0.078818 | 0.0028825 | 0.00072242
8 | 0.98894 | -0.077592 | 0 | 0
9 | 0.99037 | -0.067471 | 0 | 0
10 | 0.98848 | -0.080814 | 0.00664 | 0.0016641
11 | 0.99081 | -0.064374 | 0 | 0
12 | 0.99013 | -0.069186 | 0.010288 | 0.0025784
13 | 0.98821 | -0.082751 | 0 | 0
14 | 0.99053 | -0.066364 | 0.0054855 | 0.0013748
15 | 0.9919 | -0.056696 | 0 | 0
16 | 0.98929 | -0.075127 | 0.0040391 | 0.0010123
17 | 0.99398 | -0.042077 | 0 | 0
18 | 0.99523 | -0.033296 | 0.020259 | 0.0050774
19 | 0.99548 | -0.031581 | 0.017375 | 0.0043546
20 | 0.99596 | -0.028271 | 0 | 0
21 | 0.99535 | -0.032603 | 0 | 0
22 | 0.99687 | -0.021904 | 0.041608 | 0.010428
23 | 0.99744 | -0.017864 | 0.0061186 | 0.0015335
24 | 0.99754 | -0.017167 | 0 | 0
25 | 0.99683 | -0.022077 | 0 | 0
26 | 0.99859 | -0.0098071 | 0.026191 | 0.006564
27 | 1 | 0 | -0.22177 | -0.055525
28 | 0.99956 | -0.0030798 | 0 | 0
29 | 0.9994 | -0.0041687 | 0.015951 | 0.0039976
30 | 0.99938 | -0.0043508 | 0.011273 | 0.0028252
31 | 0.98926 | -0.075339 | 0.0014242 | 0.00035694
32 | 0.9887 | -0.079308 | 0.0030973 | 0.00077625
33 | 0.98867 | -0.079502 | 0 | 0
34 | 0.99047 | -0.06676 | 0.0017602 | 0.00044114
35 | 0.99485 | -0.036119 | 0.0087845 | 0.0022016
36 | 0.99693 | -0.021459 | 0 | 0
37 | 0.98685 | -0.092426 | 0.0054372 | 0.0013627
38 | 0.98707 | -0.09081 | 0 | 0
39 | 0.98731 | -0.089142 | 0.00061819 | 0.00015493
40 | 0.98652 | -0.094755 | 0.0040816 | 0.0010229
41 | 0.98789 | -0.084983 | 0 | 0
42 | 0.99041 | -0.067191 | 0.0012083 | 0.00030283
43 | 0.99043 | -0.06702 | 0 | 0
44 | 0.99455 | -0.038178 | 0.0087796 | 0.0022004
45 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0071252 | -0.0017857 | 0.0071323 | 0.0017872 | 7.097e-06 | 1.4731e-06 | 0.010752 | 0.010751 | 0.010752 | 0.98611 | -0.097603 | 0.98713 | -0.09041 | 3.9821
1 | -0.0071323 | -0.0017872 | 0.0071332 | 0.0017874 | 9.657e-07 | 2.0024e-07 | 0.010751 | 0.010751 | 0.010751 | 0.98713 | -0.09041 | 0.98727 | -0.089432 | 3.9819
2 | -0.0071332 | -0.0017874 | 0.0071345 | 0.0017877 | 1.2334e-06 | 2.5567e-07 | 0.010751 | 0.010751 | 0.010751 | 0.98727 | -0.089432 | 0.98744 | -0.088183 | 3.9819
3 | -0.010952 | -0.0027445 | 0.010957 | 0.0027459 | 4.5053e-06 | 1.3936e-06 | 0.016504 | 0.016504 | 0.016504 | 0.98744 | -0.088183 | 0.98786 | -0.085211 | 6.1127
4 | -0.013115 | -0.0032868 | 0.01312 | 0.0032883 | 4.467e-06 | 1.4831e-06 | 0.019755 | 0.019755 | 0.019755 | 0.98786 | -0.085211 | 0.98821 | -0.082751 | 7.3168
5 | -0.003396 | -0.00085111 | 0.0033961 | 0.00085105 | 1.5685e-07 | -6.3069e-08 | 0.0051112 | 0.0051111 | 0.0051112 | 0.98867 | -0.079457 | 0.98872 | -0.079123 | 1.893
6 | -0.0033961 | -0.00085105 | 0.0033963 | 0.00085099 | 1.4326e-07 | -5.7616e-08 | 0.0051111 | 0.0051111 | 0.0051111 | 0.98872 | -0.079123 | 0.98876 | -0.078818 | 1.893
7 | -0.0062788 | -0.0015734 | 0.0062798 | 0.0015736 | 1.0655e-06 | 1.6447e-07 | 0.009449 | 0.0094489 | 0.009449 | 0.98876 | -0.078818 | 0.98894 | -0.077592 | 3.4996
8 | -0.026052 | -0.0065304 | 0.026088 | 0.006544 | 3.6565e-05 | 1.3574e-05 | 0.0392 | 0.039199 | 0.0392 | 0.98894 | -0.077592 | 0.99037 | -0.067471 | 14.5184
9 | 0.019772 | 0.0049568 | -0.019763 | -0.0049536 | 8.8209e-06 | 3.1878e-06 | 0.029751 | 0.029751 | 0.029751 | 0.98894 | -0.077592 | 0.98848 | -0.080814 | 11.0188
10 | -0.055124 | -0.013824 | 0.055147 | 0.013833 | 2.3672e-05 | 9.0334e-06 | 0.082825 | 0.082825 | 0.082825 | 0.99037 | -0.067471 | 0.99081 | -0.064374 | 30.676
11 | 0.029035 | 0.0072797 | -0.029028 | -0.0072771 | 6.8961e-06 | 2.5776e-06 | 0.043626 | 0.043626 | 0.043626 | 0.99037 | -0.067471 | 0.99013 | -0.069186 | 16.1578
12 | 0.013123 | 0.0032895 | -0.01312 | -0.0032883 | 3.5198e-06 | 1.1685e-06 | 0.019755 | 0.019755 | 0.019755 | 0.98848 | -0.080814 | 0.98821 | -0.082751 | 7.3168
13 | 0.0084565 | 0.0021188 | -0.0084542 | -0.0021182 | 2.3279e-06 | 5.9753e-07 | 0.0127 | 0.0127 | 0.0127 | 0.99081 | -0.064374 | 0.99053 | -0.066364 | 4.7038
14 | -0.063604 | -0.015951 | 0.063672 | 0.015977 | 6.7771e-05 | 2.5912e-05 | 0.095525 | 0.095525 | 0.095525 | 0.99081 | -0.064374 | 0.9919 | -0.056696 | 35.3798
15 | 0.01874 | 0.0046986 | -0.018725 | -0.0046931 | 1.5413e-05 | 5.528e-06 | 0.028164 | 0.028165 | 0.028165 | 0.99013 | -0.069186 | 0.98929 | -0.075127 | 10.4313
16 | 0.0029687 | 0.00074344 | -0.0029685 | -0.00074355 | 1.6246e-07 | -1.0601e-07 | 0.0044595 | 0.0044596 | 0.0044596 | 0.99053 | -0.066364 | 0.99047 | -0.06676 | 1.6517
17 | -0.063672 | -0.015977 | 0.063801 | 0.016027 | 0.00012945 | 4.9496e-05 | 0.095525 | 0.095525 | 0.095525 | 0.9919 | -0.056696 | 0.99398 | -0.042077 | 35.3797
18 | 0.014686 | 0.0036808 | -0.014685 | -0.0036807 | 4.3092e-07 | 1.4757e-07 | 0.022089 | 0.022089 | 0.022089 | 0.98929 | -0.075127 | 0.98926 | -0.075339 | 8.1812
19 | -0.063801 | -0.016027 | 0.063879 | 0.016057 | 7.8008e-05 | 2.9825e-05 | 0.095525 | 0.095525 | 0.095525 | 0.99398 | -0.042077 | 0.99523 | -0.033296 | 35.3797
20 | -0.084138 | -0.021134 | 0.084158 | 0.021142 | 2.0076e-05 | 7.6953e-06 | 0.12582 | 0.12582 | 0.12582 | 0.99523 | -0.033296 | 0.99548 | -0.031581 | 46.5982
21 | -0.10153 | -0.025496 | 0.10167 | 0.025548 | 0.00013428 | 5.1525e-05 | 0.15179 | 0.15179 | 0.15179 | 0.99548 | -0.031581 | 0.99683 | -0.022077 | 56.2173
22 | 0.017586 | 0.0044094 | -0.017575 | -0.0044057 | 1.055e-05 | 3.7392e-06 | 0.026275 | 0.026275 | 0.026275 | 0.99596 | -0.028271 | 0.99535 | -0.032603 | 9.7314
23 | -0.017586 | -0.0044094 | 0.017601 | 0.0044149 | 1.5528e-05 | 5.5026e-06 | 0.026275 | 0.026274 | 0.026275 | 0.99596 | -0.028271 | 0.99687 | -0.021904 | 9.7313
24 | 0.017575 | 0.0044057 | -0.017567 | -0.0044026 | 8.5548e-06 | 3.0323e-06 | 0.026275 | 0.026275 | 0.026275 | 0.99535 | -0.032603 | 0.99485 | -0.036119 | 9.7314
25 | -0.05921 | -0.014843 | 0.059213 | 0.014844 | 3.6493e-06 | 1.3938e-06 | 0.088383 | 0.088383 | 0.088383 | 0.99687 | -0.021904 | 0.99693 | -0.021459 | 32.7344
26 | -0.0061186 | -0.0015335 | 0.0061192 | 0.0015336 | 5.9034e-07 | 7.8839e-08 | 0.009128 | 0.009128 | 0.009128 | 0.99744 | -0.017864 | 0.99754 | -0.017167 | 3.3807
27 | -0.10786 | -0.027108 | 0.10797 | 0.02715 | 0.00011064 | 4.2194e-05 | 0.16091 | 0.16091 | 0.16091 | 0.99754 | -0.017167 | 0.99859 | -0.0098071 | 29.799
28 | 0.10174 | 0.025575 | -0.10167 | -0.025548 | 6.9524e-05 | 2.6677e-05 | 0.15179 | 0.15179 | 0.15179 | 0.99754 | -0.017167 | 0.99683 | -0.022077 | 56.2173
29 | -0.13416 | -0.033714 | 0.13428 | 0.033762 | 0.00012574 | 4.8098e-05 | 0.19994 | 0.19994 | 0.19994 | 0.99859 | -0.0098071 | 0.99956 | -0.0030798 | 37.0262
30 | 0.19373 | 0.048696 | -0.19365 | -0.048664 | 8.305e-05 | 3.1858e-05 | 0.28832 | 0.28832 | 0.28832 | 1 | 0 | 0.99956 | -0.0030798 | 53.3933
31 | 0.027239 | 0.0068288 | -0.027224 | -0.0068229 | 1.572e-05 | 5.8451e-06 | 0.040533 | 0.040534 | 0.040534 | 1 | 0 | 0.9994 | -0.0041687 | 15.0124
32 | 0.059364 | 0.014902 | -0.059213 | -0.014844 | 0.00015114 | 5.7724e-05 | 0.088383 | 0.088383 | 0.088383 | 0.99956 | -0.0030798 | 0.99693 | -0.021459 | 32.7344
33 | 0.011273 | 0.0028253 | -0.011273 | -0.0028252 | 2.841e-07 | 8.8094e-08 | 0.016785 | 0.016785 | 0.016785 | 0.9994 | -0.0041687 | 0.99938 | -0.0043508 | 6.2165
34 | 0.013261 | 0.0033237 | -0.013254 | -0.0033213 | 7.285e-06 | 2.4254e-06 | 0.019947 | 0.019947 | 0.019947 | 0.98926 | -0.075339 | 0.9887 | -0.079308 | 7.3878
35 | 0.010156 | 0.002545 | -0.010156 | -0.002545 | 2.723e-07 | 8.0779e-08 | 0.015286 | 0.015286 | 0.015286 | 0.9887 | -0.079308 | 0.98867 | -0.079502 | 5.6613
36 | 0.010156 | 0.002545 | -0.010148 | -0.0025427 | 7.7004e-06 | 2.2849e-06 | 0.015286 | 0.015286 | 0.015286 | 0.98867 | -0.079502 | 0.98789 | -0.084983 | 5.6614
37 | 0.0012084 | 0.0003024 | -0.0012083 | -0.00030266 | 4.3502e-08 | -2.5556e-07 | 0.0018152 | 0.0018153 | 0.0018153 | 0.99047 | -0.06676 | 0.99043 | -0.06702 | 0.67234
38 | 0.0087821 | 0.002201 | -0.0087796 | -0.0022004 | 2.5027e-06 | 6.6085e-07 | 0.013136 | 0.013136 | 0.013136 | 0.99485 | -0.036119 | 0.99455 | -0.038178 | 4.8651
39 | -0.0054372 | -0.0013627 | 0.0054384 | 0.0013628 | 1.2163e-06 | 9.7207e-08 | 0.0081985 | 0.0081984 | 0.0081985 | 0.98685 | -0.092426 | 0.98707 | -0.09081 | 3.0365
40 | -0.0095222 | -0.0023854 | 0.0095244 | 0.002386 | 2.1971e-06 | 6.2655e-07 | 0.014354 | 0.014354 | 0.014354 | 0.98707 | -0.09081 | 0.98731 | -0.089142 | 5.3164
41 | 0.0040838 | 0.0010226 | -0.0040816 | -0.0010229 | 2.2282e-06 | -3.4665e-07 | 0.006156 | 0.0061565 | 0.0061565 | 0.98707 | -0.09081 | 0.98652 | -0.094755 | 2.2802
42 | -0.010143 | -0.0025409 | 0.010148 | 0.0025427 | 5.8366e-06 | 1.7326e-06 | 0.015286 | 0.015286 | 0.015286 | 0.98731 | -0.089142 | 0.98789 | -0.084983 | 5.6615
43 | -0.0012083 | -0.00030283 | 0.0012083 | 0.00030266 | 2.8557e-08 | -1.6773e-07 | 0.0018154 | 0.0018153 | 0.0018154 | 0.99041 | -0.067191 | 0.99043 | -0.06702 | 0.67236

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22177 | 0.055525

## res_load
| p_mw | q_mvar
0 | 0.0071252 | 0.0017857
1 | 0.0038178 | 0.00095682
2 | 0.0021584 | 0.00054095
3 | 0.003396 | 0.00085111
4 | 0.0028825 | 0.00072242
5 | 0.00664 | 0.0016641
6 | 0.010288 | 0.0025784
7 | 0.0054855 | 0.0013748
8 | 0.0040391 | 0.0010123
9 | 0.020259 | 0.0050774
10 | 0.017375 | 0.0043546
11 | 0.041608 | 0.010428
12 | 0.0061186 | 0.0015335
13 | 0.026191 | 0.006564
14 | 0.015951 | 0.0039976
15 | 0.011273 | 0.0028252
16 | 0.0014242 | 0.00035694
17 | 0.0030973 | 0.00077625
18 | 0.0017602 | 0.00044114
19 | 0.0087845 | 0.0022016
20 | 0.0054372 | 0.0013627
21 | 0.00061819 | 0.00015493
22 | 0.0040816 | 0.0010229
23 | 0.0012083 | 0.00030283
24 | 0.0087796 | 0.0022004

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1