## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2029-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2029-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2029-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2029-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2029-5_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2029-5_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2029-5_0_4_node_42 | 0.4 | n |  | TRUE
7 | bus_LV_2029-5_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_2029-5_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_2029-5_0_4_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_2029-5_0_4_node_40 | 0.4 | n |  | TRUE
11 | bus_LV_2029-5_0_4_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_2029-5_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2029-5_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_2029-5_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2029-5_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2029-5_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2029-5_0_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_2029-5_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2029-5_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2029-5_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_2029-5_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_2029-5_0_4_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_2029-5_0_4_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_2029-5_0_4_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_2029-5_0_4_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_2029-5_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_2029-5_0_4_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_2029-5_0_4_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_2029-5_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2029-5_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_2029-5_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_2029-5_0_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_2029-5_0_4_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_2029-5_0_4_node_50 | 0.4 | n |  | TRUE
35 | bus_LV_2029-5_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_2029-5_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_2029-5_0_4_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_2029-5_0_4_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_2029-5_0_4_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_2029-5_0_4_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_2029-5_0_4_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_2029-5_0_4_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_2029-5_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_2029-5_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_2029-5_0_4_node_59 | 0.4 | n |  | TRUE
46 | bus_LV_2029-5_0_4_node_58 | 0.4 | n |  | TRUE
47 | bus_LV_2029-5_0_4_node_60 | 0.4 | n |  | TRUE
48 | bus_LV_2029-5_0_4_node_57 | 0.4 | n |  | TRUE
49 | bus_LV_2029-5_0_4_node_48 | 0.4 | n |  | TRUE
50 | bus_LV_2029-5_0_4_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_2029-5_0_4_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_2029-5_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_2029-5_0_4_node_54 | 0.4 | n |  | TRUE
54 | bus_LV_2029-5_0_4_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_2029-5_0_4_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_2029-5_0_4_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_2029-5_0_4_node_65 | 0.4 | n |  | TRUE
58 | bus_LV_2029-5_0_4_node_52 | 0.4 | n |  | TRUE
59 | bus_LV_2029-5_0_4_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_2029-5_0_4_node_64 | 0.4 | n |  | TRUE
61 | bus_LV_2029-5_0_4_node_63 | 0.4 | n |  | TRUE
62 | bus_LV_2029-5_0_4_node_61 | 0.4 | n |  | TRUE
63 | bus_LV_2029-5_0_4_node_62 | 0.4 | n |  | TRUE
64 | bus_LV_2029-5_0_4_node_66 | 0.4 | n |  | TRUE
65 | bus_LV_2029-5_0_4_node_67 | 0.4 | n |  | TRUE
66 | bus_LV_2029-5_0_4_node_68 | 0.4 | n |  | TRUE
67 | bus_MV_477_0_node_29 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2029-5_0_4_load_0 | 0 | 0.0066888 | 0.0016764 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2029-5_0_4_load_3 | 3 | 0.0016186 | 0.00040567 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2029-5_0_4_load_42 | 6 | 0.00056086 | 0.00014056 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2029-5_0_4_load_10 | 8 | 0.010587 | 0.0026533 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2029-5_0_4_load_12 | 9 | 0.0046986 | 0.0011776 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2029-5_0_4_load_40 | 10 | 0.0014278 | 0.00035785 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2029-5_0_4_load_18 | 11 | 0.0022484 | 0.00056349 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2029-5_0_4_load_9 | 12 | 0.019891 | 0.0049852 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2029-5_0_4_load_6 | 13 | 0.015102 | 0.0037849 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2029-5_0_4_load_7 | 14 | 0.0040599 | 0.0010175 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2029-5_0_4_load_11 | 16 | 0.0032181 | 0.00080653 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2029-5_0_4_load_16 | 17 | 0.0071526 | 0.0017926 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2029-5_0_4_load_14 | 18 | 0.01243 | 0.0031153 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2029-5_0_4_load_15 | 19 | 0.015251 | 0.0038222 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2029-5_0_4_load_19 | 20 | 0.0013026 | 0.00032647 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2029-5_0_4_load_20 | 21 | 0.00068476 | 0.00017162 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2029-5_0_4_load_21 | 22 | 0.0014467 | 0.00036257 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2029-5_0_4_load_33 | 23 | 0.0066084 | 0.0016562 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2029-5_0_4_load_34 | 24 | 0.0023169 | 0.00058067 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2029-5_0_4_load_35 | 25 | 0.0026291 | 0.00065891 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2029-5_0_4_load_32 | 27 | 0.0031543 | 0.00079054 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2029-5_0_4_load_29 | 28 | 0.0030161 | 0.00075591 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2029-5_0_4_load_23 | 29 | 0.0014607 | 0.00036607 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2029-5_0_4_load_24 | 30 | 0.0021397 | 0.00053626 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2029-5_0_4_load_26 | 31 | 0.0027702 | 0.00069427 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2029-5_0_4_load_27 | 32 | 0.0043726 | 0.0010959 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2029-5_0_4_load_49 | 33 | 0.0029429 | 0.00073755 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2029-5_0_4_load_50 | 34 | 0.0014948 | 0.00037464 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2029-5_0_4_load_28 | 35 | 0.0020313 | 0.0005091 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2029-5_0_4_load_30 | 36 | 0.0033802 | 0.00084716 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2029-5_0_4_load_31 | 37 | 0.0083236 | 0.0020861 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2029-5_0_4_load_43 | 38 | 0.0019048 | 0.00047738 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2029-5_0_4_load_47 | 39 | 0.0017556 | 0.00044 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2029-5_0_4_load_36 | 40 | 0.0011979 | 0.00030022 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2029-5_0_4_load_37 | 41 | 0.0023669 | 0.00059321 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2029-5_0_4_load_41 | 44 | 0.0045436 | 0.0011387 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2029-5_0_4_load_58 | 46 | 0.0043964 | 0.0011018 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2029-5_0_4_load_60 | 47 | 0.0050087 | 0.0012553 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2029-5_0_4_load_57 | 48 | 0.0050786 | 0.0012728 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2029-5_0_4_load_48 | 49 | 0.0024553 | 0.00061535 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2029-5_0_4_load_44 | 50 | 0.001849 | 0.0004634 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2029-5_0_4_load_45 | 51 | 0.0018111 | 0.00045389 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2029-5_0_4_load_54 | 53 | 0.006492 | 0.0016271 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2029-5_0_4_load_55 | 54 | 0.0041513 | 0.0010404 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2029-5_0_4_load_53 | 55 | 0.0016733 | 0.00041936 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2029-5_0_4_load_56 | 56 | 0.0056413 | 0.0014139 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2029-5_0_4_load_65 | 57 | 0.0013966 | 0.00035001 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2029-5_0_4_load_52 | 58 | 0.0022084 | 0.00055349 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2029-5_0_4_load_64 | 60 | 0.0040924 | 0.0010257 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2029-5_0_4_load_63 | 61 | 0.0031421 | 0.00078749 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2029-5_0_4_load_61 | 62 | 0.0038187 | 0.00095706 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2029-5_0_4_load_62 | 63 | 0.0028414 | 0.00071213 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2029-5_0_4_load_66 | 64 | 0.0020636 | 0.00051718 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2029-5_0_4_load_68 | 66 | 0.0033917 | 0.00085004 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 46 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2029-5_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.057752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_2029-5_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.042401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_2029-5_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.033378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2029-5_0_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.059459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_2029-5_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.042804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_2029-5_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.034306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_2029-5_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.017987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2029-5_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.023837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2029-5_0_4_line_8 | NAYY 4x150 SE | 5 | 9 | 0.019141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2029-5_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.0031722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_2029-5_0_4_line_10 | NAYY 4x150 SE | 7 | 11 | 0.017566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2029-5_0_4_line_11 | NAYY 4x150 SE | 8 | 12 | 0.010802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2029-5_0_4_line_12 | NAYY 4x150 SE | 10 | 42 | 0.025242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_2029-5_0_4_line_13 | NAYY 4x150 SE | 11 | 17 | 0.030765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2029-5_0_4_line_14 | NAYY 4x150 SE | 12 | 15 | 0.017599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2029-5_0_4_line_15 | NAYY 4x150 SE | 13 | 14 | 0.0049968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2029-5_0_4_line_16 | NAYY 4x150 SE | 14 | 15 | 0.028423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2029-5_0_4_line_17 | NAYY 4x150 SE | 15 | 16 | 0.055732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2029-5_0_4_line_18 | NAYY 4x150 SE | 17 | 18 | 0.019017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2029-5_0_4_line_19 | NAYY 4x150 SE | 18 | 19 | 0.040959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2029-5_0_4_line_20 | NAYY 4x150 SE | 20 | 21 | 0.025441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2029-5_0_4_line_21 | NAYY 4x150 SE | 21 | 22 | 0.0071395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2029-5_0_4_line_22 | NAYY 4x150 SE | 22 | 26 | 0.044602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2029-5_0_4_line_23 | NAYY 4x150 SE | 23 | 24 | 0.038474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2029-5_0_4_line_24 | NAYY 4x150 SE | 23 | 25 | 0.040264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2029-5_0_4_line_25 | NAYY 4x150 SE | 24 | 38 | 0.0027956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2029-5_0_4_line_26 | NAYY 4x150 SE | 25 | 37 | 0.016597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2029-5_0_4_line_27 | NAYY 4x150 SE | 26 | 29 | 0.015475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2029-5_0_4_line_28 | NAYY 4x150 SE | 26 | 30 | 0.019979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2029-5_0_4_line_29 | NAYY 4x150 SE | 27 | 28 | 0.047431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2029-5_0_4_line_30 | NAYY 4x150 SE | 28 | 36 | 0.030368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2029-5_0_4_line_31 | NAYY 4x150 SE | 28 | 35 | 0.0088224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2029-5_0_4_line_32 | NAYY 4x150 SE | 30 | 31 | 0.030792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2029-5_0_4_line_33 | NAYY 4x150 SE | 31 | 32 | 0.0038791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2029-5_0_4_line_34 | NAYY 4x150 SE | 32 | 35 | 0.029557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2029-5_0_4_line_35 | NAYY 4x150 SE | 33 | 34 | 0.033748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2029-5_0_4_line_36 | NAYY 4x150 SE | 34 | 59 | 0.043923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2029-5_0_4_line_37 | NAYY 4x150 SE | 36 | 37 | 0.00013993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2029-5_0_4_line_38 | NAYY 4x150 SE | 38 | 39 | 0.022671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2029-5_0_4_line_39 | NAYY 4x150 SE | 39 | 49 | 0.010396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2029-5_0_4_line_40 | NAYY 4x150 SE | 40 | 41 | 0.049375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_2029-5_0_4_line_41 | NAYY 4x150 SE | 40 | 42 | 0.024249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_2029-5_0_4_line_42 | NAYY 4x150 SE | 41 | 43 | 0.014439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_2029-5_0_4_line_43 | NAYY 4x150 SE | 42 | 44 | 0.040972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2029-5_0_4_line_44 | NAYY 4x150 SE | 43 | 45 | 0.016127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2029-5_0_4_line_45 | NAYY 4x150 SE | 43 | 46 | 0.026572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_2029-5_0_4_line_46 | NAYY 4x150 SE | 45 | 47 | 0.0077128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2029-5_0_4_line_47 | NAYY 4x150 SE | 46 | 48 | 0.0088211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2029-5_0_4_line_48 | NAYY 4x150 SE | 47 | 62 | 0.02264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2029-5_0_4_line_49 | NAYY 4x150 SE | 48 | 56 | 0.029911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2029-5_0_4_line_50 | NAYY 4x150 SE | 49 | 58 | 0.014265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2029-5_0_4_line_51 | NAYY 4x150 SE | 50 | 51 | 0.053357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2029-5_0_4_line_52 | NAYY 4x150 SE | 51 | 52 | 0.051678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2029-5_0_4_line_53 | NAYY 4x150 SE | 52 | 53 | 0.037151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2029-5_0_4_line_54 | NAYY 4x150 SE | 52 | 54 | 0.025886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2029-5_0_4_line_55 | NAYY 4x150 SE | 52 | 55 | 0.01618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2029-5_0_4_line_56 | NAYY 4x150 SE | 53 | 56 | 0.0074897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2029-5_0_4_line_57 | NAYY 4x150 SE | 54 | 57 | 0.019448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2029-5_0_4_line_58 | NAYY 4x150 SE | 55 | 58 | 0.01587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2029-5_0_4_line_59 | NAYY 4x150 SE | 57 | 59 | 0.0226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2029-5_0_4_line_60 | NAYY 4x150 SE | 59 | 60 | 0.034914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2029-5_0_4_line_61 | NAYY 4x150 SE | 60 | 61 | 0.020102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2029-5_0_4_line_62 | NAYY 4x150 SE | 62 | 63 | 0.033162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2029-5_0_4_line_63 | NAYY 4x150 SE | 63 | 64 | 0.011164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2029-5_0_4_line_64 | NAYY 4x150 SE | 64 | 65 | 0.035887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2029-5_0_4_line_65 | NAYY 4x150 SE | 65 | 66 | 0.023541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2029-5_0_4_trafo_58 | 0.25 MVA 20/0.4 kV | 67 | 46 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2564941.5388 | 1185326.704 | 2564969.2758 | 1185326.0521 | 2564999.1259 | 1185322.9823
1 | 2565041.0495 | 1185316.7044 | 2565006.7624 | 1185322.197 | 2564999.1259 | 1185322.9823
2 | 2564941.5388 | 1185326.704 | 2564953.1927 | 1185357.9856
3 | 2564909.1773 | 1185288.4292 | 2564909.3793 | 1185295.5206 | 2564909.2915 | 1185303.959 | 2564911.6814 | 1185315.8513 | 2564923.1075 | 1185320.0309 | 2564934.7048 | 1185324.7542 | 2564941.5388 | 1185326.704
4 | 2565041.0495 | 1185316.7044 | 2565046.42 | 1185326.7784 | 2565061.189 | 1185354.4956
5 | 2564909.1773 | 1185288.4292 | 2564928.1917 | 1185274.8214 | 2564938.1345 | 1185270.2958
6 | 2565061.189 | 1185354.4956 | 2565070.0417 | 1185370.1633
7 | 2565061.189 | 1185354.4956 | 2565041.2628 | 1185367.5786
8 | 2565061.189 | 1185354.4956 | 2565078.5746 | 1185346.4877
9 | 2564938.1345 | 1185270.2958 | 2564941.0217 | 1185268.9816
10 | 2565070.0417 | 1185370.1633 | 2565085.1097 | 1185361.1353
11 | 2565032.2329 | 1185373.5074 | 2565041.2628 | 1185367.5786
12 | 2564963.9953 | 1185258.5248 | 2564941.0217 | 1185268.9816
13 | 2565085.1097 | 1185361.1353 | 2565111.5008 | 1185345.3231
14 | 2565017.5215 | 1185383.1665 | 2565032.2329 | 1185373.5074
15 | 2564989.5867 | 1185401.5121 | 2564993.7633 | 1185398.7692
16 | 2565017.5215 | 1185383.1665 | 2564993.7633 | 1185398.7692
17 | 2565017.5215 | 1185383.1665 | 2564997.1117 | 1185354.0038 | 2564979.7371 | 1185364.1829
18 | 2565129.6136 | 1185340.387 | 2565115.6863 | 1185342.8154 | 2565111.5008 | 1185345.3231
19 | 2565129.6136 | 1185340.387 | 2565147.6147 | 1185337.2483 | 2565150.4009 | 1185333.43 | 2565149.4803 | 1185315.4938
20 | 2564922.1416 | 1184974.0718 | 2564929.5263 | 1184998.4172
21 | 2564922.1416 | 1184974.0718 | 2564920.0692 | 1184967.2397
22 | 2564907.1228 | 1184924.5584 | 2564920.0692 | 1184967.2397
23 | 2564886.9505 | 1185060.9181 | 2564918.0206 | 1185083.6094
24 | 2564886.9505 | 1185060.9181 | 2564908.2883 | 1185026.7727
25 | 2564918.0206 | 1185083.6094 | 2564920.2782 | 1185085.2582
26 | 2564908.2883 | 1185026.7727 | 2564898.462 | 1185013.3977
27 | 2564907.1228 | 1184924.5584 | 2564921.5864 | 1184919.0558
28 | 2564907.1228 | 1184924.5584 | 2564888.2025 | 1184930.9753
29 | 2564844.7069 | 1185020.0493 | 2564880.3996 | 1184988.8119
30 | 2564880.3996 | 1184988.8119 | 2564898.3792 | 1185013.2849
31 | 2564880.3996 | 1184988.8119 | 2564875.1762 | 1184981.702
32 | 2564888.2025 | 1184930.9753 | 2564874.4997 | 1184935.6227 | 2564869.834 | 1184940.3971 | 2564868.2595 | 1184949.9149
33 | 2564868.2595 | 1184949.9149 | 2564867.6452 | 1184953.6281 | 2564867.6538 | 1184953.7432
34 | 2564867.6538 | 1184953.7432 | 2564868.7542 | 1184968.3072 | 2564872.7748 | 1184978.4334 | 2564875.1762 | 1184981.702
35 | 2564992.4713 | 1185045.2098 | 2565017.8248 | 1185067.4839
36 | 2565041.771 | 1185103.6422 | 2565035.2249 | 1185088.3502 | 2565023.3321 | 1185072.3223 | 2565017.8248 | 1185067.4839
37 | 2564898.3792 | 1185013.2849 | 2564898.462 | 1185013.3977
38 | 2564920.2782 | 1185085.2582 | 2564924.5935 | 1185088.4098 | 2564938.6357 | 1185098.5613
39 | 2564947.0607 | 1185104.652 | 2564938.6357 | 1185098.5613
40 | 2564986.6641 | 1185249.913 | 2564992.5581 | 1185247.6738 | 2565031.3199 | 1185228.8967
41 | 2564963.9953 | 1185258.5248 | 2564986.6641 | 1185249.913
42 | 2565044.3143 | 1185222.6018 | 2565031.3199 | 1185228.8967
43 | 2564963.9953 | 1185258.5248 | 2564960.2611 | 1185251.6208 | 2564956.8972 | 1185245.4039 | 2564935.0118 | 1185231.2666
44 | 2565044.3143 | 1185222.6018 | 2565056.7394 | 1185212.2792
45 | 2565044.3143 | 1185222.6018 | 2565037.5687 | 1185221.4296 | 2565026.5944 | 1185205.0392
46 | 2565056.7394 | 1185212.2792 | 2565064.4329 | 1185212.8252
47 | 2565021.6866 | 1185197.7094 | 2565026.5944 | 1185205.0392
48 | 2565064.4329 | 1185212.8252 | 2565066.4357 | 1185212.9673 | 2565077.9514 | 1185210.2652 | 2565086.0963 | 1185206.9233
49 | 2565005.5301 | 1185172.5373 | 2565020.5229 | 1185195.9713 | 2565021.6866 | 1185197.7094
50 | 2564947.0607 | 1185104.652 | 2564958.6208 | 1185113.0092
51 | 2564882.7718 | 1185131.6324 | 2564894.3322 | 1185140.1818 | 2564914.2315 | 1185147.202 | 2564930.8144 | 1185148.3385 | 2564932.0665 | 1185148.2446
52 | 2564981.472 | 1185134.9343 | 2564950.5873 | 1185146.855 | 2564932.0665 | 1185148.2446
53 | 2564981.472 | 1185134.9343 | 2565001.4937 | 1185166.2283
54 | 2564981.472 | 1185134.9343 | 2565004.4487 | 1185123.0106
55 | 2564981.472 | 1185134.9343 | 2564972.9941 | 1185123.4 | 2564971.4824 | 1185122.3071
56 | 2565005.5301 | 1185172.5373 | 2565001.4937 | 1185166.2283
57 | 2565004.4487 | 1185123.0106 | 2565021.7108 | 1185114.0524
58 | 2564971.4824 | 1185122.3071 | 2564958.6208 | 1185113.0092
59 | 2565041.771 | 1185103.6422 | 2565021.7108 | 1185114.0524
60 | 2565041.771 | 1185103.6422 | 2565051.2374 | 1185126.2989 | 2565054.1634 | 1185136.2361
61 | 2565054.1634 | 1185136.2361 | 2565059.8415 | 1185155.5197
62 | 2565086.0963 | 1185206.9233 | 2565100.0229 | 1185201.2092 | 2565115.5575 | 1185191.9033
63 | 2565115.5575 | 1185191.9033 | 2565123.3554 | 1185187.2321 | 2565125.103 | 1185186.1153
64 | 2565155.3429 | 1185166.7901 | 2565125.103 | 1185186.1153
65 | 2565155.3429 | 1185166.7901 | 2565148.7011 | 1185144.2057

## bus_geodata
| x | y | coords
0 | 2564999.1259 | 1185322.9823
1 | 2564941.5388 | 1185326.704
2 | 2565041.0495 | 1185316.7044
3 | 2564953.1927 | 1185357.9856
4 | 2564909.1773 | 1185288.4292
5 | 2565061.189 | 1185354.4956
6 | 2564938.1345 | 1185270.2958
7 | 2565070.0417 | 1185370.1633
8 | 2565041.2628 | 1185367.5786
9 | 2565078.5746 | 1185346.4877
10 | 2564941.0217 | 1185268.9816
11 | 2565085.1097 | 1185361.1353
12 | 2565032.2329 | 1185373.5074
13 | 2564989.5867 | 1185401.5121
14 | 2564993.7633 | 1185398.7692
15 | 2565017.5215 | 1185383.1665
16 | 2564979.7371 | 1185364.1829
17 | 2565111.5008 | 1185345.3231
18 | 2565129.6136 | 1185340.387
19 | 2565149.4803 | 1185315.4938
20 | 2564929.5263 | 1184998.4172
21 | 2564922.1416 | 1184974.0718
22 | 2564920.0692 | 1184967.2397
23 | 2564886.9505 | 1185060.9181
24 | 2564918.0206 | 1185083.6094
25 | 2564908.2883 | 1185026.7727
26 | 2564907.1228 | 1184924.5584
27 | 2564844.7069 | 1185020.0493
28 | 2564880.3996 | 1184988.8119
29 | 2564921.5864 | 1184919.0558
30 | 2564888.2025 | 1184930.9753
31 | 2564868.2595 | 1184949.9149
32 | 2564867.6538 | 1184953.7432
33 | 2564992.4713 | 1185045.2098
34 | 2565017.8248 | 1185067.4839
35 | 2564875.1762 | 1184981.702
36 | 2564898.3792 | 1185013.2849
37 | 2564898.462 | 1185013.3977
38 | 2564920.2782 | 1185085.2582
39 | 2564938.6357 | 1185098.5613
40 | 2564986.6641 | 1185249.913
41 | 2565031.3199 | 1185228.8967
42 | 2564963.9953 | 1185258.5248
43 | 2565044.3143 | 1185222.6018
44 | 2564935.0118 | 1185231.2666
45 | 2565056.7394 | 1185212.2792
46 | 2565026.5944 | 1185205.0392
47 | 2565064.4329 | 1185212.8252
48 | 2565021.6866 | 1185197.7094
49 | 2564947.0607 | 1185104.652
50 | 2564882.7718 | 1185131.6324
51 | 2564932.0665 | 1185148.2446
52 | 2564981.472 | 1185134.9343
53 | 2565001.4937 | 1185166.2283
54 | 2565004.4487 | 1185123.0106
55 | 2564971.4824 | 1185122.3071
56 | 2565005.5301 | 1185172.5373
57 | 2565021.7108 | 1185114.0524
58 | 2564958.6208 | 1185113.0092
59 | 2565041.771 | 1185103.6422
60 | 2565054.1634 | 1185136.2361
61 | 2565059.8415 | 1185155.5197
62 | 2565086.0963 | 1185206.9233
63 | 2565115.5575 | 1185191.9033
64 | 2565125.103 | 1185186.1153
65 | 2565155.3429 | 1185166.7901
66 | 2565148.7011 | 1185144.2057
67 | 2565044.3143 | 1185222.6018

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98458 | -0.10717 | 0.0066888 | 0.0016764
1 | 0.98743 | -0.087138 | 0 | 0
2 | 0.98165 | -0.1279 | 0 | 0
3 | 0.98736 | -0.087691 | 0.0016186 | 0.00040567
4 | 0.99041 | -0.066301 | 0 | 0
5 | 0.97869 | -0.14895 | 0 | 0
6 | 0.99213 | -0.054334 | 0.00056086 | 0.00014056
7 | 0.97772 | -0.1559 | 0 | 0
8 | 0.97685 | -0.1621 | 0.010587 | 0.0026533
9 | 0.97856 | -0.14988 | 0.0046986 | 0.0011776
10 | 0.99229 | -0.053224 | 0.0014278 | 0.00035785
11 | 0.97676 | -0.16271 | 0.0022484 | 0.00056349
12 | 0.97618 | -0.16688 | 0.019891 | 0.0049852
13 | 0.9747 | -0.17752 | 0.015102 | 0.0037849
14 | 0.97481 | -0.17673 | 0.0040599 | 0.0010175
15 | 0.97561 | -0.17101 | 0 | 0
16 | 0.97535 | -0.17289 | 0.0032181 | 0.00080653
17 | 0.9752 | -0.17394 | 0.0071526 | 0.0017926
18 | 0.97442 | -0.17947 | 0.01243 | 0.0031153
19 | 0.97351 | -0.18605 | 0.015251 | 0.0038222
20 | 0.97577 | -0.17058 | 0.0013026 | 0.00032647
21 | 0.97581 | -0.17023 | 0.00068476 | 0.00017162
22 | 0.97583 | -0.17009 | 0.0014467 | 0.00036257
23 | 0.98137 | -0.1305 | 0.0066084 | 0.0016562
24 | 0.9838 | -0.11326 | 0.0023169 | 0.00058067
25 | 0.97922 | -0.14586 | 0.0026291 | 0.00065891
26 | 0.97606 | -0.16848 | 0 | 0
27 | 0.97718 | -0.16046 | 0.0031543 | 0.00079054
28 | 0.97739 | -0.1589 | 0.0030161 | 0.00075591
29 | 0.97603 | -0.16872 | 0.0014607 | 0.00036607
30 | 0.9762 | -0.16745 | 0.0021397 | 0.00053626
31 | 0.97652 | -0.16518 | 0.0027702 | 0.00069427
32 | 0.97657 | -0.16478 | 0.0043726 | 0.0010959
33 | 0.98812 | -0.082906 | 0.0029429 | 0.00073755
34 | 0.98826 | -0.08189 | 0.0014948 | 0.00037464
35 | 0.97718 | -0.16039 | 0.0020313 | 0.0005091
36 | 0.97839 | -0.1518 | 0.0033802 | 0.00084716
37 | 0.97839 | -0.15176 | 0.0083236 | 0.0020861
38 | 0.98399 | -0.11194 | 0.0019048 | 0.00047738
39 | 0.98556 | -0.10084 | 0.0017556 | 0.00044
40 | 0.99487 | -0.035335 | 0.0011979 | 0.00030022
41 | 0.99753 | -0.016997 | 0.0023669 | 0.00059321
42 | 0.99358 | -0.044279 | 0 | 0
43 | 0.99832 | -0.011539 | 0 | 0
44 | 0.99331 | -0.046162 | 0.0045436 | 0.0011387
45 | 0.99793 | -0.014308 | 0 | 0
46 | 1 | 0 | -0.22866 | -0.057607
47 | 0.99774 | -0.015632 | 0.0050087 | 0.0012553
48 | 0.9988 | -0.0082682 | 0.0050786 | 0.0012728
49 | 0.9863 | -0.095577 | 0.0024553 | 0.00061535
50 | 0.98952 | -0.072994 | 0.001849 | 0.0004634
51 | 0.98966 | -0.071988 | 0.0018111 | 0.00045389
52 | 0.98993 | -0.070057 | 0 | 0
53 | 0.99406 | -0.0412 | 0.006492 | 0.0016271
54 | 0.98929 | -0.074604 | 0.0041513 | 0.0010404
55 | 0.98862 | -0.079243 | 0.0016733 | 0.00041936
56 | 0.99496 | -0.034921 | 0.0056413 | 0.0014139
57 | 0.98892 | -0.0772 | 0.0013966 | 0.00035001
58 | 0.98738 | -0.088006 | 0.0022084 | 0.00055349
59 | 0.98854 | -0.079896 | 0 | 0
60 | 0.98818 | -0.082478 | 0.0040924 | 0.0010257
61 | 0.98809 | -0.083124 | 0.0031421 | 0.00078749
62 | 0.99735 | -0.018386 | 0.0038187 | 0.00095706
63 | 0.99695 | -0.021151 | 0.0028414 | 0.00071213
64 | 0.99687 | -0.021763 | 0.0020636 | 0.00051718
65 | 0.99669 | -0.022987 | 0 | 0
66 | 0.99658 | -0.023789 | 0.0033917 | 0.00085004
67 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.1022 | -0.025724 | 0.10248 | 0.025832 | 0.00028671 | 0.00010806 | 0.15449 | 0.15449 | 0.15449 | 0.98458 | -0.10717 | 0.98743 | -0.087138 | 19.0731
1 | 0.095509 | 0.024048 | -0.095233 | -0.023943 | 0.00027578 | 0.00010499 | 0.14438 | 0.14438 | 0.14438 | 0.98458 | -0.10717 | 0.98165 | -0.1279 | 26.7378
2 | 0.0016188 | 0.00040529 | -0.0016186 | -0.00040567 | 1.2393e-07 | -3.7926e-07 | 0.0024393 | 0.0024394 | 0.0024394 | 0.98743 | -0.087138 | 0.98736 | -0.087691 | 0.90349
3 | -0.1041 | -0.026237 | 0.10441 | 0.026352 | 0.00030457 | 0.00011486 | 0.15693 | 0.15693 | 0.15693 | 0.98743 | -0.087138 | 0.99041 | -0.066301 | 19.3742
4 | 0.095233 | 0.023943 | -0.094955 | -0.023837 | 0.00027841 | 0.000106 | 0.14438 | 0.14438 | 0.14438 | 0.98165 | -0.1279 | 0.97869 | -0.14895 | 26.7378
5 | -0.10441 | -0.026352 | 0.10458 | 0.026419 | 0.00017573 | 6.6262e-05 | 0.15693 | 0.15693 | 0.15693 | 0.99041 | -0.066301 | 0.99213 | -0.054334 | 19.3741
6 | 0.037243 | 0.0093538 | -0.037207 | -0.0093402 | 3.5996e-05 | 1.3619e-05 | 0.056631 | 0.056631 | 0.056631 | 0.97869 | -0.14895 | 0.97772 | -0.1559 | 20.9746
7 | 0.053013 | 0.013305 | -0.052916 | -0.013268 | 9.665e-05 | 3.6874e-05 | 0.080608 | 0.080608 | 0.080608 | 0.97869 | -0.14895 | 0.97685 | -0.1621 | 29.8549
8 | 0.0046993 | 0.0011776 | -0.0046986 | -0.0011776 | 6.0972e-07 | -5.9895e-09 | 0.0071448 | 0.0071448 | 0.0071448 | 0.97869 | -0.14895 | 0.97856 | -0.14988 | 2.6462
9 | -0.10514 | -0.026559 | 0.10516 | 0.026565 | 1.6424e-05 | 6.194e-06 | 0.15777 | 0.15777 | 0.15777 | 0.99213 | -0.054334 | 0.99229 | -0.053224 | 19.4779
10 | 0.037207 | 0.0093402 | -0.037171 | -0.0093269 | 3.5153e-05 | 1.33e-05 | 0.056631 | 0.056631 | 0.056631 | 0.97772 | -0.1559 | 0.97676 | -0.16271 | 20.9746
11 | 0.04233 | 0.010615 | -0.042302 | -0.010605 | 2.8027e-05 | 1.0644e-05 | 0.064482 | 0.064482 | 0.064482 | 0.97685 | -0.1621 | 0.97618 | -0.16688 | 23.8823
12 | -0.10659 | -0.026923 | 0.10672 | 0.026974 | 0.00013426 | 5.0658e-05 | 0.15991 | 0.15991 | 0.15991 | 0.99229 | -0.053224 | 0.99358 | -0.044279 | 19.7422
13 | 0.034923 | 0.0087634 | -0.034869 | -0.0087429 | 5.4347e-05 | 2.0518e-05 | 0.053206 | 0.053206 | 0.053206 | 0.97676 | -0.16271 | 0.9752 | -0.17394 | 19.7061
14 | 0.02241 | 0.0056193 | -0.022398 | -0.0056146 | 1.2816e-05 | 4.7093e-06 | 0.034162 | 0.034162 | 0.034162 | 0.97618 | -0.16688 | 0.97561 | -0.17101 | 12.6524
15 | -0.015102 | -0.0037849 | 0.015103 | 0.0037855 | 1.6573e-06 | 5.7514e-07 | 0.023055 | 0.023055 | 0.023055 | 0.9747 | -0.17752 | 0.97481 | -0.17673 | 8.5389
16 | -0.019163 | -0.004803 | 0.019179 | 0.0048084 | 1.5177e-05 | 5.4826e-06 | 0.029252 | 0.029252 | 0.029252 | 0.97481 | -0.17673 | 0.97561 | -0.17101 | 10.8342
17 | 0.0032189 | 0.00080616 | -0.0032181 | -0.00080653 | 8.3823e-07 | -3.7335e-07 | 0.0049094 | 0.0049096 | 0.0049096 | 0.97561 | -0.17101 | 0.97535 | -0.17289 | 1.8184
18 | 0.027716 | 0.0069503 | -0.027695 | -0.0069423 | 2.1225e-05 | 7.9264e-06 | 0.042292 | 0.042293 | 0.042293 | 0.9752 | -0.17394 | 0.97442 | -0.17947 | 15.6639
19 | 0.015265 | 0.003827 | -0.015251 | -0.0038222 | 1.3888e-05 | 4.8319e-06 | 0.023311 | 0.023311 | 0.023311 | 0.97442 | -0.17947 | 0.97351 | -0.18605 | 8.6336
20 | -0.0013026 | -0.00032647 | 0.0013027 | 0.00032618 | 6.2642e-08 | -2.9371e-07 | 0.0019865 | 0.0019864 | 0.0019865 | 0.97577 | -0.17058 | 0.97581 | -0.17023 | 0.73574
21 | -0.0019875 | -0.0004978 | 0.0019875 | 0.00049772 | 4.0917e-08 | -7.3454e-08 | 0.0030306 | 0.0030305 | 0.0030306 | 0.97581 | -0.17023 | 0.97583 | -0.17009 | 1.1224
22 | -0.0034342 | -0.00086029 | 0.0034349 | 0.00086003 | 7.6314e-07 | -2.6382e-07 | 0.0052365 | 0.0052363 | 0.0052365 | 0.97583 | -0.17009 | 0.97606 | -0.16848 | 1.9395
23 | -0.043466 | -0.010909 | 0.04357 | 0.010949 | 0.0001043 | 3.9626e-05 | 0.065911 | 0.065911 | 0.065911 | 0.98137 | -0.1305 | 0.9838 | -0.11326 | 24.4115
24 | 0.036857 | 0.0092528 | -0.036779 | -0.0092231 | 7.8485e-05 | 2.9679e-05 | 0.055891 | 0.055891 | 0.055891 | 0.98137 | -0.1305 | 0.97922 | -0.14586 | 20.7004
25 | -0.045887 | -0.011529 | 0.045895 | 0.011533 | 8.4056e-06 | 3.1974e-06 | 0.069415 | 0.069415 | 0.069415 | 0.9838 | -0.11326 | 0.98399 | -0.11194 | 25.7093
26 | 0.03415 | 0.0085642 | -0.034122 | -0.0085537 | 2.7892e-05 | 1.0519e-05 | 0.051896 | 0.051896 | 0.051896 | 0.97922 | -0.14586 | 0.97839 | -0.15176 | 19.2208
27 | 0.0014607 | 0.0003659 | -0.0014607 | -0.00036607 | 4.7884e-08 | -1.7499e-07 | 0.0022268 | 0.0022269 | 0.0022269 | 0.97606 | -0.16848 | 0.97603 | -0.16872 | 0.82476
28 | -0.0048956 | -0.0012259 | 0.0048963 | 0.0012259 | 6.9437e-07 | 1.732e-08 | 0.0074631 | 0.007463 | 0.0074631 | 0.97606 | -0.16848 | 0.9762 | -0.16745 | 2.7641
29 | -0.0031543 | -0.00079054 | 0.003155 | 0.00079021 | 6.8282e-07 | -3.3169e-07 | 0.0048033 | 0.0048031 | 0.0048033 | 0.97718 | -0.16046 | 0.97739 | -0.1589 | 1.779
30 | -0.022396 | -0.0056123 | 0.022418 | 0.0056204 | 2.2029e-05 | 8.0919e-06 | 0.034096 | 0.034096 | 0.034096 | 0.97739 | -0.1589 | 0.97839 | -0.1518 | 12.6282
31 | 0.016225 | 0.0040662 | -0.016222 | -0.004065 | 3.359e-06 | 1.1814e-06 | 0.024701 | 0.024701 | 0.024701 | 0.97739 | -0.1589 | 0.97718 | -0.16039 | 9.1486
32 | -0.007036 | -0.0017622 | 0.0070383 | 0.0017627 | 2.2099e-06 | 4.6488e-07 | 0.010725 | 0.010724 | 0.010725 | 0.9762 | -0.16745 | 0.97652 | -0.16518 | 3.9721
33 | -0.0098084 | -0.0024569 | 0.009809 | 0.0024571 | 5.4069e-07 | 1.5942e-07 | 0.014946 | 0.014946 | 0.014946 | 0.97652 | -0.16518 | 0.97657 | -0.16478 | 5.5354
34 | -0.014182 | -0.003553 | 0.01419 | 0.0035559 | 8.6113e-06 | 2.942e-06 | 0.021608 | 0.021608 | 0.021608 | 0.97657 | -0.16478 | 0.97718 | -0.16039 | 8.003
35 | -0.0029429 | -0.00073755 | 0.0029433 | 0.00073728 | 4.1358e-07 | -2.7329e-07 | 0.0044317 | 0.0044315 | 0.0044317 | 0.98812 | -0.082906 | 0.98826 | -0.08189 | 1.6414
36 | -0.0044381 | -0.0011119 | 0.0044393 | 0.0011118 | 1.2238e-06 | -9.2261e-08 | 0.0066823 | 0.0066821 | 0.0066823 | 0.98826 | -0.08189 | 0.98854 | -0.079896 | 2.4749
37 | -0.025798 | -0.0064676 | 0.025798 | 0.0064676 | 1.3443e-07 | 4.9946e-08 | 0.039237 | 0.039237 | 0.039237 | 0.97839 | -0.1518 | 0.97839 | -0.15176 | 14.5322
38 | -0.0478 | -0.01201 | 0.047874 | 0.012038 | 7.394e-05 | 2.815e-05 | 0.072296 | 0.072296 | 0.072296 | 0.98399 | -0.11194 | 0.98556 | -0.10084 | 26.7762
39 | -0.04963 | -0.012478 | 0.049666 | 0.012492 | 3.6438e-05 | 1.3882e-05 | 0.074946 | 0.074946 | 0.074946 | 0.98556 | -0.10084 | 0.9863 | -0.095577 | 27.7579
40 | -0.11261 | -0.028466 | 0.1129 | 0.028576 | 0.00029162 | 0.00011023 | 0.16851 | 0.16851 | 0.16851 | 0.99487 | -0.035335 | 0.99753 | -0.016997 | 20.8036
41 | 0.11141 | 0.028165 | -0.11127 | -0.028112 | 0.00014019 | 5.2977e-05 | 0.16672 | 0.16672 | 0.16672 | 0.99487 | -0.035335 | 0.99358 | -0.044279 | 20.5824
42 | -0.11526 | -0.029169 | 0.11535 | 0.029203 | 8.8889e-05 | 3.3622e-05 | 0.17204 | 0.17204 | 0.17204 | 0.99753 | -0.016997 | 0.99832 | -0.011539 | 21.2394
43 | 0.0045448 | 0.0011387 | -0.0045436 | -0.0011387 | 1.1844e-06 | -7.4967e-08 | 0.0068062 | 0.0068064 | 0.0068064 | 0.99358 | -0.044279 | 0.99331 | -0.046162 | 2.5209
44 | 0.017143 | 0.004297 | -0.017136 | -0.0042947 | 6.5704e-06 | 2.3163e-06 | 0.025552 | 0.025552 | 0.025552 | 0.99832 | -0.011539 | 0.99793 | -0.014308 | 9.4638
45 | -0.1325 | -0.0335 | 0.13271 | 0.033582 | 0.00021578 | 8.195e-05 | 0.19759 | 0.19759 | 0.19759 | 0.99832 | -0.011539 | 1 | 0 | 24.3939
46 | 0.017136 | 0.0042947 | -0.017133 | -0.0042936 | 3.1424e-06 | 1.1078e-06 | 0.025552 | 0.025552 | 0.025552 | 0.99793 | -0.014308 | 0.99774 | -0.015632 | 9.4638
47 | 0.095146 | 0.024025 | -0.095035 | -0.023983 | 0.00011043 | 4.2358e-05 | 0.14164 | 0.14164 | 0.14164 | 1 | 0 | 0.9988 | -0.0082682 | 52.4599
48 | 0.012125 | 0.0030383 | -0.01212 | -0.0030368 | 4.6193e-06 | 1.4811e-06 | 0.018082 | 0.018082 | 0.018082 | 0.99774 | -0.015632 | 0.99735 | -0.018386 | 6.6972
49 | 0.089957 | 0.02271 | -0.089621 | -0.022582 | 0.00033552 | 0.00012866 | 0.13408 | 0.13408 | 0.13408 | 0.9988 | -0.0082682 | 0.99496 | -0.034921 | 49.6577
50 | -0.052121 | -0.013107 | 0.052176 | 0.013128 | 5.5061e-05 | 2.0995e-05 | 0.07865 | 0.07865 | 0.07865 | 0.9863 | -0.095577 | 0.98738 | -0.088006 | 29.1298
51 | -0.001849 | -0.0004634 | 0.0018492 | 0.00046281 | 2.5737e-07 | -5.8652e-07 | 0.0027804 | 0.0027802 | 0.0027804 | 0.98952 | -0.072994 | 0.98966 | -0.071988 | 1.0298
52 | -0.0036603 | -0.0009167 | 0.0036613 | 0.00091641 | 9.7658e-07 | -2.8861e-07 | 0.0055032 | 0.005503 | 0.0055032 | 0.98966 | -0.071988 | 0.98993 | -0.070057 | 2.0382
53 | -0.077103 | -0.019393 | 0.077414 | 0.019512 | 0.00031151 | 0.00011933 | 0.11592 | 0.11592 | 0.11592 | 0.98993 | -0.070057 | 0.99406 | -0.0412 | 42.9338
54 | 0.017245 | 0.0043226 | -0.017234 | -0.0043187 | 1.0854e-05 | 3.8418e-06 | 0.025921 | 0.025921 | 0.025921 | 0.98993 | -0.070057 | 0.98929 | -0.074604 | 9.6005
55 | 0.056197 | 0.014154 | -0.056125 | -0.014127 | 7.2086e-05 | 2.7518e-05 | 0.084497 | 0.084497 | 0.084497 | 0.98993 | -0.070057 | 0.98862 | -0.079243 | 31.2952
56 | -0.083906 | -0.021139 | 0.08398 | 0.021168 | 7.3773e-05 | 2.8277e-05 | 0.12564 | 0.12564 | 0.12564 | 0.99406 | -0.0412 | 0.99496 | -0.034921 | 46.5329
57 | 0.013082 | 0.0032783 | -0.013078 | -0.0032768 | 4.6989e-06 | 1.5577e-06 | 0.019677 | 0.019677 | 0.019677 | 0.98929 | -0.074604 | 0.98892 | -0.0772 | 7.2879
58 | 0.054451 | 0.013707 | -0.054385 | -0.013682 | 6.6554e-05 | 2.5394e-05 | 0.081978 | 0.081979 | 0.081979 | 0.98862 | -0.079243 | 0.98738 | -0.088006 | 30.3624
59 | 0.011681 | 0.0029268 | -0.011677 | -0.0029254 | 4.3566e-06 | 1.3857e-06 | 0.017576 | 0.017576 | 0.017576 | 0.98892 | -0.0772 | 0.98854 | -0.079896 | 6.5097
60 | 0.0072374 | 0.0018135 | -0.0072348 | -0.001813 | 2.5856e-06 | 5.4703e-07 | 0.010894 | 0.010894 | 0.010894 | 0.98854 | -0.079896 | 0.98818 | -0.082478 | 4.0349
61 | 0.0031424 | 0.00078734 | -0.0031421 | -0.00078749 | 2.8086e-07 | -1.4948e-07 | 0.0047318 | 0.0047319 | 0.0047319 | 0.98818 | -0.082478 | 0.98809 | -0.083124 | 1.7526
62 | 0.0083013 | 0.0020798 | -0.0082981 | -0.002079 | 3.1741e-06 | 7.8824e-07 | 0.012385 | 0.012385 | 0.012385 | 0.99735 | -0.018386 | 0.99695 | -0.021151 | 4.5871
63 | 0.0054567 | 0.0013668 | -0.0054562 | -0.0013668 | 4.6206e-07 | 3.2157e-08 | 0.0081442 | 0.0081442 | 0.0081442 | 0.99695 | -0.021151 | 0.99687 | -0.021763 | 3.0164
64 | 0.0033927 | 0.00084963 | -0.0033921 | -0.00084988 | 5.7428e-07 | -2.4691e-07 | 0.005064 | 0.0050641 | 0.0050641 | 0.99687 | -0.021763 | 0.99669 | -0.022987 | 1.8756
65 | 0.0033921 | 0.00084988 | -0.0033917 | -0.00085004 | 3.7673e-07 | -1.6187e-07 | 0.0050641 | 0.0050642 | 0.0050642 | 0.99669 | -0.022987 | 0.99658 | -0.023789 | 1.8756

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23305 | 0.058709

## res_load
| p_mw | q_mvar
0 | 0.0066888 | 0.0016764
1 | 0.0016186 | 0.00040567
2 | 0.00056086 | 0.00014056
3 | 0.010587 | 0.0026533
4 | 0.0046986 | 0.0011776
5 | 0.0014278 | 0.00035785
6 | 0.0022484 | 0.00056349
7 | 0.019891 | 0.0049852
8 | 0.015102 | 0.0037849
9 | 0.0040599 | 0.0010175
10 | 0.0032181 | 0.00080653
11 | 0.0071526 | 0.0017926
12 | 0.01243 | 0.0031153
13 | 0.015251 | 0.0038222
14 | 0.0013026 | 0.00032647
15 | 0.00068476 | 0.00017162
16 | 0.0014467 | 0.00036257
17 | 0.0066084 | 0.0016562
18 | 0.0023169 | 0.00058067
19 | 0.0026291 | 0.00065891
20 | 0.0031543 | 0.00079054
21 | 0.0030161 | 0.00075591
22 | 0.0014607 | 0.00036607
23 | 0.0021397 | 0.00053626
24 | 0.0027702 | 0.00069427
25 | 0.0043726 | 0.0010959
26 | 0.0029429 | 0.00073755
27 | 0.0014948 | 0.00037464
28 | 0.0020313 | 0.0005091
29 | 0.0033802 | 0.00084716
30 | 0.0083236 | 0.0020861
31 | 0.0019048 | 0.00047738
32 | 0.0017556 | 0.00044
33 | 0.0011979 | 0.00030022
34 | 0.0023669 | 0.00059321
35 | 0.0045436 | 0.0011387
36 | 0.0043964 | 0.0011018
37 | 0.0050087 | 0.0012553
38 | 0.0050786 | 0.0012728
39 | 0.0024553 | 0.00061535
40 | 0.001849 | 0.0004634
41 | 0.0018111 | 0.00045389
42 | 0.006492 | 0.0016271
43 | 0.0041513 | 0.0010404
44 | 0.0016733 | 0.00041936
45 | 0.0056413 | 0.0014139
46 | 0.0013966 | 0.00035001
47 | 0.0022084 | 0.00055349
48 | 0.0040924 | 0.0010257
49 | 0.0031421 | 0.00078749
50 | 0.0038187 | 0.00095706
51 | 0.0028414 | 0.00071213
52 | 0.0020636 | 0.00051718
53 | 0.0033917 | 0.00085004

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1