## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2029-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2029-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2029-6_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2029-6_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2029-6_0_3_node_50 | 0.4 | n |  | TRUE
5 | bus_LV_2029-6_0_3_node_48 | 0.4 | n |  | TRUE
6 | bus_LV_2029-6_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2029-6_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2029-6_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2029-6_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2029-6_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2029-6_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2029-6_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2029-6_0_3_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_2029-6_0_3_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_2029-6_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2029-6_0_3_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_2029-6_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2029-6_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2029-6_0_3_node_77 | 0.4 | n |  | TRUE
20 | bus_LV_2029-6_0_3_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_2029-6_0_3_node_44 | 0.4 | n |  | TRUE
22 | bus_LV_2029-6_0_3_node_45 | 0.4 | n |  | TRUE
23 | bus_LV_2029-6_0_3_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_2029-6_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_2029-6_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2029-6_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_2029-6_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2029-6_0_3_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_2029-6_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_2029-6_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_2029-6_0_3_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2029-6_0_3_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2029-6_0_3_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_2029-6_0_3_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_2029-6_0_3_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_2029-6_0_3_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_2029-6_0_3_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_2029-6_0_3_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_2029-6_0_3_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_2029-6_0_3_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_2029-6_0_3_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_2029-6_0_3_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_2029-6_0_3_node_64 | 0.4 | n |  | TRUE
44 | bus_LV_2029-6_0_3_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_2029-6_0_3_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_2029-6_0_3_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_2029-6_0_3_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_2029-6_0_3_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_2029-6_0_3_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_2029-6_0_3_node_51 | 0.4 | n |  | TRUE
51 | bus_LV_2029-6_0_3_node_60 | 0.4 | n |  | TRUE
52 | bus_LV_2029-6_0_3_node_52 | 0.4 | n |  | TRUE
53 | bus_LV_2029-6_0_3_node_62 | 0.4 | n |  | TRUE
54 | bus_LV_2029-6_0_3_node_59 | 0.4 | n |  | TRUE
55 | bus_LV_2029-6_0_3_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_2029-6_0_3_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_2029-6_0_3_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_2029-6_0_3_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_2029-6_0_3_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_2029-6_0_3_node_55 | 0.4 | n |  | TRUE
61 | bus_LV_2029-6_0_3_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_2029-6_0_3_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_2029-6_0_3_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_2029-6_0_3_node_69 | 0.4 | n |  | TRUE
65 | bus_LV_2029-6_0_3_node_61 | 0.4 | n |  | TRUE
66 | bus_LV_2029-6_0_3_node_70 | 0.4 | n |  | TRUE
67 | bus_LV_2029-6_0_3_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_2029-6_0_3_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_2029-6_0_3_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_2029-6_0_3_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_2029-6_0_3_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_2029-6_0_3_node_71 | 0.4 | n |  | TRUE
73 | bus_LV_2029-6_0_3_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_2029-6_0_3_node_73 | 0.4 | n |  | TRUE
75 | bus_LV_2029-6_0_3_node_74 | 0.4 | n |  | TRUE
76 | bus_LV_2029-6_0_3_node_75 | 0.4 | n |  | TRUE
77 | bus_LV_2029-6_0_3_node_76 | 0.4 | n |  | TRUE
78 | bus_MV_477_0_node_35 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2029-6_0_3_load_0 | 0 | 0.00093488 | 0.0002343 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2029-6_0_3_load_1 | 1 | 0.00075954 | 0.00019036 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2029-6_0_3_load_2 | 2 | 0.00082642 | 0.00020712 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2029-6_0_3_load_3 | 3 | 0.00097084 | 0.00024332 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2029-6_0_3_load_50 | 4 | 0.0018537 | 0.00046459 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2029-6_0_3_load_48 | 5 | 0.0015569 | 0.00039019 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2029-6_0_3_load_4 | 6 | 0.0016464 | 0.00041262 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2029-6_0_3_load_7 | 9 | 0.00046112 | 0.00011557 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2029-6_0_3_load_8 | 10 | 0.00086216 | 0.00021608 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2029-6_0_3_load_9 | 11 | 0.0011064 | 0.00027728 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2029-6_0_3_load_12 | 13 | 0.0017562 | 0.00044016 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2029-6_0_3_load_11 | 15 | 0.0014397 | 0.00036083 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2029-6_0_3_load_16 | 16 | 0.0031102 | 0.0007795 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2029-6_0_3_load_13 | 17 | 0.0012032 | 0.00030154 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2029-6_0_3_load_14 | 18 | 0.00083191 | 0.0002085 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2029-6_0_3_load_77 | 19 | 0.0088477 | 0.0022174 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2029-6_0_3_load_34 | 20 | 0.0037265 | 0.00093395 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2029-6_0_3_load_45 | 22 | 0.0004961 | 0.00012433 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2029-6_0_3_load_41 | 23 | 0.0024082 | 0.00060355 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2029-6_0_3_load_17 | 24 | 0.0021952 | 0.00055016 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2029-6_0_3_load_18 | 25 | 0.0076698 | 0.0019222 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2029-6_0_3_load_19 | 26 | 0.0079496 | 0.0019924 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2029-6_0_3_load_20 | 27 | 0.01451 | 0.0036364 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2029-6_0_3_load_27 | 29 | 0.004877 | 0.0012223 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2029-6_0_3_load_24 | 30 | 0.014871 | 0.003727 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2029-6_0_3_load_21 | 31 | 0.013872 | 0.0034766 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2029-6_0_3_load_22 | 32 | 0.011457 | 0.0028713 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2029-6_0_3_load_23 | 33 | 0.00043994 | 0.00011026 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2029-6_0_3_load_25 | 34 | 0.0021833 | 0.00054719 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2029-6_0_3_load_32 | 35 | 0.0035733 | 0.00089555 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2029-6_0_3_load_30 | 36 | 0.0040665 | 0.0010191 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2029-6_0_3_load_31 | 37 | 0.00086684 | 0.00021725 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2029-6_0_3_load_33 | 38 | 0.0019773 | 0.00049555 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2029-6_0_3_load_28 | 39 | 0.0017346 | 0.00043474 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2029-6_0_3_load_35 | 40 | 0.0020999 | 0.00052629 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2029-6_0_3_load_36 | 41 | 0.0027165 | 0.00068082 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2029-6_0_3_load_29 | 42 | 0.0029848 | 0.00074807 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2029-6_0_3_load_64 | 43 | 0.0033715 | 0.00084497 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2029-6_0_3_load_37 | 44 | 0.006799 | 0.001704 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2029-6_0_3_load_38 | 46 | 0.00090663 | 0.00022722 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2029-6_0_3_load_39 | 47 | 0.00096923 | 0.00024291 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2029-6_0_3_load_42 | 49 | 0.0010442 | 0.00026171 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2029-6_0_3_load_51 | 50 | 0.00067533 | 0.00016925 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2029-6_0_3_load_52 | 52 | 0.0024674 | 0.00061839 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2029-6_0_3_load_62 | 53 | 0.0022258 | 0.00055784 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2029-6_0_3_load_59 | 54 | 0.0012937 | 0.00032423 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2029-6_0_3_load_46 | 55 | 0.0020467 | 0.00051295 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2029-6_0_3_load_49 | 57 | 0.00068488 | 0.00017165 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2029-6_0_3_load_53 | 58 | 0.0065103 | 0.0016316 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2029-6_0_3_load_54 | 59 | 0.0032367 | 0.00081119 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2029-6_0_3_load_55 | 60 | 0.0013338 | 0.00033429 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2029-6_0_3_load_56 | 61 | 0.0023584 | 0.00059108 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2029-6_0_3_load_57 | 62 | 0.00090599 | 0.00022706 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2029-6_0_3_load_69 | 64 | 0.0061434 | 0.0015397 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2029-6_0_3_load_70 | 66 | 0.0072601 | 0.0018196 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2029-6_0_3_load_63 | 67 | 0.0029807 | 0.00074704 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2029-6_0_3_load_68 | 68 | 0.0072217 | 0.0018099 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2029-6_0_3_load_67 | 69 | 0.002293 | 0.00057468 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2029-6_0_3_load_65 | 70 | 0.0091921 | 0.0023037 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2029-6_0_3_load_66 | 71 | 0.006108 | 0.0015308 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2029-6_0_3_load_71 | 72 | 0.0065403 | 0.0016392 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2029-6_0_3_load_72 | 73 | 0.0010582 | 0.0002652 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2029-6_0_3_load_73 | 74 | 0.0015882 | 0.00039804 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2029-6_0_3_load_75 | 76 | 0.0035283 | 0.00088427 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2029-6_0_3_load_76 | 77 | 0.0075076 | 0.0018816 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2029-6_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.023524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2029-6_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.032982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2029-6_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.027068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2029-6_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.020375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2029-6_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.0038063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2029-6_0_3_line_5 | NAYY 4x150 SE | 5 | 56 | 0.012049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2029-6_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.01103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2029-6_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.028471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2029-6_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.043665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2029-6_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.032117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2029-6_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.025374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2029-6_0_3_line_11 | NAYY 4x150 SE | 8 | 12 | 0.009258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2029-6_0_3_line_12 | NAYY 4x150 SE | 9 | 13 | 0.0015272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2029-6_0_3_line_13 | NAYY 4x150 SE | 10 | 14 | 0.0020535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2029-6_0_3_line_14 | NAYY 4x150 SE | 12 | 15 | 0.025584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2029-6_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.044922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2029-6_0_3_line_16 | NAYY 4x150 SE | 14 | 17 | 0.037805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2029-6_0_3_line_17 | NAYY 4x150 SE | 16 | 21 | 0.018332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2029-6_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.0062629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2029-6_0_3_line_19 | NAYY 4x150 SE | 19 | 20 | 0.074984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2029-6_0_3_line_20 | NAYY 4x150 SE | 20 | 35 | 0.015685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2029-6_0_3_line_21 | NAYY 4x150 SE | 21 | 22 | 0.037388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2029-6_0_3_line_22 | NAYY 4x150 SE | 21 | 23 | 0.016941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2029-6_0_3_line_23 | NAYY 4x150 SE | 22 | 55 | 0.0098977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2029-6_0_3_line_24 | NAYY 4x150 SE | 23 | 47 | 0.02723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2029-6_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.0072971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2029-6_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.045306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2029-6_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.037529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2029-6_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.015577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2029-6_0_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.049945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2029-6_0_3_line_30 | NAYY 4x150 SE | 28 | 30 | 0.020516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2029-6_0_3_line_31 | NAYY 4x150 SE | 29 | 43 | 0.00010145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2029-6_0_3_line_32 | NAYY 4x150 SE | 30 | 32 | 0.024606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2029-6_0_3_line_33 | NAYY 4x150 SE | 31 | 32 | 0.00081912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2029-6_0_3_line_34 | NAYY 4x150 SE | 31 | 33 | 0.018599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2029-6_0_3_line_35 | NAYY 4x150 SE | 33 | 34 | 0.0023098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2029-6_0_3_line_36 | NAYY 4x150 SE | 34 | 39 | 0.0068787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2029-6_0_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.0022509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2029-6_0_3_line_38 | NAYY 4x150 SE | 36 | 37 | 0.012378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2029-6_0_3_line_39 | NAYY 4x150 SE | 37 | 38 | 0.0073728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2029-6_0_3_line_40 | NAYY 4x150 SE | 38 | 40 | 0.015167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2029-6_0_3_line_41 | NAYY 4x150 SE | 39 | 42 | 0.0060113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2029-6_0_3_line_42 | NAYY 4x150 SE | 40 | 41 | 0.0061474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2029-6_0_3_line_43 | NAYY 4x150 SE | 41 | 44 | 0.016951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2029-6_0_3_line_44 | NAYY 4x150 SE | 43 | 45 | 0.020877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_2029-6_0_3_line_45 | NAYY 4x150 SE | 44 | 46 | 0.092292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2029-6_0_3_line_46 | NAYY 4x150 SE | 45 | 51 | 0.002419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2029-6_0_3_line_47 | NAYY 4x150 SE | 45 | 48 | 0.02647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_2029-6_0_3_line_48 | NAYY 4x150 SE | 46 | 47 | 0.014091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2029-6_0_3_line_49 | NAYY 4x150 SE | 48 | 49 | 0.034938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2029-6_0_3_line_50 | NAYY 4x150 SE | 49 | 50 | 0.012632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2029-6_0_3_line_51 | NAYY 4x150 SE | 50 | 52 | 0.019992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2029-6_0_3_line_52 | NAYY 4x150 SE | 51 | 53 | 0.042328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2029-6_0_3_line_53 | NAYY 4x150 SE | 51 | 54 | 0.020306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2029-6_0_3_line_54 | NAYY 4x150 SE | 52 | 57 | 0.018343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2029-6_0_3_line_55 | NAYY 4x150 SE | 54 | 65 | 0.034301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2029-6_0_3_line_56 | NAYY 4x150 SE | 55 | 56 | 0.033262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2029-6_0_3_line_57 | NAYY 4x150 SE | 56 | 57 | 0.010955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2029-6_0_3_line_58 | NAYY 4x150 SE | 58 | 59 | 0.026257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2029-6_0_3_line_59 | NAYY 4x150 SE | 58 | 60 | 0.031156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2029-6_0_3_line_60 | NAYY 4x150 SE | 59 | 61 | 0.005129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2029-6_0_3_line_61 | NAYY 4x150 SE | 61 | 62 | 0.0094543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2029-6_0_3_line_62 | NAYY 4x150 SE | 62 | 63 | 0.010655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2029-6_0_3_line_63 | NAYY 4x150 SE | 63 | 64 | 0.040547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2029-6_0_3_line_64 | NAYY 4x150 SE | 63 | 65 | 0.016261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2029-6_0_3_line_65 | NAYY 4x150 SE | 64 | 66 | 0.0014251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2029-6_0_3_line_66 | NAYY 4x150 SE | 65 | 67 | 0.014348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2029-6_0_3_line_67 | NAYY 4x150 SE | 66 | 72 | 0.022366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2029-6_0_3_line_68 | NAYY 4x150 SE | 67 | 68 | 0.017722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2029-6_0_3_line_69 | NAYY 4x150 SE | 68 | 69 | 0.009829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2029-6_0_3_line_70 | NAYY 4x150 SE | 69 | 71 | 0.0097108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2029-6_0_3_line_71 | NAYY 4x150 SE | 70 | 71 | 0.0059205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2029-6_0_3_line_72 | NAYY 4x150 SE | 72 | 73 | 0.01254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2029-6_0_3_line_73 | NAYY 4x150 SE | 73 | 74 | 0.0068028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2029-6_0_3_line_74 | NAYY 4x150 SE | 74 | 75 | 0.0068866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2029-6_0_3_line_75 | NAYY 4x150 SE | 75 | 76 | 0.018269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2029-6_0_3_line_76 | NAYY 4x150 SE | 76 | 77 | 0.0049293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2029-6_0_3_trafo_64 | 0.25 MVA 20/0.4 kV | 78 | 43 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2565979.1386 | 1185389.4143 | 2565982.963 | 1185387.8712 | 2565994.6786 | 1185382.7239 | 2566000.0194 | 1185378.8402
1 | 2566000.0194 | 1185378.8402 | 2566009.2858 | 1185372.1018 | 2566024.9719 | 1185357.3624
2 | 2566045.6323 | 1185339.8981 | 2566043.0126 | 1185341.805 | 2566028.6047 | 1185353.9489 | 2566024.9719 | 1185357.3624
3 | 2566045.6323 | 1185339.8981 | 2566058.8664 | 1185330.2643 | 2566062.2637 | 1185328.1419
4 | 2566065.4917 | 1185326.1251 | 2566062.2637 | 1185328.1419
5 | 2566075.7105 | 1185319.7408 | 2566065.4917 | 1185326.1251
6 | 2566099.8491 | 1185464.8921 | 2566093.5022 | 1185473.9134
7 | 2566075.2753 | 1185495.6369 | 2566084.9055 | 1185486.1327 | 2566093.5022 | 1185473.9134
8 | 2566099.8491 | 1185464.8921 | 2566103.8319 | 1185482.2232 | 2566123.3657 | 1185499.2033
9 | 2566099.8491 | 1185464.8921 | 2566110.7309 | 1185434.6747
10 | 2566075.2753 | 1185495.6369 | 2566056.1218 | 1185512.2801
11 | 2566075.2753 | 1185495.6369 | 2566073.5947 | 1185504.7402
12 | 2566123.3657 | 1185499.2033 | 2566124.5183 | 1185500.2053
13 | 2566111.4266 | 1185432.7427 | 2566110.7309 | 1185434.6747
14 | 2566073.5947 | 1185504.7402 | 2566075.7175 | 1185518.402 | 2566082.3453 | 1185528.1141
15 | 2566111.4266 | 1185432.7427 | 2566119.6233 | 1185403.2471 | 2566123.6636 | 1185389.5202
16 | 2566111.4266 | 1185432.7427 | 2566145.4653 | 1185449.1918
17 | 2566128.84 | 1185371.9338 | 2566123.6636 | 1185389.5202
18 | 2566151.1043 | 1185451.9168 | 2566145.4653 | 1185449.1918
19 | 2566307.1442 | 1185356.9233 | 2566315.6818 | 1185431.42
20 | 2566307.1442 | 1185356.9233 | 2566293.7226 | 1185348.8073
21 | 2566128.84 | 1185371.9338 | 2566095.0813 | 1185355.8639
22 | 2566128.84 | 1185371.9338 | 2566136.0214 | 1185356.5907
23 | 2566086.6575 | 1185351.1497 | 2566086.9519 | 1185351.9941 | 2566095.0813 | 1185355.8639
24 | 2566145.8854 | 1185331.2695 | 2566141.5753 | 1185344.7249 | 2566136.0214 | 1185356.5907
25 | 2566241.7615 | 1185141.3847 | 2566239.3904 | 1185148.2858
26 | 2566239.3904 | 1185148.2858 | 2566231.4634 | 1185171.3572 | 2566232.3146 | 1185192.2506
27 | 2566233.8423 | 1185229.7483 | 2566232.3146 | 1185192.2506
28 | 2566234.4765 | 1185245.3128 | 2566233.8423 | 1185229.7483
29 | 2566234.4765 | 1185245.3128 | 2566205.0648 | 1185248.1362 | 2566187.6957 | 1185248.2345 | 2566184.7062 | 1185247.7479
30 | 2566234.4765 | 1185245.3128 | 2566254.8443 | 1185242.8491
31 | 2566184.6061 | 1185247.7316 | 2566184.7062 | 1185247.7479
32 | 2566254.8443 | 1185242.8491 | 2566279.2725 | 1185239.8943
33 | 2566280.0857 | 1185239.7959 | 2566279.2725 | 1185239.8943
34 | 2566280.0857 | 1185239.7959 | 2566298.5499 | 1185237.5625
35 | 2566300.843 | 1185237.2851 | 2566298.5499 | 1185237.5625
36 | 2566300.843 | 1185237.2851 | 2566307.6719 | 1185236.4591
37 | 2566291.7964 | 1185347.6425 | 2566293.7226 | 1185348.8073
38 | 2566291.7964 | 1185347.6425 | 2566281.2041 | 1185341.2374
39 | 2566281.2041 | 1185341.2374 | 2566274.8951 | 1185337.4224
40 | 2566274.8951 | 1185337.4224 | 2566274.8951 | 1185337.4224 | 2566260.1939 | 1185341.154
41 | 2566307.6719 | 1185236.4591 | 2566313.6396 | 1185235.7372
42 | 2566254.2355 | 1185342.6664 | 2566260.1939 | 1185341.154
43 | 2566237.8056 | 1185346.8369 | 2566254.2355 | 1185342.6664
44 | 2566164.0004 | 1185244.3777 | 2566184.6061 | 1185247.7316
45 | 2566150.1839 | 1185317.8507 | 2566237.8056 | 1185346.8369
46 | 2566164.0004 | 1185244.3777 | 2566161.6316 | 1185243.8576
47 | 2566158.0565 | 1185270.1696 | 2566164.0004 | 1185244.3777
48 | 2566150.1839 | 1185317.8507 | 2566145.8854 | 1185331.2695
49 | 2566158.0565 | 1185270.1696 | 2566125.5885 | 1185283.0716
50 | 2566115.4624 | 1185290.6241 | 2566125.5885 | 1185283.0716
51 | 2566115.4624 | 1185290.6241 | 2566107.7906 | 1185296.3463 | 2566099.4918 | 1185302.6496
52 | 2566161.6316 | 1185243.8576 | 2566162.644 | 1185231.2673 | 2566164.2368 | 1185224.1434 | 2566171.1443 | 1185220.2467 | 2566185.5734 | 1185221.2853
53 | 2566161.6316 | 1185243.8576 | 2566157.6101 | 1185242.5797 | 2566155.37 | 1185241.8697 | 2566142.7593 | 1185236.4245
54 | 2566084.7996 | 1185313.625 | 2566086.9242 | 1185312.1953 | 2566099.4918 | 1185302.6496
55 | 2566112.1628 | 1185220.9369 | 2566139.3348 | 1185234.9458 | 2566142.7593 | 1185236.4245
56 | 2566075.7105 | 1185319.7408 | 2566086.6575 | 1185351.1497
57 | 2566075.7105 | 1185319.7408 | 2566084.7996 | 1185313.625
58 | 2566073.2617 | 1185253.9807 | 2566070.4682 | 1185244.6306 | 2566081.2942 | 1185232.1808
59 | 2566073.8278 | 1185283.8769 | 2566077.9288 | 1185269.6015 | 2566073.2617 | 1185253.9807
60 | 2566084.6597 | 1185228.3105 | 2566081.2942 | 1185232.1808
61 | 2566084.6597 | 1185228.3105 | 2566090.8635 | 1185221.1762
62 | 2566097.8549 | 1185213.1362 | 2566090.8635 | 1185221.1762
63 | 2566097.8549 | 1185213.1362 | 2566086.8981 | 1185205.4832 | 2566076.4515 | 1185196.3043 | 2566069.2595 | 1185186.3843 | 2566068.7769 | 1185185.4823
64 | 2566112.1628 | 1185220.9369 | 2566097.8549 | 1185213.1362
65 | 2566068.1046 | 1185184.2258 | 2566068.7769 | 1185185.4823
66 | 2566112.1628 | 1185220.9369 | 2566119.9331 | 1185208.8748
67 | 2566068.1046 | 1185184.2258 | 2566057.553 | 1185164.5054
68 | 2566119.9331 | 1185208.8748 | 2566129.5303 | 1185193.9765
69 | 2566129.5303 | 1185193.9765 | 2566134.8532 | 1185185.7135
70 | 2566140.1121 | 1185177.5499 | 2566134.8532 | 1185185.7135
71 | 2566143.3183 | 1185172.5727 | 2566140.1121 | 1185177.5499
72 | 2566057.553 | 1185164.5054 | 2566052.5362 | 1185155.1293 | 2566051.6376 | 1185153.4481
73 | 2566048.431 | 1185147.4485 | 2566051.6376 | 1185153.4481
74 | 2566045.1849 | 1185141.3749 | 2566048.431 | 1185147.4485
75 | 2566045.1849 | 1185141.3749 | 2566048.7191 | 1185123.4512
76 | 2566049.6727 | 1185118.6151 | 2566048.7191 | 1185123.4512

## bus_geodata
| x | y | coords
0 | 2565979.1386 | 1185389.4143
1 | 2566000.0194 | 1185378.8402
2 | 2566024.9719 | 1185357.3624
3 | 2566045.6323 | 1185339.8981
4 | 2566062.2637 | 1185328.1419
5 | 2566065.4917 | 1185326.1251
6 | 2566093.5022 | 1185473.9134
7 | 2566099.8491 | 1185464.8921
8 | 2566075.2753 | 1185495.6369
9 | 2566123.3657 | 1185499.2033
10 | 2566110.7309 | 1185434.6747
11 | 2566056.1218 | 1185512.2801
12 | 2566073.5947 | 1185504.7402
13 | 2566124.5183 | 1185500.2053
14 | 2566111.4266 | 1185432.7427
15 | 2566082.3453 | 1185528.1141
16 | 2566123.6636 | 1185389.5202
17 | 2566145.4653 | 1185449.1918
18 | 2566151.1043 | 1185451.9168
19 | 2566315.6818 | 1185431.42
20 | 2566307.1442 | 1185356.9233
21 | 2566128.84 | 1185371.9338
22 | 2566095.0813 | 1185355.8639
23 | 2566136.0214 | 1185356.5907
24 | 2566241.7615 | 1185141.3847
25 | 2566239.3904 | 1185148.2858
26 | 2566232.3146 | 1185192.2506
27 | 2566233.8423 | 1185229.7483
28 | 2566234.4765 | 1185245.3128
29 | 2566184.7062 | 1185247.7479
30 | 2566254.8443 | 1185242.8491
31 | 2566280.0857 | 1185239.7959
32 | 2566279.2725 | 1185239.8943
33 | 2566298.5499 | 1185237.5625
34 | 2566300.843 | 1185237.2851
35 | 2566293.7226 | 1185348.8073
36 | 2566291.7964 | 1185347.6425
37 | 2566281.2041 | 1185341.2374
38 | 2566274.8951 | 1185337.4224
39 | 2566307.6719 | 1185236.4591
40 | 2566260.1939 | 1185341.154
41 | 2566254.2355 | 1185342.6664
42 | 2566313.6396 | 1185235.7372
43 | 2566184.6061 | 1185247.7316
44 | 2566237.8056 | 1185346.8369
45 | 2566164.0004 | 1185244.3777
46 | 2566150.1839 | 1185317.8507
47 | 2566145.8854 | 1185331.2695
48 | 2566158.0565 | 1185270.1696
49 | 2566125.5884 | 1185283.0716
50 | 2566115.4624 | 1185290.6241
51 | 2566161.6316 | 1185243.8576
52 | 2566099.4918 | 1185302.6496
53 | 2566185.5734 | 1185221.2853
54 | 2566142.7593 | 1185236.4245
55 | 2566086.6575 | 1185351.1497
56 | 2566075.7105 | 1185319.7408
57 | 2566084.7996 | 1185313.625
58 | 2566073.2617 | 1185253.9807
59 | 2566081.2942 | 1185232.1808
60 | 2566073.8278 | 1185283.8769
61 | 2566084.6597 | 1185228.3105
62 | 2566090.8635 | 1185221.1762
63 | 2566097.8549 | 1185213.1362
64 | 2566068.7769 | 1185185.4823
65 | 2566112.1628 | 1185220.9369
66 | 2566068.1046 | 1185184.2258
67 | 2566119.9331 | 1185208.8748
68 | 2566129.5303 | 1185193.9765
69 | 2566134.8532 | 1185185.7135
70 | 2566143.3183 | 1185172.5727
71 | 2566140.1121 | 1185177.5499
72 | 2566057.553 | 1185164.5054
73 | 2566051.6376 | 1185153.4481
74 | 2566048.431 | 1185147.4485
75 | 2566045.1849 | 1185141.3749
76 | 2566048.7191 | 1185123.4512
77 | 2566049.6727 | 1185118.6151
78 | 2566164.0004 | 1185244.3777

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98705 | -0.089984 | 0.00093488 | 0.0002343
1 | 0.98708 | -0.089758 | 0.00075954 | 0.00019036
2 | 0.98716 | -0.089185 | 0.00082642 | 0.00020712
3 | 0.98726 | -0.088484 | 0.00097084 | 0.00024332
4 | 0.98736 | -0.087754 | 0.0018537 | 0.00046459
5 | 0.98739 | -0.087545 | 0.0015569 | 0.00039019
6 | 0.98 | -0.13978 | 0.0016464 | 0.00041262
7 | 0.98007 | -0.13929 | 0 | 0
8 | 0.9799 | -0.14053 | 0 | 0
9 | 0.97993 | -0.1403 | 0.00046112 | 0.00011557
10 | 0.98037 | -0.13715 | 0.00086216 | 0.00021608
11 | 0.97986 | -0.14082 | 0.0011064 | 0.00027728
12 | 0.97988 | -0.14067 | 0 | 0
13 | 0.97993 | -0.14033 | 0.0017562 | 0.00044016
14 | 0.98039 | -0.13699 | 0 | 0
15 | 0.97982 | -0.14105 | 0.0014397 | 0.00036083
16 | 0.981 | -0.13265 | 0.0031102 | 0.0007795
17 | 0.98028 | -0.13779 | 0.0012032 | 0.00030154
18 | 0.98027 | -0.13785 | 0.00083191 | 0.0002085
19 | 0.97013 | -0.21038 | 0.0088477 | 0.0022174
20 | 0.9711 | -0.20335 | 0.0037265 | 0.00093395
21 | 0.98133 | -0.13028 | 0 | 0
22 | 0.98414 | -0.11041 | 0.0004961 | 0.00012433
23 | 0.98036 | -0.13713 | 0.0024082 | 0.00060355
24 | 0.99191 | -0.056689 | 0.0021952 | 0.00055016
25 | 0.99193 | -0.056526 | 0.0076698 | 0.0019222
26 | 0.99257 | -0.051995 | 0.0079496 | 0.0019924
27 | 0.99354 | -0.045226 | 0.01451 | 0.0036364
28 | 0.99426 | -0.040137 | 0 | 0
29 | 0.99999 | -8.5829e-05 | 0.004877 | 0.0012223
30 | 0.99286 | -0.05 | 0.014871 | 0.003727
31 | 0.99168 | -0.058326 | 0.013872 | 0.0034766
32 | 0.9917 | -0.05815 | 0.011457 | 0.0028713
33 | 0.99148 | -0.059713 | 0.00043994 | 0.00011026
34 | 0.99146 | -0.059875 | 0.0021833 | 0.00054719
35 | 0.97139 | -0.20126 | 0.0035733 | 0.00089555
36 | 0.97144 | -0.20087 | 0.0040665 | 0.0010191
37 | 0.97181 | -0.19823 | 0.00086684 | 0.00021725
38 | 0.97204 | -0.19658 | 0.0019773 | 0.00049555
39 | 0.99141 | -0.060204 | 0.0017346 | 0.00043474
40 | 0.97255 | -0.19289 | 0.0020999 | 0.00052629
41 | 0.97278 | -0.19126 | 0.0027165 | 0.00068082
42 | 0.99138 | -0.060386 | 0.0029848 | 0.00074807
43 | 1 | 0 | -0.23343 | -0.058671
44 | 0.97347 | -0.18628 | 0.006799 | 0.001704
45 | 0.99781 | -0.01515 | 0 | 0
46 | 0.97817 | -0.15272 | 0.00090663 | 0.00022722
47 | 0.9789 | -0.14749 | 0.00096923 | 0.00024291
48 | 0.99654 | -0.023888 | 0 | 0
49 | 0.99319 | -0.04706 | 0.0010442 | 0.00026171
50 | 0.992 | -0.055342 | 0.00067533 | 0.00016925
51 | 0.99753 | -0.017074 | 0 | 0
52 | 0.99013 | -0.068354 | 0.0024674 | 0.00061839
53 | 0.9974 | -0.01802 | 0.0022258 | 0.00055784
54 | 0.99528 | -0.03281 | 0.0012937 | 0.00032423
55 | 0.98489 | -0.10512 | 0.0020467 | 0.00051295
56 | 0.98751 | -0.086692 | 0 | 0
57 | 0.98849 | -0.079872 | 0.00068488 | 0.00017165
58 | 0.98962 | -0.072563 | 0.0065103 | 0.0016316
59 | 0.98992 | -0.070463 | 0.0032367 | 0.00081119
60 | 0.98956 | -0.072987 | 0.0013338 | 0.00033429
61 | 0.99 | -0.069884 | 0.0023584 | 0.00059108
62 | 0.99018 | -0.06859 | 0.00090599 | 0.00022706
63 | 0.99041 | -0.067034 | 0 | 0
64 | 0.98844 | -0.080937 | 0.0061434 | 0.0015397
65 | 0.99153 | -0.059103 | 0 | 0
66 | 0.98838 | -0.081338 | 0.0072601 | 0.0018196
67 | 0.99096 | -0.063154 | 0.0029807 | 0.00074704
68 | 0.99032 | -0.067627 | 0.0072217 | 0.0018099
69 | 0.99007 | -0.069388 | 0.002293 | 0.00057468
70 | 0.98978 | -0.071455 | 0.0091921 | 0.0023037
71 | 0.98986 | -0.070901 | 0.006108 | 0.0015308
72 | 0.98773 | -0.085963 | 0.0065403 | 0.0016392
73 | 0.98748 | -0.087719 | 0.0010582 | 0.0002652
74 | 0.98736 | -0.088598 | 0.0015882 | 0.00039804
75 | 0.98725 | -0.089377 | 0 | 0
76 | 0.98696 | -0.091442 | 0.0035283 | 0.00088427
77 | 0.9869 | -0.091821 | 0.0075076 | 0.0018816
78 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00093488 | -0.0002343 | 0.00093491 | 0.00023401 | 2.9155e-08 | -2.8947e-07 | 0.0014094 | 0.0014093 | 0.0014094 | 0.98705 | -0.089984 | 0.98708 | -0.089758 | 0.52199
1 | -0.0016944 | -0.00042437 | 0.0016946 | 0.000424 | 1.3427e-07 | -3.6999e-07 | 0.0025543 | 0.0025541 | 0.0025543 | 0.98708 | -0.089758 | 0.98716 | -0.089185 | 0.94602
2 | -0.002521 | -0.00063112 | 0.0025212 | 0.00063087 | 2.4387e-07 | -2.523e-07 | 0.0037998 | 0.0037997 | 0.0037998 | 0.98716 | -0.089185 | 0.98726 | -0.088484 | 1.4073
3 | -0.0034921 | -0.00087419 | 0.0034924 | 0.00087406 | 3.5216e-07 | -1.2512e-07 | 0.005263 | 0.0052629 | 0.005263 | 0.98726 | -0.088484 | 0.98736 | -0.087754 | 1.9492
4 | -0.0053462 | -0.0013387 | 0.0053463 | 0.0013387 | 1.5416e-07 | 1.0611e-08 | 0.0080566 | 0.0080566 | 0.0080566 | 0.98736 | -0.087754 | 0.98739 | -0.087545 | 2.9839
5 | -0.0069032 | -0.0017289 | 0.006904 | 0.001729 | 8.1366e-07 | 1.5881e-07 | 0.010403 | 0.010403 | 0.010403 | 0.98739 | -0.087545 | 0.98751 | -0.086692 | 3.8529
6 | -0.0041929 | -0.0010498 | 0.0041932 | 0.0010497 | 2.7893e-07 | -3.1707e-08 | 0.006366 | 0.0063659 | 0.006366 | 0.98 | -0.13978 | 0.98007 | -0.13929 | 2.3578
7 | 0.0025465 | 0.00063716 | -0.0025463 | -0.00063741 | 2.6556e-07 | -2.5655e-07 | 0.0038662 | 0.0038663 | 0.0038663 | 0.98 | -0.13978 | 0.9799 | -0.14053 | 1.432
8 | 0.0022177 | 0.00055528 | -0.0022174 | -0.00055571 | 3.0888e-07 | -4.3137e-07 | 0.0033669 | 0.0033671 | 0.0033671 | 0.98007 | -0.13929 | 0.97993 | -0.1403 | 1.2471
9 | -0.0064108 | -0.001605 | 0.0064127 | 0.0016053 | 1.8984e-06 | 3.2531e-07 | 0.0097328 | 0.0097327 | 0.0097328 | 0.98007 | -0.13929 | 0.98037 | -0.13715 | 3.6047
10 | 0.0011064 | 0.00027698 | -0.0011064 | -0.00027728 | 4.4694e-08 | -3.0244e-07 | 0.00168 | 0.0016802 | 0.0016802 | 0.9799 | -0.14053 | 0.97986 | -0.14082 | 0.62228
11 | 0.0014398 | 0.00036043 | -0.0014398 | -0.00036054 | 2.7614e-08 | -1.06e-07 | 0.0021863 | 0.0021863 | 0.0021863 | 0.9799 | -0.14053 | 0.97988 | -0.14067 | 0.80975
12 | 0.0017563 | 0.00044014 | -0.0017562 | -0.00044016 | 6.7778e-09 | -1.6633e-08 | 0.0026669 | 0.0026669 | 0.0026669 | 0.97993 | -0.1403 | 0.97993 | -0.14033 | 0.98773
13 | -0.0072749 | -0.0018214 | 0.0072751 | 0.0018215 | 1.5621e-07 | 3.4188e-08 | 0.011041 | 0.011041 | 0.011041 | 0.98037 | -0.13715 | 0.98039 | -0.13699 | 4.0894
14 | 0.0014398 | 0.00036054 | -0.0014397 | -0.00036083 | 7.6314e-08 | -2.929e-07 | 0.0021863 | 0.0021864 | 0.0021864 | 0.97988 | -0.14067 | 0.97982 | -0.14105 | 0.80979
15 | -0.0093104 | -0.002331 | 0.009316 | 0.0023326 | 5.5968e-06 | 1.5858e-06 | 0.01413 | 0.01413 | 0.01413 | 0.98039 | -0.13699 | 0.981 | -0.13265 | 5.2334
16 | 0.0020353 | 0.00050957 | -0.0020351 | -0.00050996 | 2.251e-07 | -3.9008e-07 | 0.003089 | 0.0030891 | 0.0030891 | 0.98039 | -0.13699 | 0.98028 | -0.13779 | 1.1441
17 | -0.012426 | -0.0031121 | 0.01243 | 0.0031134 | 4.0637e-06 | 1.3314e-06 | 0.018848 | 0.018848 | 0.018848 | 0.981 | -0.13265 | 0.98133 | -0.13028 | 6.9806
18 | 0.00083192 | 0.00020842 | -0.00083191 | -0.0002085 | 6.2319e-09 | -7.6558e-08 | 0.0012628 | 0.0012628 | 0.0012628 | 0.98028 | -0.13779 | 0.98027 | -0.13785 | 0.46771
19 | -0.0088477 | -0.0022174 | 0.0088563 | 0.0022198 | 8.6171e-06 | 2.3875e-06 | 0.013571 | 0.013571 | 0.013571 | 0.97013 | -0.21038 | 0.9711 | -0.20335 | 5.0263
20 | -0.012583 | -0.0031538 | 0.012586 | 0.003155 | 3.6383e-06 | 1.2053e-06 | 0.019281 | 0.019281 | 0.019281 | 0.9711 | -0.20335 | 0.97139 | -0.20126 | 7.141
21 | -0.051729 | -0.013005 | 0.051873 | 0.013059 | 0.00014359 | 5.4754e-05 | 0.078453 | 0.078452 | 0.078453 | 0.98133 | -0.13028 | 0.98414 | -0.11041 | 29.0565
22 | 0.039299 | 0.0098912 | -0.039261 | -0.009877 | 3.7556e-05 | 1.4231e-05 | 0.059605 | 0.059605 | 0.059605 | 0.98133 | -0.13028 | 0.98036 | -0.13713 | 22.0759
23 | -0.052369 | -0.013184 | 0.052408 | 0.013199 | 3.8743e-05 | 1.4775e-05 | 0.079202 | 0.079202 | 0.079202 | 0.98414 | -0.11041 | 0.98489 | -0.10512 | 29.3342
24 | 0.036853 | 0.0092734 | -0.0368 | -0.0092533 | 5.319e-05 | 2.0115e-05 | 0.05595 | 0.05595 | 0.05595 | 0.98036 | -0.13713 | 0.9789 | -0.14749 | 20.7222
25 | -0.0021952 | -0.00055016 | 0.0021952 | 0.00055009 | 4.9379e-08 | -7.52e-08 | 0.0032931 | 0.0032931 | 0.0032931 | 0.99191 | -0.056689 | 0.99193 | -0.056526 | 1.2197
26 | -0.009865 | -0.0024723 | 0.0098712 | 0.0024741 | 6.1912e-06 | 1.796e-06 | 0.014799 | 0.014798 | 0.014799 | 0.99193 | -0.056526 | 0.99257 | -0.051995 | 5.481
27 | -0.017821 | -0.0044665 | 0.017837 | 0.0044724 | 1.6714e-05 | 5.9431e-06 | 0.026716 | 0.026716 | 0.026716 | 0.99257 | -0.051995 | 0.99354 | -0.045226 | 9.8948
28 | -0.032347 | -0.0081088 | 0.03237 | 0.0081174 | 2.2814e-05 | 8.5729e-06 | 0.048447 | 0.048447 | 0.048447 | 0.99354 | -0.045226 | 0.99426 | -0.040137 | 17.9433
29 | -0.080016 | -0.020072 | 0.080463 | 0.020243 | 0.00044699 | 0.00017127 | 0.11976 | 0.11976 | 0.11976 | 0.99426 | -0.040137 | 0.99999 | -8.5829e-05 | 44.3554
30 | 0.047647 | 0.011954 | -0.047581 | -0.01193 | 6.5106e-05 | 2.4775e-05 | 0.071313 | 0.071313 | 0.071313 | 0.99426 | -0.040137 | 0.99286 | -0.05 | 26.4122
31 | -0.08534 | -0.021465 | 0.085341 | 0.021466 | 1.0213e-06 | 3.9149e-07 | 0.12702 | 0.12702 | 0.12702 | 0.99999 | -8.5829e-05 | 1 | 0 | 47.0431
32 | 0.03271 | 0.0082025 | -0.032674 | -0.0081886 | 3.6904e-05 | 1.3876e-05 | 0.049025 | 0.049026 | 0.049026 | 0.99286 | -0.05 | 0.9917 | -0.05815 | 18.1576
33 | -0.021216 | -0.0053172 | 0.021217 | 0.0053173 | 5.1803e-07 | 1.8867e-07 | 0.031835 | 0.031835 | 0.031835 | 0.99168 | -0.058326 | 0.9917 | -0.05815 | 11.7909
34 | 0.0073446 | 0.0018405 | -0.0073432 | -0.0018402 | 1.4095e-06 | 3.0222e-07 | 0.011021 | 0.011021 | 0.011021 | 0.99168 | -0.058326 | 0.99148 | -0.059713 | 4.0817
35 | 0.0069032 | 0.00173 | -0.0069031 | -0.0017299 | 1.547e-07 | 2.9714e-08 | 0.01036 | 0.01036 | 0.01036 | 0.99148 | -0.059713 | 0.99146 | -0.059875 | 3.8372
36 | 0.0047198 | 0.0011828 | -0.0047195 | -0.0011828 | 2.1537e-07 | -5.8678e-09 | 0.0070835 | 0.0070836 | 0.0070836 | 0.99146 | -0.059875 | 0.99141 | -0.060204 | 2.6235
37 | -0.01616 | -0.0040505 | 0.016161 | 0.0040508 | 8.607e-07 | 3.0317e-07 | 0.024754 | 0.024754 | 0.024754 | 0.97139 | -0.20126 | 0.97144 | -0.20087 | 9.1682
38 | -0.020227 | -0.00507 | 0.020234 | 0.0050727 | 7.4147e-06 | 2.6985e-06 | 0.030983 | 0.030983 | 0.030983 | 0.97144 | -0.20087 | 0.97181 | -0.19823 | 11.4752
39 | -0.021101 | -0.0052899 | 0.021106 | 0.0052917 | 4.8029e-06 | 1.7559e-06 | 0.03231 | 0.03231 | 0.03231 | 0.97181 | -0.19823 | 0.97204 | -0.19658 | 11.9668
40 | -0.023083 | -0.0057872 | 0.023095 | 0.0057916 | 1.1818e-05 | 4.3574e-06 | 0.035337 | 0.035337 | 0.035337 | 0.97204 | -0.19658 | 0.97255 | -0.19289 | 13.0878
41 | 0.0029849 | 0.00074802 | -0.0029848 | -0.00074807 | 7.5287e-08 | -4.8556e-08 | 0.0044801 | 0.0044801 | 0.0044801 | 0.99141 | -0.060204 | 0.99138 | -0.060386 | 1.6593
42 | -0.025195 | -0.0063179 | 0.025201 | 0.00632 | 5.7006e-06 | 2.1162e-06 | 0.03855 | 0.03855 | 0.03855 | 0.97255 | -0.19289 | 0.97278 | -0.19126 | 14.2778
43 | -0.027917 | -0.0070008 | 0.027937 | 0.007008 | 1.929e-05 | 7.2088e-06 | 0.042705 | 0.042705 | 0.042705 | 0.97278 | -0.19126 | 0.97347 | -0.18628 | 15.8168
44 | 0.14728 | 0.037205 | -0.14697 | -0.037085 | 0.00031316 | 0.0001199 | 0.21927 | 0.21927 | 0.21927 | 1 | 0 | 0.99781 | -0.01515 | 40.6047
45 | -0.034736 | -0.008712 | 0.034898 | 0.0087733 | 0.00016237 | 6.1296e-05 | 0.053098 | 0.053097 | 0.053098 | 0.97347 | -0.18628 | 0.97817 | -0.15272 | 19.6659
46 | 0.079946 | 0.02012 | -0.079925 | -0.020112 | 2.1466e-05 | 8.2246e-06 | 0.11925 | 0.11925 | 0.11925 | 0.99781 | -0.01515 | 0.99753 | -0.017074 | 44.1676
47 | 0.067025 | 0.016965 | -0.066943 | -0.016934 | 8.2608e-05 | 3.1082e-05 | 0.10001 | 0.10001 | 0.10001 | 0.99781 | -0.01515 | 0.99654 | -0.023888 | 18.521
48 | -0.035805 | -0.0090005 | 0.035831 | 0.0090104 | 2.6093e-05 | 9.8589e-06 | 0.054477 | 0.054477 | 0.054477 | 0.97817 | -0.15272 | 0.9789 | -0.14749 | 20.1765
49 | 0.066943 | 0.016934 | -0.066725 | -0.016851 | 0.00021807 | 8.3419e-05 | 0.10001 | 0.10001 | 0.10001 | 0.99654 | -0.023888 | 0.99319 | -0.04706 | 37.042
50 | 0.065681 | 0.016589 | -0.065604 | -0.01656 | 7.64e-05 | 2.9221e-05 | 0.098449 | 0.098449 | 0.098449 | 0.99319 | -0.04706 | 0.992 | -0.055342 | 36.4626
51 | 0.064929 | 0.01639 | -0.06481 | -0.016345 | 0.00011844 | 4.5295e-05 | 0.097436 | 0.097436 | 0.097436 | 0.992 | -0.055342 | 0.99013 | -0.068354 | 36.0875
52 | 0.0022261 | 0.0005574 | -0.0022258 | -0.00055784 | 2.9123e-07 | -4.4049e-07 | 0.0033205 | 0.0033207 | 0.0033207 | 0.99753 | -0.017074 | 0.9974 | -0.01802 | 1.2299
53 | 0.077699 | 0.019555 | -0.077529 | -0.019489 | 0.0001703 | 6.5235e-05 | 0.11593 | 0.11593 | 0.11593 | 0.99753 | -0.017074 | 0.99528 | -0.03281 | 42.9378
54 | 0.062343 | 0.015727 | -0.062242 | -0.015688 | 0.00010055 | 3.8438e-05 | 0.093728 | 0.093728 | 0.093728 | 0.99013 | -0.068354 | 0.98849 | -0.079872 | 34.7141
55 | 0.076235 | 0.019165 | -0.075957 | -0.019059 | 0.00027815 | 0.00010654 | 0.114 | 0.114 | 0.114 | 0.99528 | -0.03281 | 0.99153 | -0.059103 | 42.2215
56 | -0.054454 | -0.013711 | 0.054595 | 0.013765 | 0.00014056 | 5.3639e-05 | 0.082295 | 0.082294 | 0.082295 | 0.98489 | -0.10512 | 0.98751 | -0.086692 | 30.4795
57 | -0.061499 | -0.015494 | 0.061558 | 0.015517 | 5.874e-05 | 2.2452e-05 | 0.092697 | 0.092697 | 0.092697 | 0.98751 | -0.086692 | 0.98849 | -0.079872 | 34.3323
58 | -0.0078442 | -0.0019656 | 0.0078465 | 0.0019661 | 2.2792e-06 | 5.3917e-07 | 0.011795 | 0.011794 | 0.011795 | 0.98962 | -0.072563 | 0.98992 | -0.070463 | 4.3684
59 | 0.0013339 | 0.00033392 | -0.0013338 | -0.00033429 | 7.8203e-08 | -3.702e-07 | 0.0020055 | 0.0020057 | 0.0020057 | 0.98962 | -0.072563 | 0.98956 | -0.072987 | 0.74285
60 | -0.011083 | -0.0027773 | 0.011084 | 0.0027776 | 8.8828e-07 | 2.757e-07 | 0.01666 | 0.01666 | 0.01666 | 0.98992 | -0.070463 | 0.99 | -0.069884 | 6.1703
61 | -0.013443 | -0.0033686 | 0.013445 | 0.0033694 | 2.4083e-06 | 8.0468e-07 | 0.020205 | 0.020204 | 0.020205 | 0.99 | -0.069884 | 0.99018 | -0.06859 | 7.4832
62 | -0.014351 | -0.0035965 | 0.014354 | 0.0035976 | 3.0922e-06 | 1.0522e-06 | 0.021566 | 0.021566 | 0.021566 | 0.99018 | -0.06859 | 0.99041 | -0.067034 | 7.9874
63 | 0.033715 | 0.0084603 | -0.03365 | -0.0084358 | 6.493e-05 | 2.4452e-05 | 0.050658 | 0.050658 | 0.050658 | 0.99041 | -0.067034 | 0.98844 | -0.080937 | 18.7624
64 | -0.048069 | -0.012058 | 0.048122 | 0.012078 | 5.2929e-05 | 2.0148e-05 | 0.072224 | 0.072224 | 0.072224 | 0.99041 | -0.067034 | 0.99153 | -0.059103 | 26.7497
65 | 0.027507 | 0.0068961 | -0.027505 | -0.0068956 | 1.5249e-06 | 5.6823e-07 | 0.04141 | 0.04141 | 0.04141 | 0.98844 | -0.080937 | 0.98838 | -0.081338 | 15.3371
66 | 0.027835 | 0.0069805 | -0.027819 | -0.0069747 | 1.5624e-05 | 5.8243e-06 | 0.041774 | 0.041774 | 0.041774 | 0.99153 | -0.059103 | 0.99096 | -0.063154 | 15.4718
67 | 0.020245 | 0.005076 | -0.020232 | -0.0050713 | 1.2966e-05 | 4.7004e-06 | 0.03048 | 0.03048 | 0.03048 | 0.98838 | -0.081338 | 0.98773 | -0.085963 | 11.2889
68 | 0.024838 | 0.0062277 | -0.024823 | -0.006222 | 1.5384e-05 | 5.6888e-06 | 0.037298 | 0.037298 | 0.037298 | 0.99096 | -0.063154 | 0.99032 | -0.067627 | 13.8141
69 | 0.017601 | 0.0044121 | -0.017597 | -0.0044105 | 4.29e-06 | 1.5235e-06 | 0.026447 | 0.026447 | 0.026447 | 0.99032 | -0.067627 | 0.99007 | -0.069388 | 9.7953
70 | 0.015304 | 0.0038359 | -0.015301 | -0.0038347 | 3.2058e-06 | 1.1081e-06 | 0.023001 | 0.023001 | 0.023001 | 0.99007 | -0.069388 | 0.98986 | -0.070901 | 8.5189
71 | -0.0091921 | -0.0023037 | 0.0091928 | 0.0023039 | 7.0551e-07 | 1.9525e-07 | 0.013819 | 0.013819 | 0.013819 | 0.98978 | -0.071455 | 0.98986 | -0.070901 | 5.1182
72 | 0.013692 | 0.0034322 | -0.013689 | -0.003431 | 3.3294e-06 | 1.1201e-06 | 0.020627 | 0.020627 | 0.020627 | 0.98773 | -0.085963 | 0.98748 | -0.087719 | 7.6397
73 | 0.01263 | 0.0031658 | -0.012629 | -0.0031653 | 1.5377e-06 | 5.044e-07 | 0.019033 | 0.019033 | 0.019033 | 0.98748 | -0.087719 | 0.98736 | -0.088598 | 7.0491
74 | 0.011041 | 0.0027673 | -0.011039 | -0.0027669 | 1.1897e-06 | 3.6952e-07 | 0.016639 | 0.016639 | 0.016639 | 0.98736 | -0.088598 | 0.98725 | -0.089377 | 6.1626
75 | 0.011039 | 0.0027669 | -0.011036 | -0.0027659 | 3.1561e-06 | 9.8037e-07 | 0.016639 | 0.016639 | 0.016639 | 0.98725 | -0.089377 | 0.98696 | -0.091442 | 6.1627
76 | 0.007508 | 0.0018817 | -0.0075076 | -0.0018816 | 3.9413e-07 | 8.8599e-08 | 0.01132 | 0.01132 | 0.01132 | 0.98696 | -0.091442 | 0.9869 | -0.091821 | 4.1925

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2368 | 0.059516

## res_load
| p_mw | q_mvar
0 | 0.00093488 | 0.0002343
1 | 0.00075954 | 0.00019036
2 | 0.00082642 | 0.00020712
3 | 0.00097084 | 0.00024332
4 | 0.0018537 | 0.00046459
5 | 0.0015569 | 0.00039019
6 | 0.0016464 | 0.00041262
7 | 0.00046112 | 0.00011557
8 | 0.00086216 | 0.00021608
9 | 0.0011064 | 0.00027728
10 | 0.0017562 | 0.00044016
11 | 0.0014397 | 0.00036083
12 | 0.0031102 | 0.0007795
13 | 0.0012032 | 0.00030154
14 | 0.00083191 | 0.0002085
15 | 0.0088477 | 0.0022174
16 | 0.0037265 | 0.00093395
17 | 0.0004961 | 0.00012433
18 | 0.0024082 | 0.00060355
19 | 0.0021952 | 0.00055016
20 | 0.0076698 | 0.0019222
21 | 0.0079496 | 0.0019924
22 | 0.01451 | 0.0036364
23 | 0.004877 | 0.0012223
24 | 0.014871 | 0.003727
25 | 0.013872 | 0.0034766
26 | 0.011457 | 0.0028713
27 | 0.00043994 | 0.00011026
28 | 0.0021833 | 0.00054719
29 | 0.0035733 | 0.00089555
30 | 0.0040665 | 0.0010191
31 | 0.00086684 | 0.00021725
32 | 0.0019773 | 0.00049555
33 | 0.0017346 | 0.00043474
34 | 0.0020999 | 0.00052629
35 | 0.0027165 | 0.00068082
36 | 0.0029848 | 0.00074807
37 | 0.0033715 | 0.00084497
38 | 0.006799 | 0.001704
39 | 0.00090663 | 0.00022722
40 | 0.00096923 | 0.00024291
41 | 0.0010442 | 0.00026171
42 | 0.00067533 | 0.00016925
43 | 0.0024674 | 0.00061839
44 | 0.0022258 | 0.00055784
45 | 0.0012937 | 0.00032423
46 | 0.0020467 | 0.00051295
47 | 0.00068488 | 0.00017165
48 | 0.0065103 | 0.0016316
49 | 0.0032367 | 0.00081119
50 | 0.0013338 | 0.00033429
51 | 0.0023584 | 0.00059108
52 | 0.00090599 | 0.00022706
53 | 0.0061434 | 0.0015397
54 | 0.0072601 | 0.0018196
55 | 0.0029807 | 0.00074704
56 | 0.0072217 | 0.0018099
57 | 0.002293 | 0.00057468
58 | 0.0091921 | 0.0023037
59 | 0.006108 | 0.0015308
60 | 0.0065403 | 0.0016392
61 | 0.0010582 | 0.0002652
62 | 0.0015882 | 0.00039804
63 | 0.0035283 | 0.00088427
64 | 0.0075076 | 0.0018816

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1