## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2035-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2035-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2035-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2035-1_0_3_node_28 | 0.4 | n |  | TRUE
4 | bus_LV_2035-1_0_3_node_26 | 0.4 | n |  | TRUE
5 | bus_LV_2035-1_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_2035-1_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2035-1_0_3_node_67 | 0.4 | n |  | TRUE
8 | bus_LV_2035-1_0_3_node_72 | 0.4 | n |  | TRUE
9 | bus_LV_2035-1_0_3_node_77 | 0.4 | n |  | TRUE
10 | bus_LV_2035-1_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2035-1_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2035-1_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2035-1_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2035-1_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2035-1_0_3_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_2035-1_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2035-1_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2035-1_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2035-1_0_3_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2035-1_0_3_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_2035-1_0_3_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_2035-1_0_3_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_2035-1_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_2035-1_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2035-1_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2035-1_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_2035-1_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2035-1_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_2035-1_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2035-1_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_2035-1_0_3_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_2035-1_0_3_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_2035-1_0_3_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_2035-1_0_3_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_2035-1_0_3_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_2035-1_0_3_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_2035-1_0_3_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_2035-1_0_3_node_42 | 0.4 | n |  | TRUE
39 | bus_LV_2035-1_0_3_node_74 | 0.4 | n |  | TRUE
40 | bus_LV_2035-1_0_3_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_2035-1_0_3_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_2035-1_0_3_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_2035-1_0_3_node_46 | 0.4 | n |  | TRUE
44 | bus_LV_2035-1_0_3_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_2035-1_0_3_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_2035-1_0_3_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_2035-1_0_3_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_2035-1_0_3_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_2035-1_0_3_node_54 | 0.4 | n |  | TRUE
50 | bus_LV_2035-1_0_3_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_2035-1_0_3_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_2035-1_0_3_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_2035-1_0_3_node_75 | 0.4 | n |  | TRUE
54 | bus_LV_2035-1_0_3_node_65 | 0.4 | n |  | TRUE
55 | bus_LV_2035-1_0_3_node_66 | 0.4 | n |  | TRUE
56 | bus_LV_2035-1_0_3_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_2035-1_0_3_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_2035-1_0_3_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_2035-1_0_3_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_2035-1_0_3_node_55 | 0.4 | n |  | TRUE
61 | bus_LV_2035-1_0_3_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_2035-1_0_3_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_2035-1_0_3_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_2035-1_0_3_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_2035-1_0_3_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_2035-1_0_3_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_2035-1_0_3_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_2035-1_0_3_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_2035-1_0_3_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_2035-1_0_3_node_59 | 0.4 | n |  | TRUE
71 | bus_LV_2035-1_0_3_node_64 | 0.4 | n |  | TRUE
72 | bus_LV_2035-1_0_3_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_2035-1_0_3_node_76 | 0.4 | n |  | TRUE
74 | bus_LV_2035-1_0_3_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_2035-1_0_3_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_2035-1_0_3_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_2035-1_0_3_node_73 | 0.4 | n |  | TRUE
78 | bus_MV_478_0_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2035-1_0_3_load_0 | 0 | 0.0027078 | 0.00067863 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2035-1_0_3_load_1 | 1 | 0.00099615 | 0.00024966 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2035-1_0_3_load_28 | 3 | 0.0033479 | 0.00083906 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2035-1_0_3_load_3 | 5 | 0.0069745 | 0.001748 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2035-1_0_3_load_72 | 8 | 0.004391 | 0.0011005 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2035-1_0_3_load_77 | 9 | 0.0018295 | 0.00045851 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2035-1_0_3_load_5 | 10 | 0.0096463 | 0.0024176 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2035-1_0_3_load_7 | 12 | 0.0089508 | 0.0022433 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2035-1_0_3_load_8 | 13 | 0.00094505 | 0.00023685 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2035-1_0_3_load_9 | 14 | 0.0029187 | 0.0007315 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2035-1_0_3_load_13 | 15 | 0.0028058 | 0.00070319 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2035-1_0_3_load_11 | 16 | 0.0018283 | 0.0004582 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2035-1_0_3_load_10 | 17 | 0.0041102 | 0.0010301 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2035-1_0_3_load_12 | 18 | 0.0025513 | 0.00063942 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2035-1_0_3_load_18 | 20 | 0.0015025 | 0.00037655 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2035-1_0_3_load_30 | 21 | 0.0040381 | 0.001012 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2035-1_0_3_load_31 | 22 | 0.0021036 | 0.00052721 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2035-1_0_3_load_16 | 23 | 0.0035613 | 0.00089254 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2035-1_0_3_load_15 | 24 | 0.00070509 | 0.00017671 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2035-1_0_3_load_17 | 25 | 0.00058185 | 0.00014583 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2035-1_0_3_load_19 | 26 | 0.0015279 | 0.00038292 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2035-1_0_3_load_21 | 28 | 0.0017208 | 0.00043126 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2035-1_0_3_load_22 | 29 | 0.00050704 | 0.00012708 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2035-1_0_3_load_37 | 31 | 0.00089534 | 0.00022439 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2035-1_0_3_load_23 | 32 | 0.0014033 | 0.00035171 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2035-1_0_3_load_38 | 33 | 0.0019733 | 0.00049456 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2035-1_0_3_load_27 | 35 | 0.0013401 | 0.00033586 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2035-1_0_3_load_42 | 38 | 0.00039097 | 9.7986e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2035-1_0_3_load_74 | 39 | 0.0039302 | 0.000985 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2035-1_0_3_load_32 | 40 | 0.0041985 | 0.0010522 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2035-1_0_3_load_33 | 41 | 0.0011889 | 0.00029798 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2035-1_0_3_load_34 | 42 | 0.0022662 | 0.00056795 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2035-1_0_3_load_35 | 44 | 0.0015397 | 0.00038587 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2035-1_0_3_load_45 | 45 | 0.0015063 | 0.00037751 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2035-1_0_3_load_50 | 48 | 0.0034533 | 0.00086547 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2035-1_0_3_load_44 | 50 | 0.00156 | 0.00039097 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2035-1_0_3_load_41 | 51 | 0.002301 | 0.00057669 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2035-1_0_3_load_40 | 52 | 0.00083091 | 0.00020824 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2035-1_0_3_load_75 | 53 | 0.0038879 | 0.0009744 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2035-1_0_3_load_65 | 54 | 0.00099592 | 0.0002496 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2035-1_0_3_load_66 | 55 | 0.00051026 | 0.00012788 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2035-1_0_3_load_48 | 57 | 0.0095493 | 0.0023933 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2035-1_0_3_load_49 | 58 | 0.0078344 | 0.0019635 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2035-1_0_3_load_51 | 59 | 0.0018996 | 0.00047607 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2035-1_0_3_load_55 | 60 | 0.0083343 | 0.0020888 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2035-1_0_3_load_52 | 61 | 0.001688 | 0.00042304 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2035-1_0_3_load_53 | 63 | 0.0037003 | 0.00092739 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2035-1_0_3_load_61 | 64 | 0.00053118 | 0.00013313 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2035-1_0_3_load_62 | 65 | 0.0027079 | 0.00067866 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2035-1_0_3_load_60 | 66 | 0.00090021 | 0.00022561 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2035-1_0_3_load_63 | 67 | 0.00030165 | 7.5602e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2035-1_0_3_load_57 | 68 | 0.0028573 | 0.0007161 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2035-1_0_3_load_58 | 69 | 0.0014705 | 0.00036855 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2035-1_0_3_load_64 | 71 | 0.0010123 | 0.00025371 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2035-1_0_3_load_76 | 73 | 0.0055286 | 0.0013856 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2035-1_0_3_load_68 | 74 | 0.0026833 | 0.00067249 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2035-1_0_3_load_70 | 75 | 0.0045611 | 0.0011431 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2035-1_0_3_load_71 | 76 | 0.0037404 | 0.00093743 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2035-1_0_3_load_73 | 77 | 0.002674 | 0.00067016 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2035-1_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.019237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2035-1_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.021427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2035-1_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.015055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2035-1_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.0048917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2035-1_0_3_line_4 | NAYY 4x150 SE | 4 | 30 | 0.017191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2035-1_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.0019323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2035-1_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.019752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2035-1_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.0087245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2035-1_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.016483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2035-1_0_3_line_9 | NAYY 4x150 SE | 8 | 72 | 0.019308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2035-1_0_3_line_10 | NAYY 4x150 SE | 9 | 73 | 0.017649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2035-1_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.042129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2035-1_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.041393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2035-1_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.18602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2035-1_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.011597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2035-1_0_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.030982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2035-1_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.011162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2035-1_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.017248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2035-1_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.012189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2035-1_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.014856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2035-1_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.021558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2035-1_0_3_line_21 | NAYY 4x150 SE | 20 | 23 | 0.0085775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2035-1_0_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.0089332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2035-1_0_3_line_23 | NAYY 4x150 SE | 22 | 40 | 0.015776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2035-1_0_3_line_24 | NAYY 4x150 SE | 22 | 41 | 0.007545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2035-1_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.0083153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2035-1_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.011977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2035-1_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.019679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2035-1_0_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.017711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_2035-1_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.024349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2035-1_0_3_line_30 | NAYY 4x150 SE | 27 | 29 | 0.010139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_2035-1_0_3_line_31 | NAYY 4x150 SE | 28 | 30 | 0.010114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2035-1_0_3_line_32 | NAYY 4x150 SE | 29 | 31 | 0.0098784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_2035-1_0_3_line_33 | NAYY 4x150 SE | 30 | 32 | 0.0058066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2035-1_0_3_line_34 | NAYY 4x150 SE | 31 | 33 | 0.025688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_2035-1_0_3_line_35 | NAYY 4x150 SE | 32 | 34 | 0.023951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2035-1_0_3_line_36 | NAYY 4x150 SE | 33 | 36 | 0.010625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_2035-1_0_3_line_37 | NAYY 4x150 SE | 34 | 35 | 0.045479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2035-1_0_3_line_38 | NAYY 4x150 SE | 36 | 37 | 0.005456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_2035-1_0_3_line_39 | NAYY 4x150 SE | 37 | 38 | 0.02666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2035-1_0_3_line_40 | NAYY 4x150 SE | 37 | 39 | 0.013177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2035-1_0_3_line_41 | NAYY 4x150 SE | 38 | 52 | 0.021853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2035-1_0_3_line_42 | NAYY 4x150 SE | 39 | 53 | 0.025502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2035-1_0_3_line_43 | NAYY 4x150 SE | 40 | 42 | 0.01398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2035-1_0_3_line_44 | NAYY 4x150 SE | 41 | 43 | 0.0038317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2035-1_0_3_line_45 | NAYY 4x150 SE | 42 | 44 | 0.0049652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2035-1_0_3_line_46 | NAYY 4x150 SE | 43 | 45 | 0.011561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2035-1_0_3_line_47 | NAYY 4x150 SE | 44 | 46 | 0.0098429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2035-1_0_3_line_48 | NAYY 4x150 SE | 45 | 56 | 0.020526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2035-1_0_3_line_49 | NAYY 4x150 SE | 46 | 47 | 0.024324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2035-1_0_3_line_50 | NAYY 4x150 SE | 47 | 50 | 0.0028488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2035-1_0_3_line_51 | NAYY 4x150 SE | 47 | 51 | 0.014314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2035-1_0_3_line_52 | NAYY 4x150 SE | 48 | 49 | 0.018256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2035-1_0_3_line_53 | NAYY 4x150 SE | 49 | 62 | 0.027173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2035-1_0_3_line_54 | NAYY 4x150 SE | 50 | 54 | 0.017907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2035-1_0_3_line_55 | NAYY 4x150 SE | 51 | 52 | 0.010333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2035-1_0_3_line_56 | NAYY 4x150 SE | 53 | 73 | 0.034937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2035-1_0_3_line_57 | NAYY 4x150 SE | 54 | 55 | 0.0090912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2035-1_0_3_line_58 | NAYY 4x150 SE | 55 | 71 | 0.0029365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2035-1_0_3_line_59 | NAYY 4x150 SE | 56 | 57 | 0.0073911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2035-1_0_3_line_60 | NAYY 4x150 SE | 56 | 58 | 0.0091219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2035-1_0_3_line_61 | NAYY 4x150 SE | 57 | 59 | 0.018671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2035-1_0_3_line_62 | NAYY 4x150 SE | 58 | 60 | 0.037985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2035-1_0_3_line_63 | NAYY 4x150 SE | 59 | 61 | 0.0045632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2035-1_0_3_line_64 | NAYY 4x150 SE | 61 | 63 | 0.011491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2035-1_0_3_line_65 | NAYY 4x150 SE | 62 | 64 | 0.021153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2035-1_0_3_line_66 | NAYY 4x150 SE | 62 | 65 | 0.004021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2035-1_0_3_line_67 | NAYY 4x150 SE | 64 | 66 | 0.002288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2035-1_0_3_line_68 | NAYY 4x150 SE | 65 | 67 | 0.015876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2035-1_0_3_line_69 | NAYY 4x150 SE | 66 | 70 | 0.014822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2035-1_0_3_line_70 | NAYY 4x150 SE | 67 | 71 | 0.00012955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2035-1_0_3_line_71 | NAYY 4x150 SE | 68 | 69 | 0.032303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2035-1_0_3_line_72 | NAYY 4x150 SE | 68 | 70 | 0.028587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2035-1_0_3_line_73 | NAYY 4x150 SE | 72 | 76 | 0.017215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2035-1_0_3_line_74 | NAYY 4x150 SE | 72 | 74 | 0.06747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2035-1_0_3_line_75 | NAYY 4x150 SE | 74 | 75 | 0.005224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2035-1_0_3_line_76 | NAYY 4x150 SE | 76 | 77 | 0.039642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2035-1_0_3_trafo_19 | 0.25 MVA 20/0.4 kV | 78 | 26 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2553578.9607 | 1181609.1469 | 2553564.1888 | 1181596.824
1 | 2553545.3706 | 1181600.8467 | 2553560.6199 | 1181593.8468 | 2553564.1888 | 1181596.824
2 | 2553545.3706 | 1181600.8467 | 2553533.1299 | 1181592.0815
3 | 2553532.0542 | 1181587.3095 | 2553533.1299 | 1181592.0815
4 | 2553532.0542 | 1181587.3095 | 2553520.8347 | 1181584.1728 | 2553517.8199 | 1181579.4826
5 | 2553642.3195 | 1181657.3807 | 2553640.7435 | 1181656.2627
6 | 2553655.4618 | 1181642.6042 | 2553642.3195 | 1181657.3807
7 | 2553655.4618 | 1181642.6042 | 2553661.79 | 1181648.6101
8 | 2553655.4618 | 1181642.6042 | 2553643.0277 | 1181631.7835
9 | 2553675.7945 | 1181661.9015 | 2553661.79 | 1181648.6101
10 | 2553629.7139 | 1181620.1972 | 2553643.0277 | 1181631.7835
11 | 2553160.2706 | 1181438.4067 | 2553163.3779 | 1181450.978 | 2553178.7349 | 1181473.3477 | 2553180.06 | 1181474.9062
12 | 2553160.2706 | 1181438.4067 | 2553172.0347 | 1181441.783 | 2553194.5661 | 1181441.1953 | 2553200.9587 | 1181439.4966
13 | 2553386.5055 | 1181452.7201 | 2553200.9587 | 1181439.4966
14 | 2553386.5055 | 1181452.7201 | 2553398.0671 | 1181453.6211
15 | 2553428.7238 | 1181457.5716 | 2553418.0725 | 1181455.1802 | 2553398.0671 | 1181453.6211
16 | 2553428.7238 | 1181457.5716 | 2553439.6146 | 1181460.0167
17 | 2553456.4435 | 1181463.7951 | 2553439.6146 | 1181460.0167
18 | 2553468.3477 | 1181466.4058 | 2553467.3161 | 1181466.2362 | 2553456.4435 | 1181463.7951
19 | 2553483.0066 | 1181468.8155 | 2553468.3477 | 1181466.4058
20 | 2553483.0066 | 1181468.8155 | 2553482.2269 | 1181487.3538 | 2553483.1082 | 1181490.2245
21 | 2553483.1082 | 1181490.2245 | 2553484.4129 | 1181494.474 | 2553485.6271 | 1181498.4238
22 | 2553529.7791 | 1181473.4322 | 2553521.0946 | 1181471.3392
23 | 2553529.7791 | 1181473.4322 | 2553539.9014 | 1181475.8771 | 2553544.5549 | 1181478.5429
24 | 2553529.7791 | 1181473.4322 | 2553530.891 | 1181465.9696
25 | 2553485.6271 | 1181498.4238 | 2553486.8574 | 1181502.426 | 2553489.0026 | 1181505.9531
26 | 2553495.2265 | 1181516.1862 | 2553489.0026 | 1181505.9531
27 | 2553495.2265 | 1181516.1862 | 2553505.4528 | 1181533
28 | 2553517.697 | 1181545.0204 | 2553510.0951 | 1181540.6327 | 2553505.4528 | 1181533
29 | 2553517.697 | 1181545.0204 | 2553517.7782 | 1181568.2212 | 2553517.7813 | 1181569.3688
30 | 2553517.697 | 1181545.0204 | 2553526.4815 | 1181550.0836
31 | 2553517.8199 | 1181579.4826 | 2553517.7824 | 1181569.7442 | 2553517.7813 | 1181569.3688
32 | 2553526.4815 | 1181550.0836 | 2553535.04 | 1181555.0166
33 | 2553517.8199 | 1181579.4826 | 2553514.5492 | 1181584.2803
34 | 2553535.04 | 1181555.0166 | 2553540.1346 | 1181557.9531 | 2553557.6083 | 1181567.2816
35 | 2553501.058 | 1181604.0706 | 2553514.5492 | 1181584.2803
36 | 2553566.9816 | 1181572.2857 | 2553557.6083 | 1181567.2816
37 | 2553501.058 | 1181604.0706 | 2553494.9946 | 1181601.1162 | 2553470.3019 | 1181571.2031
38 | 2553571.805 | 1181574.8607 | 2553566.9816 | 1181572.2857
39 | 2553571.805 | 1181574.8607 | 2553578.6458 | 1181549.0937 | 2553578.6458 | 1181549.0937
40 | 2553571.805 | 1181574.8607 | 2553582.478 | 1181582.5887
41 | 2553582.2762 | 1181527.5447 | 2553578.6458 | 1181549.0937
42 | 2553582.478 | 1181582.5887 | 2553603.1341 | 1181597.5451
43 | 2553544.5549 | 1181478.5429 | 2553556.6851 | 1181485.4918
44 | 2553531.4557 | 1181462.1797 | 2553530.891 | 1181465.9696
45 | 2553556.6851 | 1181485.4918 | 2553560.9935 | 1181487.9598
46 | 2553531.4557 | 1181462.1797 | 2553535.6414 | 1181451.4035
47 | 2553569.564 | 1181492.8004 | 2553561.7096 | 1181488.3701 | 2553560.9935 | 1181487.9598
48 | 2553548.9104 | 1181436.2635 | 2553543.2197 | 1181440.0208 | 2553536.0901 | 1181450.2484 | 2553535.6414 | 1181451.4035
49 | 2553590.7952 | 1181504.7754 | 2553569.564 | 1181492.8004
50 | 2553590.7952 | 1181504.7754 | 2553592.6795 | 1181502.6387
51 | 2553590.7952 | 1181504.7754 | 2553587.6784 | 1181508.5794 | 2553585.0234 | 1181517.593
52 | 2553614.2908 | 1181454.2769 | 2553605.5478 | 1181455.4009 | 2553598.2188 | 1181461.3519
53 | 2553633.221 | 1181473.8185 | 2553614.2908 | 1181454.2769
54 | 2553592.6795 | 1181502.6387 | 2553597.419 | 1181497.2644 | 2553606.4049 | 1181491.3797
55 | 2553582.2762 | 1181527.5447 | 2553582.5222 | 1181526.0845 | 2553585.0234 | 1181517.593
56 | 2553629.7139 | 1181620.1972 | 2553606.4098 | 1181599.9169 | 2553603.1341 | 1181597.5451
57 | 2553614.0103 | 1181486.3991 | 2553606.4049 | 1181491.3797
58 | 2553614.0103 | 1181486.3991 | 2553616.4669 | 1181484.7903
59 | 2553548.9104 | 1181436.2635 | 2553556.2517 | 1181437.1196
60 | 2553548.9104 | 1181436.2635 | 2553543.5454 | 1181428.8861
61 | 2553556.2517 | 1181437.1196 | 2553562.8524 | 1181437.8894 | 2553568.392 | 1181435.3228 | 2553574.0214 | 1181437.1571
62 | 2553528.1958 | 1181394.524 | 2553535.5968 | 1181416.256 | 2553536.8838 | 1181419.7257 | 2553543.5454 | 1181428.8861
63 | 2553578.36 | 1181438.5709 | 2553574.0214 | 1181437.1571
64 | 2553578.36 | 1181438.5709 | 2553589.2855 | 1181442.131 | 2553589.2855 | 1181442.131
65 | 2553633.221 | 1181473.8185 | 2553651.5079 | 1181463.1855
66 | 2553633.221 | 1181473.8185 | 2553629.8572 | 1181476.0214
67 | 2553653.4858 | 1181462.0354 | 2553651.5079 | 1181463.1855
68 | 2553629.8572 | 1181476.0214 | 2553616.5753 | 1181484.7194
69 | 2553666.2992 | 1181454.5851 | 2553653.4858 | 1181462.0354
70 | 2553616.5753 | 1181484.7194 | 2553616.4669 | 1181484.7903
71 | 2553657.7322 | 1181427.312 | 2553655.392 | 1181419.8619 | 2553654.1907 | 1181395.3971
72 | 2553666.2992 | 1181454.5851 | 2553657.7322 | 1181427.312
73 | 2553675.7945 | 1181661.9015 | 2553688.0773 | 1181673.9633
74 | 2553675.7945 | 1181661.9015 | 2553636.7975 | 1181699.613 | 2553623.6138 | 1181700.6078
75 | 2553618.4046 | 1181701.0008 | 2553623.6138 | 1181700.6078
76 | 2553715.3541 | 1181702.7214 | 2553693.4853 | 1181679.2739 | 2553688.0773 | 1181673.9633

## bus_geodata
| x | y | coords
0 | 2553578.9607 | 1181609.1469
1 | 2553564.1888 | 1181596.824
2 | 2553545.3706 | 1181600.8467
3 | 2553533.1299 | 1181592.0815
4 | 2553532.0542 | 1181587.3095
5 | 2553640.7435 | 1181656.2627
6 | 2553642.3195 | 1181657.3807
7 | 2553655.4618 | 1181642.6042
8 | 2553661.79 | 1181648.6101
9 | 2553643.0277 | 1181631.7835
10 | 2553180.06 | 1181474.9062
11 | 2553160.2706 | 1181438.4067
12 | 2553200.9587 | 1181439.4966
13 | 2553386.5055 | 1181452.7201
14 | 2553398.0671 | 1181453.6211
15 | 2553428.7238 | 1181457.5716
16 | 2553439.6146 | 1181460.0167
17 | 2553456.4435 | 1181463.7951
18 | 2553468.3477 | 1181466.4058
19 | 2553483.0066 | 1181468.8155
20 | 2553483.1082 | 1181490.2245
21 | 2553521.0946 | 1181471.3392
22 | 2553529.7791 | 1181473.4322
23 | 2553485.6271 | 1181498.4238
24 | 2553489.0026 | 1181505.9531
25 | 2553495.2265 | 1181516.1862
26 | 2553505.4528 | 1181533
27 | 2553517.697 | 1181545.0204
28 | 2553517.7814 | 1181569.3688
29 | 2553526.4815 | 1181550.0836
30 | 2553517.8199 | 1181579.4826
31 | 2553535.04 | 1181555.0166
32 | 2553514.5492 | 1181584.2803
33 | 2553557.6083 | 1181567.2816
34 | 2553501.058 | 1181604.0706
35 | 2553470.3019 | 1181571.2031
36 | 2553566.9816 | 1181572.2857
37 | 2553571.805 | 1181574.8607
38 | 2553578.6458 | 1181549.0937
39 | 2553582.478 | 1181582.5887
40 | 2553544.5549 | 1181478.5429
41 | 2553530.891 | 1181465.9696
42 | 2553556.6851 | 1181485.4918
43 | 2553531.4557 | 1181462.1797
44 | 2553560.9935 | 1181487.9598
45 | 2553535.6414 | 1181451.4035
46 | 2553569.564 | 1181492.8004
47 | 2553590.7952 | 1181504.7754
48 | 2553598.2188 | 1181461.3519
49 | 2553614.2908 | 1181454.2769
50 | 2553592.6795 | 1181502.6387
51 | 2553585.0234 | 1181517.593
52 | 2553582.2762 | 1181527.5447
53 | 2553603.1341 | 1181597.5451
54 | 2553606.4049 | 1181491.3797
55 | 2553614.0103 | 1181486.3991
56 | 2553548.9104 | 1181436.2635
57 | 2553556.2517 | 1181437.1196
58 | 2553543.5454 | 1181428.8861
59 | 2553574.0214 | 1181437.1571
60 | 2553528.1958 | 1181394.524
61 | 2553578.36 | 1181438.5709
62 | 2553633.221 | 1181473.8185
63 | 2553589.2855 | 1181442.131
64 | 2553651.5079 | 1181463.1855
65 | 2553629.8571 | 1181476.0214
66 | 2553653.4858 | 1181462.0354
67 | 2553616.5753 | 1181484.7194
68 | 2553657.7322 | 1181427.312
69 | 2553654.1907 | 1181395.3971
70 | 2553666.2992 | 1181454.5851
71 | 2553616.4669 | 1181484.7903
72 | 2553675.7945 | 1181661.9015
73 | 2553629.7139 | 1181620.1972
74 | 2553623.6138 | 1181700.6078
75 | 2553618.4046 | 1181701.0008
76 | 2553688.0773 | 1181673.9633
77 | 2553715.3541 | 1181702.7214
78 | 2553517.697 | 1181545.0204

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99737 | -0.018303 | 0.0027078 | 0.00067863
1 | 0.99744 | -0.01778 | 0.00099615 | 0.00024966
2 | 0.99756 | -0.016983 | 0 | 0
3 | 0.99764 | -0.016423 | 0.0033479 | 0.00083906
4 | 0.99769 | -0.016077 | 0 | 0
5 | 0.98818 | -0.08267 | 0.0069745 | 0.001748
6 | 0.9882 | -0.082532 | 0 | 0
7 | 0.9884 | -0.081124 | 0 | 0
8 | 0.98817 | -0.082734 | 0.004391 | 0.0011005
9 | 0.98899 | -0.07691 | 0.0018295 | 0.00045851
10 | 0.9864 | -0.095548 | 0.0096463 | 0.0024176
11 | 0.98698 | -0.091381 | 0 | 0
12 | 0.98756 | -0.08729 | 0.0089508 | 0.0022433
13 | 0.99256 | -0.052035 | 0.00094505 | 0.00023685
14 | 0.99288 | -0.049737 | 0.0029187 | 0.0007315
15 | 0.99389 | -0.04269 | 0.0028058 | 0.00070319
16 | 0.99429 | -0.039839 | 0.0018283 | 0.0004582
17 | 0.99497 | -0.035119 | 0.0041102 | 0.0010301
18 | 0.99552 | -0.031282 | 0.0025513 | 0.00063942
19 | 0.99624 | -0.026231 | 0 | 0
20 | 0.99729 | -0.018913 | 0.0015025 | 0.00037655
21 | 0.98133 | -0.1309 | 0.0040381 | 0.001012
22 | 0.98138 | -0.13053 | 0.0021036 | 0.00052721
23 | 0.99772 | -0.015876 | 0.0035613 | 0.00089254
24 | 0.99818 | -0.012638 | 0.00070509 | 0.00017671
25 | 0.99887 | -0.0078944 | 0.00058185 | 0.00014583
26 | 1 | 0 | -0.16776 | -0.042104
27 | 0.9984 | -0.011053 | 0 | 0
28 | 0.998 | -0.013866 | 0.0017208 | 0.00043126
29 | 0.99757 | -0.016811 | 0.00050704 | 0.00012708
30 | 0.99786 | -0.014861 | 0 | 0
31 | 0.99676 | -0.022404 | 0.00089534 | 0.00022439
32 | 0.99784 | -0.015021 | 0.0014033 | 0.00035171
33 | 0.99468 | -0.036874 | 0.0019733 | 0.00049456
34 | 0.99779 | -0.015344 | 0 | 0
35 | 0.9977 | -0.015956 | 0.0013401 | 0.00033586
36 | 0.99384 | -0.042772 | 0 | 0
37 | 0.9934 | -0.045804 | 0 | 0
38 | 0.99071 | -0.064651 | 0.00039097 | 9.7986e-05
39 | 0.99264 | -0.051168 | 0.0039302 | 0.000985
40 | 0.98234 | -0.12369 | 0.0041985 | 0.0010522
41 | 0.98099 | -0.13332 | 0.0011889 | 0.00029798
42 | 0.98328 | -0.11704 | 0.0022662 | 0.00056795
43 | 0.9808 | -0.1347 | 0 | 0
44 | 0.98363 | -0.11457 | 0.0015397 | 0.00038587
45 | 0.98022 | -0.13884 | 0.0015063 | 0.00037751
46 | 0.98434 | -0.10951 | 0 | 0
47 | 0.98611 | -0.097035 | 0 | 0
48 | 0.98486 | -0.10587 | 0.0034533 | 0.00086547
49 | 0.98495 | -0.10522 | 0 | 0
50 | 0.98604 | -0.097512 | 0.00156 | 0.00039097
51 | 0.98748 | -0.087325 | 0.002301 | 0.00057669
52 | 0.98851 | -0.080089 | 0.00083091 | 0.00020824
53 | 0.99131 | -0.060556 | 0.0038879 | 0.0009744
54 | 0.98566 | -0.10023 | 0.00099592 | 0.0002496
55 | 0.98548 | -0.10151 | 0.00051026 | 0.00012788
56 | 0.97923 | -0.14588 | 0 | 0
57 | 0.97905 | -0.14718 | 0.0095493 | 0.0023933
58 | 0.97902 | -0.14742 | 0.0078344 | 0.0019635
59 | 0.97885 | -0.1486 | 0.0018996 | 0.00047607
60 | 0.97855 | -0.15072 | 0.0083343 | 0.0020888
61 | 0.97881 | -0.14885 | 0.001688 | 0.00042304
62 | 0.98509 | -0.10426 | 0 | 0
63 | 0.97875 | -0.1493 | 0.0037003 | 0.00092739
64 | 0.98491 | -0.10551 | 0.00053118 | 0.00013313
65 | 0.98514 | -0.10388 | 0.0027079 | 0.00067866
66 | 0.9849 | -0.10564 | 0.00090021 | 0.00022561
67 | 0.98542 | -0.10193 | 0.00030165 | 7.5602e-05
68 | 0.98462 | -0.10757 | 0.0028573 | 0.0007161
69 | 0.98456 | -0.10806 | 0.0014705 | 0.00036855
70 | 0.9848 | -0.1063 | 0 | 0
71 | 0.98542 | -0.10191 | 0.0010123 | 0.00025371
72 | 0.98779 | -0.085433 | 0 | 0
73 | 0.98968 | -0.072073 | 0.0055286 | 0.0013856
74 | 0.98708 | -0.090439 | 0.0026833 | 0.00067249
75 | 0.98705 | -0.090683 | 0.0045611 | 0.0011431
76 | 0.98763 | -0.086564 | 0.0037404 | 0.00093743
77 | 0.98748 | -0.087649 | 0.002674 | 0.00067016
78 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0027078 | -0.00067863 | 0.002708 | 0.00067846 | 1.959e-07 | -1.7572e-07 | 0.0040398 | 0.0040398 | 0.0040398 | 0.99737 | -0.018303 | 0.99744 | -0.01778 | 1.4962
1 | -0.0037041 | -0.00092812 | 0.0037045 | 0.00092799 | 4.0825e-07 | -1.2268e-07 | 0.0055258 | 0.0055257 | 0.0055258 | 0.99744 | -0.01778 | 0.99756 | -0.016983 | 2.0466
2 | -0.0037045 | -0.00092799 | 0.0037048 | 0.00092791 | 2.8685e-07 | -8.6242e-08 | 0.0055257 | 0.0055257 | 0.0055257 | 0.99756 | -0.016983 | 0.99764 | -0.016423 | 2.0466
3 | -0.0070527 | -0.001767 | 0.0070531 | 0.001767 | 3.3776e-07 | 6.6032e-08 | 0.010519 | 0.010519 | 0.010519 | 0.99764 | -0.016423 | 0.99769 | -0.016077 | 3.896
4 | -0.0070531 | -0.001767 | 0.0070542 | 0.0017673 | 1.187e-06 | 2.32e-07 | 0.010519 | 0.010519 | 0.010519 | 0.99769 | -0.016077 | 0.99786 | -0.014861 | 3.896
5 | -0.0069745 | -0.001748 | 0.0069747 | 0.001748 | 1.3299e-07 | 2.6396e-08 | 0.010502 | 0.010502 | 0.010502 | 0.98818 | -0.08267 | 0.9882 | -0.082532 | 3.8898
6 | -0.0069747 | -0.001748 | 0.006976 | 0.0017483 | 1.3595e-06 | 2.6977e-07 | 0.010502 | 0.010502 | 0.010502 | 0.9882 | -0.082532 | 0.9884 | -0.081124 | 3.8898
7 | 0.018065 | 0.0045277 | -0.018061 | -0.0045263 | 4.0269e-06 | 1.437e-06 | 0.027197 | 0.027197 | 0.027197 | 0.9884 | -0.081124 | 0.98817 | -0.082734 | 10.0731
8 | -0.025041 | -0.006276 | 0.025056 | 0.0062814 | 1.4618e-05 | 5.411e-06 | 0.0377 | 0.037699 | 0.0377 | 0.9884 | -0.081124 | 0.98899 | -0.07691 | 13.9628
9 | 0.01367 | 0.0034258 | -0.013665 | -0.0034241 | 5.1054e-06 | 1.7164e-06 | 0.020585 | 0.020585 | 0.020585 | 0.98817 | -0.082734 | 0.98779 | -0.085433 | 7.6242
10 | -0.026886 | -0.0067399 | 0.026904 | 0.0067466 | 1.8022e-05 | 6.7048e-06 | 0.040452 | 0.040452 | 0.040452 | 0.98899 | -0.07691 | 0.98968 | -0.072073 | 14.9822
11 | -0.0096463 | -0.0024176 | 0.0096519 | 0.0024192 | 5.5666e-06 | 1.6029e-06 | 0.014552 | 0.014552 | 0.014552 | 0.9864 | -0.095548 | 0.98698 | -0.091381 | 5.3896
12 | -0.0096519 | -0.0024192 | 0.0096573 | 0.0024208 | 5.4692e-06 | 1.5742e-06 | 0.014552 | 0.014551 | 0.014552 | 0.98698 | -0.091381 | 0.98756 | -0.08729 | 5.3895
13 | -0.018608 | -0.004664 | 0.018699 | 0.0046968 | 9.1248e-05 | 3.2703e-05 | 0.028038 | 0.028037 | 0.028038 | 0.98756 | -0.08729 | 0.99256 | -0.052035 | 10.3845
14 | -0.019644 | -0.0049336 | 0.019651 | 0.0049359 | 6.2778e-06 | 2.2646e-06 | 0.029454 | 0.029454 | 0.029454 | 0.99256 | -0.052035 | 0.99288 | -0.049737 | 10.9089
15 | -0.022569 | -0.0056674 | 0.022592 | 0.0056755 | 2.2124e-05 | 8.108e-06 | 0.033828 | 0.033828 | 0.033828 | 0.99288 | -0.049737 | 0.99389 | -0.04269 | 12.529
16 | -0.025397 | -0.0063787 | 0.025407 | 0.0063824 | 1.0073e-05 | 3.7294e-06 | 0.038029 | 0.038029 | 0.038029 | 0.99389 | -0.04269 | 0.99429 | -0.039839 | 14.0847
17 | -0.027236 | -0.0068406 | 0.027254 | 0.0068473 | 1.7885e-05 | 6.655e-06 | 0.040765 | 0.040765 | 0.040765 | 0.99429 | -0.039839 | 0.99497 | -0.035119 | 15.0981
18 | -0.031364 | -0.0078774 | 0.03138 | 0.0078836 | 1.6738e-05 | 6.2793e-06 | 0.046912 | 0.046912 | 0.046912 | 0.99497 | -0.035119 | 0.99552 | -0.031282 | 17.3747
19 | -0.033932 | -0.0085231 | 0.033956 | 0.008532 | 2.3852e-05 | 8.9805e-06 | 0.050725 | 0.050725 | 0.050725 | 0.99552 | -0.031282 | 0.99624 | -0.026231 | 18.7871
20 | -0.033956 | -0.008532 | 0.03399 | 0.0085451 | 3.4612e-05 | 1.3031e-05 | 0.050725 | 0.050725 | 0.050725 | 0.99624 | -0.026231 | 0.99729 | -0.018913 | 18.7871
21 | -0.035493 | -0.0089216 | 0.035508 | 0.0089273 | 1.5016e-05 | 5.6634e-06 | 0.052967 | 0.052967 | 0.052967 | 0.99729 | -0.018913 | 0.99772 | -0.015876 | 19.6173
22 | -0.0040381 | -0.001012 | 0.0040383 | 0.001012 | 2.0899e-07 | -3.2486e-08 | 0.0061231 | 0.006123 | 0.0061231 | 0.98133 | -0.1309 | 0.98138 | -0.13053 | 2.2678
23 | -0.041928 | -0.010518 | 0.041967 | 0.010533 | 3.979e-05 | 1.5104e-05 | 0.063576 | 0.063576 | 0.063576 | 0.98138 | -0.13053 | 0.98234 | -0.12369 | 23.5466
24 | 0.035786 | 0.0089784 | -0.035772 | -0.0089732 | 1.3863e-05 | 5.2366e-06 | 0.054263 | 0.054263 | 0.054263 | 0.98138 | -0.13053 | 0.98099 | -0.13332 | 20.0975
25 | -0.039069 | -0.0098198 | 0.039087 | 0.0098265 | 1.7623e-05 | 6.6693e-06 | 0.058278 | 0.058278 | 0.058278 | 0.99772 | -0.015876 | 0.99818 | -0.012638 | 21.5845
26 | -0.039792 | -0.010003 | 0.039818 | 0.010013 | 2.6307e-05 | 9.9615e-06 | 0.059329 | 0.059329 | 0.059329 | 0.99818 | -0.012638 | 0.99887 | -0.0078944 | 21.9737
27 | -0.0404 | -0.010159 | 0.040444 | 0.010176 | 4.4497e-05 | 1.6856e-05 | 0.060196 | 0.060196 | 0.060196 | 0.99887 | -0.0078944 | 1 | 0 | 22.2948
28 | 0.12651 | 0.031928 | -0.12632 | -0.031853 | 0.000196 | 7.4919e-05 | 0.18833 | 0.18833 | 0.18833 | 1 | 0 | 0.9984 | -0.011053 | 34.8764
29 | 0.011525 | 0.002887 | -0.01152 | -0.0028856 | 4.4822e-06 | 1.4056e-06 | 0.017176 | 0.017176 | 0.017176 | 0.9984 | -0.011053 | 0.998 | -0.013866 | 6.3614
30 | 0.11479 | 0.028966 | -0.1147 | -0.02893 | 9.2671e-05 | 3.5378e-05 | 0.17116 | 0.17116 | 0.17116 | 0.9984 | -0.011053 | 0.99757 | -0.016811 | 31.6958
31 | 0.0097993 | 0.0024543 | -0.0097979 | -0.0024539 | 1.3471e-06 | 3.8599e-07 | 0.01461 | 0.01461 | 0.01461 | 0.998 | -0.013866 | 0.99786 | -0.014861 | 5.4112
32 | 0.11419 | 0.028803 | -0.1141 | -0.028769 | 8.9492e-05 | 3.4162e-05 | 0.1704 | 0.1704 | 0.1704 | 0.99757 | -0.016811 | 0.99676 | -0.022404 | 31.5557
33 | 0.0027437 | 0.00068668 | -0.0027436 | -0.00068673 | 6.0642e-08 | -5.2527e-08 | 0.0040911 | 0.0040911 | 0.0040911 | 0.99786 | -0.014861 | 0.99784 | -0.015021 | 1.5152
34 | 0.11321 | 0.028545 | -0.11298 | -0.028457 | 0.00022908 | 8.7441e-05 | 0.16906 | 0.16906 | 0.16906 | 0.99676 | -0.022404 | 0.99468 | -0.036874 | 31.3082
35 | 0.0013403 | 0.00033502 | -0.0013402 | -0.00033531 | 5.9687e-08 | -2.899e-07 | 0.0019984 | 0.0019985 | 0.0019985 | 0.99784 | -0.015021 | 0.99779 | -0.015344 | 0.74017
36 | 0.11101 | 0.027963 | -0.11092 | -0.027928 | 9.1475e-05 | 3.4907e-05 | 0.16611 | 0.16611 | 0.16611 | 0.99468 | -0.036874 | 0.99384 | -0.042772 | 30.7616
37 | 0.0013402 | 0.00033531 | -0.0013401 | -0.00033586 | 1.1335e-07 | -5.5037e-07 | 0.0019985 | 0.0019987 | 0.0019987 | 0.99779 | -0.015344 | 0.9977 | -0.015956 | 0.74025
38 | 0.11092 | 0.027928 | -0.11087 | -0.02791 | 4.6971e-05 | 1.7925e-05 | 0.16611 | 0.16611 | 0.16611 | 0.99384 | -0.042772 | 0.9934 | -0.045804 | 30.7616
39 | 0.070488 | 0.01777 | -0.070303 | -0.017699 | 0.00018558 | 7.1034e-05 | 0.10562 | 0.10562 | 0.10562 | 0.9934 | -0.045804 | 0.99071 | -0.064651 | 39.1189
40 | 0.04038 | 0.01014 | -0.04035 | -0.010129 | 3.0088e-05 | 1.1402e-05 | 0.060492 | 0.060492 | 0.060492 | 0.9934 | -0.045804 | 0.99264 | -0.051168 | 22.4043
41 | 0.069912 | 0.017601 | -0.069761 | -0.017543 | 0.00015043 | 5.7579e-05 | 0.10503 | 0.10503 | 0.10503 | 0.99071 | -0.064651 | 0.98851 | -0.080089 | 38.9015
42 | 0.036419 | 0.009144 | -0.036372 | -0.0091261 | 4.7441e-05 | 1.7917e-05 | 0.0546 | 0.0546 | 0.0546 | 0.99264 | -0.051168 | 0.99131 | -0.060556 | 20.2223
43 | -0.046166 | -0.011585 | 0.046208 | 0.011601 | 4.2665e-05 | 1.6233e-05 | 0.069936 | 0.069935 | 0.069936 | 0.98234 | -0.12369 | 0.98328 | -0.11704 | 25.902
44 | 0.034583 | 0.0086752 | -0.034576 | -0.0086727 | 6.58e-06 | 2.4824e-06 | 0.05246 | 0.05246 | 0.05246 | 0.98099 | -0.13332 | 0.9808 | -0.1347 | 19.4296
45 | -0.048475 | -0.012169 | 0.048491 | 0.012176 | 1.6676e-05 | 6.351e-06 | 0.073365 | 0.073365 | 0.073365 | 0.98328 | -0.11704 | 0.98363 | -0.11457 | 27.1722
46 | 0.034576 | 0.0086727 | -0.034556 | -0.0086652 | 1.9853e-05 | 7.4899e-06 | 0.05246 | 0.05246 | 0.05246 | 0.9808 | -0.1347 | 0.98022 | -0.13884 | 19.4296
47 | -0.050031 | -0.012561 | 0.050066 | 0.012575 | 3.5191e-05 | 1.341e-05 | 0.075694 | 0.075694 | 0.075694 | 0.98363 | -0.11457 | 0.98434 | -0.10951 | 28.0348
48 | 0.03305 | 0.0082877 | -0.033018 | -0.0082756 | 3.2243e-05 | 1.2143e-05 | 0.050173 | 0.050173 | 0.050173 | 0.98022 | -0.13884 | 0.97923 | -0.14588 | 18.5828
49 | -0.050066 | -0.012575 | 0.050153 | 0.012608 | 8.6964e-05 | 3.3138e-05 | 0.075694 | 0.075694 | 0.075694 | 0.98434 | -0.10951 | 0.98611 | -0.097035 | 28.0348
50 | 0.016317 | 0.0040892 | -0.016316 | -0.0040888 | 1.0777e-06 | 3.7816e-07 | 0.024622 | 0.024622 | 0.024622 | 0.98611 | -0.097035 | 0.98604 | -0.097512 | 9.1193
51 | -0.06647 | -0.016697 | 0.06656 | 0.016731 | 8.9886e-05 | 3.4389e-05 | 0.10032 | 0.10032 | 0.10032 | 0.98611 | -0.097035 | 0.98748 | -0.087325 | 37.1541
52 | -0.0034533 | -0.00086547 | 0.0034536 | 0.00086535 | 3.101e-07 | -1.1306e-07 | 0.0052175 | 0.0052174 | 0.0052175 | 0.98486 | -0.10587 | 0.98495 | -0.10522 | 1.9324
53 | -0.0034536 | -0.00086535 | 0.003454 | 0.00086519 | 4.6155e-07 | -1.6837e-07 | 0.0052174 | 0.0052173 | 0.0052174 | 0.98495 | -0.10522 | 0.98509 | -0.10426 | 1.9324
54 | 0.014756 | 0.0036978 | -0.01475 | -0.0036959 | 5.5408e-06 | 1.9027e-06 | 0.022268 | 0.022268 | 0.022268 | 0.98604 | -0.097512 | 0.98566 | -0.10023 | 8.2474
55 | -0.068861 | -0.017308 | 0.068931 | 0.017335 | 6.9449e-05 | 2.6579e-05 | 0.10378 | 0.10378 | 0.10378 | 0.98748 | -0.087325 | 0.98851 | -0.080089 | 38.4382
56 | 0.032484 | 0.0081517 | -0.032432 | -0.0081322 | 5.1841e-05 | 1.9489e-05 | 0.048764 | 0.048764 | 0.048764 | 0.99131 | -0.060556 | 0.98968 | -0.072073 | 18.0609
57 | 0.013755 | 0.0034463 | -0.013752 | -0.0034455 | 2.446e-06 | 8.249e-07 | 0.020765 | 0.020765 | 0.020765 | 0.98566 | -0.10023 | 0.98548 | -0.10151 | 7.6906
58 | 0.013242 | 0.0033176 | -0.013241 | -0.0033174 | 7.3253e-07 | 2.4433e-07 | 0.019994 | 0.019994 | 0.019994 | 0.98548 | -0.10151 | 0.98542 | -0.10191 | 7.4052
59 | 0.016842 | 0.0042211 | -0.016839 | -0.00422 | 3.0208e-06 | 1.0689e-06 | 0.025593 | 0.025593 | 0.025593 | 0.97923 | -0.14588 | 0.97905 | -0.14718 | 9.4788
60 | 0.016176 | 0.0040544 | -0.016172 | -0.0040532 | 3.4392e-06 | 1.208e-06 | 0.024581 | 0.024581 | 0.024581 | 0.97923 | -0.14588 | 0.97902 | -0.14742 | 9.104
61 | 0.0072897 | 0.0018268 | -0.0072882 | -0.0018265 | 1.4302e-06 | 3.1531e-07 | 0.011079 | 0.011079 | 0.011079 | 0.97905 | -0.14718 | 0.97885 | -0.1486 | 4.1034
62 | 0.0083381 | 0.0020897 | -0.0083343 | -0.0020888 | 3.8069e-06 | 9.8677e-07 | 0.012673 | 0.012673 | 0.012673 | 0.97902 | -0.14742 | 0.97855 | -0.15072 | 4.6938
63 | 0.0053887 | 0.0013504 | -0.0053885 | -0.0013504 | 1.9107e-07 | 1.6131e-08 | 0.0081917 | 0.0081917 | 0.0081917 | 0.97885 | -0.1486 | 0.97881 | -0.14885 | 3.034
64 | 0.0037005 | 0.00092733 | -0.0037003 | -0.00092739 | 2.2693e-07 | -5.7145e-08 | 0.0056256 | 0.0056257 | 0.0056257 | 0.97881 | -0.14885 | 0.97875 | -0.1493 | 2.0836
65 | 0.0057615 | 0.001443 | -0.0057605 | -0.0014429 | 9.9971e-07 | 1.1525e-07 | 0.0087027 | 0.0087028 | 0.0087028 | 0.98509 | -0.10426 | 0.98491 | -0.10551 | 3.2232
66 | -0.0092156 | -0.0023082 | 0.009216 | 0.0023084 | 4.8618e-07 | 1.358e-07 | 0.01392 | 0.01392 | 0.01392 | 0.98509 | -0.10426 | 0.98514 | -0.10388 | 5.1555
67 | 0.0052294 | 0.0013098 | -0.0052293 | -0.0013098 | 8.911e-08 | 5.1554e-09 | 0.0079003 | 0.0079003 | 0.0079003 | 0.98491 | -0.10551 | 0.9849 | -0.10564 | 2.926
68 | -0.011924 | -0.002987 | 0.011927 | 0.002988 | 3.2134e-06 | 1.0337e-06 | 0.01801 | 0.01801 | 0.01801 | 0.98514 | -0.10388 | 0.98542 | -0.10193 | 6.6704
69 | 0.0043291 | 0.0010842 | -0.0043287 | -0.0010842 | 3.9562e-07 | -3.6445e-08 | 0.0065402 | 0.0065403 | 0.0065403 | 0.9849 | -0.10564 | 0.9848 | -0.1063 | 2.4223
70 | -0.012229 | -0.0030636 | 0.012229 | 0.0030637 | 2.7563e-08 | 8.9511e-09 | 0.018466 | 0.018466 | 0.018466 | 0.98542 | -0.10193 | 0.98542 | -0.10191 | 6.8391
71 | 0.0014706 | 0.00036817 | -0.0014705 | -0.00036855 | 9.9558e-08 | -3.7254e-07 | 0.0022223 | 0.0022225 | 0.0022225 | 0.98462 | -0.10757 | 0.98456 | -0.10806 | 0.82314
72 | -0.0043279 | -0.0010843 | 0.0043287 | 0.0010842 | 7.6305e-07 | -7.0182e-08 | 0.0065404 | 0.0065403 | 0.0065404 | 0.98462 | -0.10757 | 0.9848 | -0.1063 | 2.4224
73 | 0.0064157 | 0.0016074 | -0.0064147 | -0.0016072 | 1.0034e-06 | 1.6558e-07 | 0.0096646 | 0.0096646 | 0.0096646 | 0.98779 | -0.085433 | 0.98763 | -0.086564 | 3.5795
74 | 0.0072496 | 0.0018167 | -0.0072445 | -0.0018156 | 5.0212e-06 | 1.0682e-06 | 0.010921 | 0.010921 | 0.010921 | 0.98779 | -0.085433 | 0.98708 | -0.090439 | 4.0448
75 | 0.0045613 | 0.0011431 | -0.0045611 | -0.0011431 | 1.5412e-07 | -7.4955e-09 | 0.0068761 | 0.0068761 | 0.0068761 | 0.98708 | -0.090439 | 0.98705 | -0.090683 | 2.5467
76 | 0.0026744 | 0.00066981 | -0.002674 | -0.00067016 | 4.016e-07 | -3.5275e-07 | 0.0040292 | 0.0040294 | 0.0040294 | 0.98763 | -0.086564 | 0.98748 | -0.087649 | 1.4924

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16929 | 0.042487

## res_load
| p_mw | q_mvar
0 | 0.0027078 | 0.00067863
1 | 0.00099615 | 0.00024966
2 | 0.0033479 | 0.00083906
3 | 0.0069745 | 0.001748
4 | 0.004391 | 0.0011005
5 | 0.0018295 | 0.00045851
6 | 0.0096463 | 0.0024176
7 | 0.0089508 | 0.0022433
8 | 0.00094505 | 0.00023685
9 | 0.0029187 | 0.0007315
10 | 0.0028058 | 0.00070319
11 | 0.0018283 | 0.0004582
12 | 0.0041102 | 0.0010301
13 | 0.0025513 | 0.00063942
14 | 0.0015025 | 0.00037655
15 | 0.0040381 | 0.001012
16 | 0.0021036 | 0.00052721
17 | 0.0035613 | 0.00089254
18 | 0.00070509 | 0.00017671
19 | 0.00058185 | 0.00014583
20 | 0.0015279 | 0.00038292
21 | 0.0017208 | 0.00043126
22 | 0.00050704 | 0.00012708
23 | 0.00089534 | 0.00022439
24 | 0.0014033 | 0.00035171
25 | 0.0019733 | 0.00049456
26 | 0.0013401 | 0.00033586
27 | 0.00039097 | 9.7986e-05
28 | 0.0039302 | 0.000985
29 | 0.0041985 | 0.0010522
30 | 0.0011889 | 0.00029798
31 | 0.0022662 | 0.00056795
32 | 0.0015397 | 0.00038587
33 | 0.0015063 | 0.00037751
34 | 0.0034533 | 0.00086547
35 | 0.00156 | 0.00039097
36 | 0.002301 | 0.00057669
37 | 0.00083091 | 0.00020824
38 | 0.0038879 | 0.0009744
39 | 0.00099592 | 0.0002496
40 | 0.00051026 | 0.00012788
41 | 0.0095493 | 0.0023933
42 | 0.0078344 | 0.0019635
43 | 0.0018996 | 0.00047607
44 | 0.0083343 | 0.0020888
45 | 0.001688 | 0.00042304
46 | 0.0037003 | 0.00092739
47 | 0.00053118 | 0.00013313
48 | 0.0027079 | 0.00067866
49 | 0.00090021 | 0.00022561
50 | 0.00030165 | 7.5602e-05
51 | 0.0028573 | 0.0007161
52 | 0.0014705 | 0.00036855
53 | 0.0010123 | 0.00025371
54 | 0.0055286 | 0.0013856
55 | 0.0026833 | 0.00067249
56 | 0.0045611 | 0.0011431
57 | 0.0037404 | 0.00093743
58 | 0.002674 | 0.00067016

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1