## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2041-2_1_3_node_47 | 0.4 | n |  | TRUE
1 | bus_LV_2041-2_1_3_node_48 | 0.4 | n |  | TRUE
2 | bus_LV_2041-2_1_3_node_49 | 0.4 | n |  | TRUE
3 | bus_LV_2041-2_1_3_node_50 | 0.4 | n |  | TRUE
4 | bus_LV_2041-2_1_3_node_51 | 0.4 | n |  | TRUE
5 | bus_LV_2041-2_1_3_node_52 | 0.4 | n |  | TRUE
6 | bus_LV_2041-2_1_3_node_71 | 0.4 | n |  | TRUE
7 | bus_LV_2041-2_1_3_node_82 | 0.4 | n |  | TRUE
8 | bus_LV_2041-2_1_3_node_85 | 0.4 | n |  | TRUE
9 | bus_LV_2041-2_1_3_node_53 | 0.4 | n |  | TRUE
10 | bus_LV_2041-2_1_3_node_54 | 0.4 | n |  | TRUE
11 | bus_LV_2041-2_1_3_node_55 | 0.4 | n |  | TRUE
12 | bus_LV_2041-2_1_3_node_56 | 0.4 | n |  | TRUE
13 | bus_LV_2041-2_1_3_node_57 | 0.4 | n |  | TRUE
14 | bus_LV_2041-2_1_3_node_58 | 0.4 | n |  | TRUE
15 | bus_LV_2041-2_1_3_node_59 | 0.4 | n |  | TRUE
16 | bus_LV_2041-2_1_3_node_76 | 0.4 | n |  | TRUE
17 | bus_LV_2041-2_1_3_node_65 | 0.4 | n |  | TRUE
18 | bus_LV_2041-2_1_3_node_67 | 0.4 | n |  | TRUE
19 | bus_LV_2041-2_1_3_node_69 | 0.4 | n |  | TRUE
20 | bus_LV_2041-2_1_3_node_60 | 0.4 | n |  | TRUE
21 | bus_LV_2041-2_1_3_node_61 | 0.4 | n |  | TRUE
22 | bus_LV_2041-2_1_3_node_62 | 0.4 | n |  | TRUE
23 | bus_LV_2041-2_1_3_node_63 | 0.4 | n |  | TRUE
24 | bus_LV_2041-2_1_3_node_64 | 0.4 | n |  | TRUE
25 | bus_LV_2041-2_1_3_node_72 | 0.4 | n |  | TRUE
26 | bus_LV_2041-2_1_3_node_70 | 0.4 | n |  | TRUE
27 | bus_LV_2041-2_1_3_node_68 | 0.4 | n |  | TRUE
28 | bus_LV_2041-2_1_3_node_90 | 0.4 | n |  | TRUE
29 | bus_LV_2041-2_1_3_node_81 | 0.4 | n |  | TRUE
30 | bus_LV_2041-2_1_3_node_73 | 0.4 | n |  | TRUE
31 | bus_LV_2041-2_1_3_node_75 | 0.4 | n |  | TRUE
32 | bus_LV_2041-2_1_3_node_78 | 0.4 | n |  | TRUE
33 | bus_LV_2041-2_1_3_node_92 | 0.4 | n |  | TRUE
34 | bus_LV_2041-2_1_3_node_80 | 0.4 | n |  | TRUE
35 | bus_LV_2041-2_1_3_node_79 | 0.4 | n |  | TRUE
36 | bus_LV_2041-2_1_3_node_91 | 0.4 | n |  | TRUE
37 | bus_LV_2041-2_1_3_node_83 | 0.4 | n |  | TRUE
38 | bus_LV_2041-2_1_3_node_84 | 0.4 | n |  | TRUE
39 | bus_MV_377_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2041-2_1_3_load_47 | 0 | 0.00331 | 0.00082958 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2041-2_1_3_load_48 | 1 | 0.0075044 | 0.0018808 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2041-2_1_3_load_49 | 2 | 0.0026671 | 0.00066843 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2041-2_1_3_load_71 | 6 | 0.0070077 | 0.0017563 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2041-2_1_3_load_82 | 7 | 0.010533 | 0.0026399 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2041-2_1_3_load_85 | 8 | 0.0038399 | 0.00096236 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2041-2_1_3_load_53 | 9 | 0.0023781 | 0.00059601 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2041-2_1_3_load_54 | 10 | 0.0035245 | 0.00088331 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2041-2_1_3_load_56 | 12 | 0.0017728 | 0.00044432 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2041-2_1_3_load_57 | 13 | 0.0022941 | 0.00057497 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2041-2_1_3_load_58 | 14 | 0.0043199 | 0.0010827 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2041-2_1_3_load_59 | 15 | 0.0051595 | 0.0012931 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2041-2_1_3_load_76 | 16 | 0.0022859 | 0.00057291 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2041-2_1_3_load_65 | 17 | 0.001636 | 0.00041002 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2041-2_1_3_load_67 | 18 | 0.0015276 | 0.00038284 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2041-2_1_3_load_69 | 19 | 0.0009101 | 0.00022809 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2041-2_1_3_load_60 | 20 | 0.0091447 | 0.0022919 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2041-2_1_3_load_61 | 21 | 0.0061046 | 0.0015299 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2041-2_1_3_load_62 | 22 | 0.0097501 | 0.0024436 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2041-2_1_3_load_63 | 23 | 0.002242 | 0.00056189 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2041-2_1_3_load_72 | 25 | 0.0092428 | 0.0023165 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2041-2_1_3_load_68 | 27 | 0.0022045 | 0.0005525 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2041-2_1_3_load_90 | 28 | 0.0081525 | 0.0020432 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2041-2_1_3_load_73 | 30 | 0.0024568 | 0.00061574 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2041-2_1_3_load_75 | 31 | 0.0014503 | 0.00036348 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2041-2_1_3_load_92 | 33 | 0.0013116 | 0.00032872 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2041-2_1_3_load_79 | 35 | 0.010104 | 0.0025323 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2041-2_1_3_load_91 | 36 | 0.0015881 | 0.00039802 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2041-2_1_3_load_83 | 37 | 0.012633 | 0.003166 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2041-2_1_3_load_84 | 38 | 0.012633 | 0.003166 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2041-2_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.029257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2041-2_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.015204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2041-2_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.018208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2041-2_1_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.017429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2041-2_1_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.04809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2041-2_1_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0036804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2041-2_1_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.021649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2041-2_1_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.074465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2041-2_1_3_line_8 | NAYY 4x150 SE | 6 | 24 | 0.046941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2041-2_1_3_line_9 | NAYY 4x150 SE | 7 | 37 | 0.038618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2041-2_1_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.0051371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2041-2_1_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.017494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2041-2_1_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.022468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2041-2_1_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.024004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2041-2_1_3_line_14 | NAYY 4x150 SE | 11 | 14 | 0.03019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2041-2_1_3_line_15 | NAYY 4x150 SE | 11 | 15 | 0.062953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2041-2_1_3_line_16 | NAYY 4x150 SE | 12 | 16 | 0.025466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2041-2_1_3_line_17 | NAYY 4x150 SE | 13 | 17 | 0.030247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2041-2_1_3_line_18 | NAYY 4x150 SE | 14 | 18 | 0.018792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2041-2_1_3_line_19 | NAYY 4x150 SE | 15 | 19 | 0.0042357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2041-2_1_3_line_20 | NAYY 4x150 SE | 16 | 31 | 0.0016821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2041-2_1_3_line_21 | NAYY 4x150 SE | 18 | 27 | 0.029262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2041-2_1_3_line_22 | NAYY 4x150 SE | 19 | 24 | 0.028709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2041-2_1_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.0024113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2041-2_1_3_line_24 | NAYY 4x150 SE | 20 | 22 | 0.034693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2041-2_1_3_line_25 | NAYY 4x150 SE | 21 | 23 | 0.027954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2041-2_1_3_line_26 | NAYY 4x150 SE | 22 | 24 | 0.024755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_2041-2_1_3_line_27 | NAYY 4x150 SE | 23 | 25 | 0.0039805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2041-2_1_3_line_28 | NAYY 4x150 SE | 24 | 26 | 0.03059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2041-2_1_3_line_29 | NAYY 4x150 SE | 25 | 30 | 0.001943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2041-2_1_3_line_30 | NAYY 4x150 SE | 26 | 28 | 0.008185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2041-2_1_3_line_31 | NAYY 4x150 SE | 26 | 29 | 0.002711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2041-2_1_3_line_32 | NAYY 4x150 SE | 29 | 36 | 0.022243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2041-2_1_3_line_33 | NAYY 4x150 SE | 29 | 34 | 0.022079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2041-2_1_3_line_34 | NAYY 4x150 SE | 32 | 33 | 0.018946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2041-2_1_3_line_35 | NAYY 4x150 SE | 32 | 34 | 0.001342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2041-2_1_3_line_36 | NAYY 4x150 SE | 34 | 35 | 0.021003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2041-2_1_3_line_37 | NAYY 4x150 SE | 37 | 38 | 0.037706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2041-2_1_3_trafo_62 | 0.25 MVA 20/0.4 kV | 39 | 22 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2565569.8831 | 1193399.1927 | 2565578.6932 | 1193427.092
1 | 2565569.8831 | 1193399.1927 | 2565565.3049 | 1193384.6948
2 | 2565584.176 | 1193444.4549 | 2565578.6932 | 1193427.092
3 | 2565584.176 | 1193444.4549 | 2565568.5982 | 1193452.3602
4 | 2565628.2822 | 1193425.0011 | 2565584.176 | 1193444.4549
5 | 2565568.5982 | 1193452.3602 | 2565565.3085 | 1193454.0103
6 | 2565568.5982 | 1193452.3602 | 2565576.9076 | 1193472.3515
7 | 2565628.2822 | 1193425.0011 | 2565612.7876 | 1193369.3936 | 2565608.5032 | 1193353.2119
8 | 2565526.7877 | 1193479.9388 | 2565541.378 | 1193466.0136 | 2565565.3085 | 1193454.0103
9 | 2565576.9076 | 1193472.3515 | 2565578.228 | 1193475.5283 | 2565593.8191 | 1193507.0625
10 | 2565439.2306 | 1193522.4895 | 2565436.2232 | 1193518.3247
11 | 2565449.472 | 1193536.6725 | 2565439.2306 | 1193522.4895
12 | 2565436.2232 | 1193518.3247 | 2565423.07 | 1193500.1093
13 | 2565449.472 | 1193536.6725 | 2565463.4902 | 1193556.1574
14 | 2565449.472 | 1193536.6725 | 2565424.986 | 1193554.3328
15 | 2565449.472 | 1193536.6725 | 2565500.2265 | 1193499.4292
16 | 2565423.07 | 1193500.1093 | 2565408.1619 | 1193479.4635
17 | 2565463.4902 | 1193556.1574 | 2565481.1545 | 1193580.7102
18 | 2565424.986 | 1193554.3328 | 2565409.7449 | 1193565.3252
19 | 2565503.6414 | 1193496.9234 | 2565500.2265 | 1193499.4292
20 | 2565407.1772 | 1193478.0997 | 2565408.1619 | 1193479.4635
21 | 2565409.7449 | 1193565.3252 | 2565386.0114 | 1193582.4428
22 | 2565526.7877 | 1193479.9388 | 2565503.6414 | 1193496.9234
23 | 2565555.5866 | 1193531.9444 | 2565556.7548 | 1193534.0539
24 | 2565555.5866 | 1193531.9444 | 2565538.7799 | 1193501.5946
25 | 2565570.2969 | 1193558.5086 | 2565556.7548 | 1193534.0539
26 | 2565526.7877 | 1193479.9388 | 2565538.7799 | 1193501.5946
27 | 2565570.2969 | 1193558.5086 | 2565572.2253 | 1193561.9908
28 | 2565526.7877 | 1193479.9388 | 2565510.686 | 1193453.9066
29 | 2565572.2253 | 1193561.9908 | 2565573.1665 | 1193563.6906
30 | 2565510.686 | 1193453.9066 | 2565517.9036 | 1193450.0072
31 | 2565510.686 | 1193453.9066 | 2565509.2551 | 1193451.6025
32 | 2565509.2551 | 1193451.6025 | 2565501.84 | 1193455.6032 | 2565490.2848 | 1193463.263
33 | 2565509.2551 | 1193451.6025 | 2565497.6308 | 1193432.8151
34 | 2565496.923 | 1193431.6741 | 2565480.655 | 1193441.4625
35 | 2565496.923 | 1193431.6741 | 2565497.6308 | 1193432.8151
36 | 2565497.6308 | 1193432.8151 | 2565515.8686 | 1193422.3992
37 | 2565610.5305 | 1193540.8624 | 2565593.8191 | 1193507.0625

## bus_geodata
| x | y | coords
0 | 2565569.8831 | 1193399.1927
1 | 2565578.6932 | 1193427.092
2 | 2565565.3049 | 1193384.6948
3 | 2565584.176 | 1193444.4549
4 | 2565568.5982 | 1193452.3602
5 | 2565628.2822 | 1193425.0011
6 | 2565565.3085 | 1193454.0103
7 | 2565576.9076 | 1193472.3515
8 | 2565608.5032 | 1193353.2119
9 | 2565439.2306 | 1193522.4895
10 | 2565436.2232 | 1193518.3247
11 | 2565449.472 | 1193536.6725
12 | 2565423.07 | 1193500.1093
13 | 2565463.4902 | 1193556.1574
14 | 2565424.986 | 1193554.3328
15 | 2565500.2265 | 1193499.4292
16 | 2565408.1619 | 1193479.4635
17 | 2565481.1545 | 1193580.7102
18 | 2565409.7449 | 1193565.3252
19 | 2565503.6414 | 1193496.9234
20 | 2565555.5866 | 1193531.9444
21 | 2565556.7548 | 1193534.0539
22 | 2565538.7799 | 1193501.5946
23 | 2565570.2969 | 1193558.5086
24 | 2565526.7877 | 1193479.9388
25 | 2565572.2253 | 1193561.9908
26 | 2565510.686 | 1193453.9066
27 | 2565386.0114 | 1193582.4428
28 | 2565517.9036 | 1193450.0072
29 | 2565509.2551 | 1193451.6025
30 | 2565573.1665 | 1193563.6906
31 | 2565407.1772 | 1193478.0997
32 | 2565496.923 | 1193431.6741
33 | 2565480.655 | 1193441.4625
34 | 2565497.6308 | 1193432.8151
35 | 2565515.8686 | 1193422.3992
36 | 2565490.2849 | 1193463.263
37 | 2565593.8191 | 1193507.0625
38 | 2565610.5305 | 1193540.8624
39 | 2565526.7877 | 1193479.9388

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99266 | -0.051417 | 0.00331 | 0.00082958
1 | 0.99291 | -0.049645 | 0.0075044 | 0.0018808
2 | 0.9926 | -0.051828 | 0.0026671 | 0.00066843
3 | 0.99326 | -0.04716 | 0 | 0
4 | 0.9937 | -0.044104 | 0 | 0
5 | 0.993 | -0.049033 | 0 | 0
6 | 0.99398 | -0.042128 | 0.0070077 | 0.0017563
7 | 0.99258 | -0.051948 | 0.010533 | 0.0026399
8 | 0.99259 | -0.051931 | 0.0038399 | 0.00096236
9 | 0.99425 | -0.040286 | 0.0023781 | 0.00059601
10 | 0.99418 | -0.040755 | 0.0035245 | 0.00088331
11 | 0.99454 | -0.03827 | 0 | 0
12 | 0.99401 | -0.042006 | 0.0017728 | 0.00044432
13 | 0.9944 | -0.039223 | 0.0022941 | 0.00057497
14 | 0.99419 | -0.040725 | 0.0043199 | 0.0010827
15 | 0.99665 | -0.023427 | 0.0051595 | 0.0012931
16 | 0.99387 | -0.042967 | 0.0022859 | 0.00057291
17 | 0.99433 | -0.039723 | 0.001636 | 0.00041002
18 | 0.99409 | -0.041434 | 0.0015276 | 0.00038284
19 | 0.99682 | -0.022211 | 0.0009101 | 0.00022809
20 | 0.99855 | -0.010124 | 0.0091447 | 0.0022919
21 | 0.99848 | -0.010607 | 0.0061046 | 0.0015299
22 | 1 | 0 | -0.14148 | -0.035344
23 | 0.99793 | -0.014512 | 0.002242 | 0.00056189
24 | 0.99803 | -0.013717 | 0 | 0
25 | 0.99786 | -0.014978 | 0.0092428 | 0.0023165
26 | 0.99711 | -0.020211 | 0 | 0
27 | 0.994 | -0.042086 | 0.0022045 | 0.0005525
28 | 0.99701 | -0.020881 | 0.0081525 | 0.0020432
29 | 0.99706 | -0.020565 | 0 | 0
30 | 0.99785 | -0.015026 | 0.0024568 | 0.00061574
31 | 0.99387 | -0.042992 | 0.0014503 | 0.00036348
32 | 0.99669 | -0.023115 | 0 | 0
33 | 0.99666 | -0.023365 | 0.0013116 | 0.00032872
34 | 0.9967 | -0.023097 | 0 | 0
35 | 0.99639 | -0.02523 | 0.010104 | 0.0025323
36 | 0.99701 | -0.02092 | 0.0015881 | 0.00039802
37 | 0.99118 | -0.061848 | 0.012633 | 0.003166
38 | 0.99049 | -0.066691 | 0.012633 | 0.003166
39 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0059773 | -0.0014979 | 0.0059787 | 0.0014981 | 1.4656e-06 | 1.8539e-07 | 0.00896 | 0.0089598 | 0.00896 | 0.99266 | -0.051417 | 0.99291 | -0.049645 | 3.3185
1 | 0.0026672 | 0.00066829 | -0.0026671 | -0.00066843 | 1.5166e-07 | -1.382e-07 | 0.0039982 | 0.0039982 | 0.0039982 | 0.99266 | -0.051417 | 0.9926 | -0.051828 | 1.4808
2 | -0.013483 | -0.0033788 | 0.013488 | 0.0033804 | 4.6389e-06 | 1.5486e-06 | 0.020206 | 0.020206 | 0.020206 | 0.99291 | -0.049645 | 0.99326 | -0.04716 | 7.4838
3 | -0.01733 | -0.0043421 | 0.017338 | 0.0043447 | 7.3305e-06 | 2.5937e-06 | 0.025962 | 0.025962 | 0.025962 | 0.99326 | -0.04716 | 0.9937 | -0.044104 | 9.6156
4 | 0.0038424 | 0.00096175 | -0.0038414 | -0.00096199 | 9.9421e-07 | -2.3988e-07 | 0.0057559 | 0.0057561 | 0.0057561 | 0.99326 | -0.04716 | 0.993 | -0.049033 | 2.1319
5 | -0.053218 | -0.013347 | 0.053233 | 0.013353 | 1.4586e-05 | 5.5623e-06 | 0.079695 | 0.079695 | 0.079695 | 0.9937 | -0.044104 | 0.99398 | -0.042128 | 29.5167
6 | 0.035881 | 0.0090023 | -0.035842 | -0.0089876 | 3.9004e-05 | 1.4722e-05 | 0.053733 | 0.053733 | 0.053733 | 0.9937 | -0.044104 | 0.99258 | -0.051948 | 19.9011
7 | 0.0038414 | 0.00096199 | -0.0038399 | -0.00096236 | 1.5396e-06 | -3.7073e-07 | 0.0057561 | 0.0057564 | 0.0057564 | 0.993 | -0.049033 | 0.99259 | -0.051931 | 2.132
8 | -0.06024 | -0.015109 | 0.060479 | 0.0152 | 0.00023824 | 9.102e-05 | 0.090186 | 0.090186 | 0.090186 | 0.99398 | -0.042128 | 0.99803 | -0.013717 | 33.4021
9 | 0.025308 | 0.0063476 | -0.025274 | -0.0063348 | 3.4691e-05 | 1.2844e-05 | 0.037942 | 0.037942 | 0.037942 | 0.99258 | -0.051948 | 0.99118 | -0.061848 | 14.0527
10 | 0.0090356 | 0.0022641 | -0.009035 | -0.0022639 | 5.8617e-07 | 1.5883e-07 | 0.013523 | 0.013523 | 0.013523 | 0.99425 | -0.040286 | 0.99418 | -0.040755 | 5.0084
11 | -0.011414 | -0.0028601 | 0.011417 | 0.0028611 | 3.1852e-06 | 9.9814e-07 | 0.017082 | 0.017082 | 0.017082 | 0.99425 | -0.040286 | 0.99454 | -0.03827 | 6.3266
12 | 0.0055105 | 0.0013806 | -0.0055096 | -0.0013805 | 9.5369e-07 | 7.5511e-08 | 0.0082476 | 0.0082477 | 0.0082477 | 0.99418 | -0.040755 | 0.99401 | -0.042006 | 3.0547
13 | 0.0039308 | 0.00098453 | -0.0039303 | -0.00098464 | 5.1804e-07 | -1.1219e-07 | 0.005881 | 0.0058811 | 0.0058811 | 0.99454 | -0.03827 | 0.9944 | -0.039223 | 2.1782
14 | 0.0080553 | 0.0020183 | -0.0080526 | -0.0020176 | 2.7364e-06 | 6.6084e-07 | 0.012052 | 0.012052 | 0.012052 | 0.99454 | -0.03827 | 0.99419 | -0.040725 | 4.4638
15 | -0.023403 | -0.0058639 | 0.023451 | 0.0058816 | 4.8162e-05 | 1.7705e-05 | 0.035015 | 0.035014 | 0.035015 | 0.99454 | -0.03827 | 0.99665 | -0.023427 | 12.9684
16 | 0.0037367 | 0.00093623 | -0.0037362 | -0.00093637 | 4.9723e-07 | -1.3881e-07 | 0.0055938 | 0.0055939 | 0.0055939 | 0.99401 | -0.042006 | 0.99387 | -0.042967 | 2.0718
17 | 0.0016361 | 0.00040967 | -0.001636 | -0.00041002 | 1.1312e-07 | -3.4885e-07 | 0.0024481 | 0.0024483 | 0.0024483 | 0.9944 | -0.039223 | 0.99433 | -0.039723 | 0.90677
18 | 0.0037326 | 0.00093494 | -0.0037323 | -0.00093504 | 3.6596e-07 | -1.029e-07 | 0.0055865 | 0.0055866 | 0.0055866 | 0.99419 | -0.040725 | 0.99409 | -0.041434 | 2.0691
19 | -0.028611 | -0.0071747 | 0.028615 | 0.0071765 | 4.8231e-06 | 1.7998e-06 | 0.042718 | 0.042718 | 0.042718 | 0.99665 | -0.023427 | 0.99682 | -0.022211 | 15.8214
20 | 0.0014503 | 0.00036346 | -0.0014503 | -0.00036348 | 4.949e-09 | -1.9895e-08 | 0.0021714 | 0.0021714 | 0.0021714 | 0.99387 | -0.042967 | 0.99387 | -0.042992 | 0.80422
21 | 0.0022047 | 0.0005522 | -0.0022045 | -0.0005525 | 1.9886e-07 | -3.0286e-07 | 0.0033 | 0.0033002 | 0.0033002 | 0.99409 | -0.041434 | 0.994 | -0.042086 | 1.2223
22 | -0.029526 | -0.0074046 | 0.02956 | 0.0074176 | 3.4803e-05 | 1.3011e-05 | 0.044076 | 0.044076 | 0.044076 | 0.99682 | -0.022211 | 0.99803 | -0.013717 | 16.3245
23 | 0.020056 | 0.0050273 | -0.020054 | -0.0050268 | 1.344e-06 | 4.8538e-07 | 0.029887 | 0.029887 | 0.029887 | 0.99855 | -0.010124 | 0.99848 | -0.010607 | 11.0692
24 | -0.0292 | -0.0073191 | 0.029241 | 0.0073344 | 4.099e-05 | 1.5311e-05 | 0.043514 | 0.043514 | 0.043514 | 0.99855 | -0.010124 | 1 | 0 | 16.1163
25 | 0.01395 | 0.0034968 | -0.013942 | -0.0034943 | 7.539e-06 | 2.5342e-06 | 0.020789 | 0.020789 | 0.020789 | 0.99848 | -0.010607 | 0.99793 | -0.014512 | 7.6998
26 | 0.11144 | 0.02801 | -0.11122 | -0.027929 | 0.00021243 | 8.1057e-05 | 0.16585 | 0.16585 | 0.16585 | 1 | 0 | 0.99803 | -0.013717 | 30.7123
27 | 0.0117 | 0.0029324 | -0.0117 | -0.0029322 | 7.5604e-07 | 2.3878e-07 | 0.017446 | 0.017447 | 0.017447 | 0.99793 | -0.014512 | 0.99786 | -0.014978 | 6.4617
28 | 0.021184 | 0.0053112 | -0.021165 | -0.0053043 | 1.9042e-05 | 6.9246e-06 | 0.031585 | 0.031585 | 0.031585 | 0.99803 | -0.013717 | 0.99711 | -0.020211 | 11.6981
29 | 0.0024569 | 0.00061573 | -0.0024568 | -0.00061574 | 1.6274e-08 | -1.9122e-08 | 0.0036637 | 0.0036637 | 0.0036637 | 0.99786 | -0.014978 | 0.99785 | -0.015026 | 1.3569
30 | 0.0081532 | 0.0020434 | -0.0081525 | -0.0020432 | 7.5613e-07 | 1.8407e-07 | 0.012167 | 0.012167 | 0.012167 | 0.99711 | -0.020211 | 0.99701 | -0.020881 | 4.5064
31 | 0.013012 | 0.0032609 | -0.013011 | -0.0032607 | 6.3782e-07 | 2.0996e-07 | 0.019417 | 0.019417 | 0.019417 | 0.99711 | -0.020211 | 0.99706 | -0.020565 | 7.1917
32 | 0.0015882 | 0.00039776 | -0.0015881 | -0.00039802 | 7.7972e-08 | -2.6009e-07 | 0.0023701 | 0.0023702 | 0.0023702 | 0.99706 | -0.020565 | 0.99701 | -0.02092 | 0.87786
33 | 0.011423 | 0.0028629 | -0.011419 | -0.0028617 | 4.0039e-06 | 1.2521e-06 | 0.017047 | 0.017047 | 0.017047 | 0.99706 | -0.020565 | 0.9967 | -0.023097 | 6.3139
34 | 0.0013116 | 0.00032849 | -0.0013116 | -0.00032872 | 4.5332e-08 | -2.2947e-07 | 0.0019581 | 0.0019582 | 0.0019582 | 0.99669 | -0.023115 | 0.99666 | -0.023365 | 0.72526
35 | -0.0013116 | -0.00032849 | 0.0013116 | 0.00032847 | 3.2108e-09 | -1.6255e-08 | 0.0019581 | 0.0019581 | 0.0019581 | 0.99669 | -0.023115 | 0.9967 | -0.023097 | 0.72523
36 | 0.010107 | 0.0025332 | -0.010104 | -0.0025323 | 2.984e-06 | 8.7405e-07 | 0.015089 | 0.015089 | 0.015089 | 0.9967 | -0.023097 | 0.99639 | -0.02523 | 5.5887
37 | 0.012641 | 0.0031688 | -0.012633 | -0.003166 | 8.4738e-06 | 2.7735e-06 | 0.018978 | 0.018978 | 0.018978 | 0.99118 | -0.061848 | 0.99049 | -0.066691 | 7.0288

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15123 | 0.037788

## res_load
| p_mw | q_mvar
0 | 0.00331 | 0.00082958
1 | 0.0075044 | 0.0018808
2 | 0.0026671 | 0.00066843
3 | 0.0070077 | 0.0017563
4 | 0.010533 | 0.0026399
5 | 0.0038399 | 0.00096236
6 | 0.0023781 | 0.00059601
7 | 0.0035245 | 0.00088331
8 | 0.0017728 | 0.00044432
9 | 0.0022941 | 0.00057497
10 | 0.0043199 | 0.0010827
11 | 0.0051595 | 0.0012931
12 | 0.0022859 | 0.00057291
13 | 0.001636 | 0.00041002
14 | 0.0015276 | 0.00038284
15 | 0.0009101 | 0.00022809
16 | 0.0091447 | 0.0022919
17 | 0.0061046 | 0.0015299
18 | 0.0097501 | 0.0024436
19 | 0.002242 | 0.00056189
20 | 0.0092428 | 0.0023165
21 | 0.0022045 | 0.0005525
22 | 0.0081525 | 0.0020432
23 | 0.0024568 | 0.00061574
24 | 0.0014503 | 0.00036348
25 | 0.0013116 | 0.00032872
26 | 0.010104 | 0.0025323
27 | 0.0015881 | 0.00039802
28 | 0.012633 | 0.003166
29 | 0.012633 | 0.003166

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1