## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2051-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2051-7_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2051-7_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2051-7_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2051-7_0_4_node_87 | 0.4 | n |  | TRUE
5 | bus_LV_2051-7_0_4_node_86 | 0.4 | n |  | TRUE
6 | bus_LV_2051-7_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2051-7_0_4_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_2051-7_0_4_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_2051-7_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2051-7_0_4_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_2051-7_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_2051-7_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_2051-7_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2051-7_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2051-7_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2051-7_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2051-7_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2051-7_0_4_node_118 | 0.4 | n |  | TRUE
19 | bus_LV_2051-7_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2051-7_0_4_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_2051-7_0_4_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_2051-7_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_2051-7_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_2051-7_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2051-7_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_2051-7_0_4_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_2051-7_0_4_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_2051-7_0_4_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_2051-7_0_4_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_2051-7_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_2051-7_0_4_node_123 | 0.4 | n |  | TRUE
32 | bus_LV_2051-7_0_4_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_2051-7_0_4_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_2051-7_0_4_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_2051-7_0_4_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_2051-7_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_2051-7_0_4_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_2051-7_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2051-7_0_4_node_119 | 0.4 | n |  | TRUE
40 | bus_LV_2051-7_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_2051-7_0_4_node_124 | 0.4 | n |  | TRUE
42 | bus_LV_2051-7_0_4_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_2051-7_0_4_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_2051-7_0_4_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_2051-7_0_4_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_2051-7_0_4_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_2051-7_0_4_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_2051-7_0_4_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_2051-7_0_4_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_2051-7_0_4_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_2051-7_0_4_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_2051-7_0_4_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_2051-7_0_4_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_2051-7_0_4_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_2051-7_0_4_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_2051-7_0_4_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_2051-7_0_4_node_55 | 0.4 | n |  | TRUE
58 | bus_LV_2051-7_0_4_node_52 | 0.4 | n |  | TRUE
59 | bus_LV_2051-7_0_4_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_2051-7_0_4_node_53 | 0.4 | n |  | TRUE
61 | bus_LV_2051-7_0_4_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_2051-7_0_4_node_60 | 0.4 | n |  | TRUE
63 | bus_LV_2051-7_0_4_node_106 | 0.4 | n |  | TRUE
64 | bus_LV_2051-7_0_4_node_112 | 0.4 | n |  | TRUE
65 | bus_LV_2051-7_0_4_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_2051-7_0_4_node_105 | 0.4 | n |  | TRUE
67 | bus_LV_2051-7_0_4_node_121 | 0.4 | n |  | TRUE
68 | bus_LV_2051-7_0_4_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_2051-7_0_4_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_2051-7_0_4_node_61 | 0.4 | n |  | TRUE
71 | bus_LV_2051-7_0_4_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_2051-7_0_4_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_2051-7_0_4_node_66 | 0.4 | n |  | TRUE
74 | bus_LV_2051-7_0_4_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_2051-7_0_4_node_69 | 0.4 | n |  | TRUE
76 | bus_LV_2051-7_0_4_node_68 | 0.4 | n |  | TRUE
77 | bus_LV_2051-7_0_4_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_2051-7_0_4_node_72 | 0.4 | n |  | TRUE
79 | bus_LV_2051-7_0_4_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_2051-7_0_4_node_65 | 0.4 | n |  | TRUE
81 | bus_LV_2051-7_0_4_node_67 | 0.4 | n |  | TRUE
82 | bus_LV_2051-7_0_4_node_113 | 0.4 | n |  | TRUE
83 | bus_LV_2051-7_0_4_node_92 | 0.4 | n |  | TRUE
84 | bus_LV_2051-7_0_4_node_115 | 0.4 | n |  | TRUE
85 | bus_LV_2051-7_0_4_node_114 | 0.4 | n |  | TRUE
86 | bus_LV_2051-7_0_4_node_91 | 0.4 | n |  | TRUE
87 | bus_LV_2051-7_0_4_node_116 | 0.4 | n |  | TRUE
88 | bus_LV_2051-7_0_4_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_2051-7_0_4_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_2051-7_0_4_node_79 | 0.4 | n |  | TRUE
91 | bus_LV_2051-7_0_4_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_2051-7_0_4_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_2051-7_0_4_node_80 | 0.4 | n |  | TRUE
94 | bus_LV_2051-7_0_4_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_2051-7_0_4_node_82 | 0.4 | n |  | TRUE
96 | bus_LV_2051-7_0_4_node_81 | 0.4 | n |  | TRUE
97 | bus_LV_2051-7_0_4_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_2051-7_0_4_node_83 | 0.4 | n |  | TRUE
99 | bus_LV_2051-7_0_4_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_2051-7_0_4_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_2051-7_0_4_node_88 | 0.4 | n |  | TRUE
102 | bus_LV_2051-7_0_4_node_89 | 0.4 | n |  | TRUE
103 | bus_LV_2051-7_0_4_node_90 | 0.4 | n |  | TRUE
104 | bus_LV_2051-7_0_4_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_2051-7_0_4_node_94 | 0.4 | n |  | TRUE
106 | bus_LV_2051-7_0_4_node_95 | 0.4 | n |  | TRUE
107 | bus_LV_2051-7_0_4_node_97 | 0.4 | n |  | TRUE
108 | bus_LV_2051-7_0_4_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_2051-7_0_4_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_2051-7_0_4_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_2051-7_0_4_node_102 | 0.4 | n |  | TRUE
112 | bus_LV_2051-7_0_4_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_2051-7_0_4_node_109 | 0.4 | n |  | TRUE
114 | bus_LV_2051-7_0_4_node_110 | 0.4 | n |  | TRUE
115 | bus_LV_2051-7_0_4_node_111 | 0.4 | n |  | TRUE
116 | bus_LV_2051-7_0_4_node_103 | 0.4 | n |  | TRUE
117 | bus_LV_2051-7_0_4_node_104 | 0.4 | n |  | TRUE
118 | bus_LV_2051-7_0_4_node_107 | 0.4 | n |  | TRUE
119 | bus_LV_2051-7_0_4_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_2051-7_0_4_node_122 | 0.4 | n |  | TRUE
121 | bus_LV_2051-7_0_4_node_117 | 0.4 | n |  | TRUE
122 | bus_MV_377_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2051-7_0_4_load_0 | 0 | 0.0014119 | 0.00035387 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2051-7_0_4_load_3 | 2 | 0.0012206 | 0.0003059 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2051-7_0_4_load_86 | 5 | 0.0053994 | 0.0013532 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2051-7_0_4_load_5 | 6 | 0.0013958 | 0.00034981 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2051-7_0_4_load_23 | 8 | 0.0044127 | 0.0011059 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2051-7_0_4_load_6 | 9 | 0.0024583 | 0.00061611 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2051-7_0_4_load_15 | 10 | 0.0012152 | 0.00030457 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2051-7_0_4_load_12 | 11 | 0.0011681 | 0.00029275 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2051-7_0_4_load_7 | 13 | 0.0010258 | 0.0002571 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2051-7_0_4_load_8 | 14 | 0.0010201 | 0.00025566 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2051-7_0_4_load_9 | 15 | 0.0011658 | 0.00029219 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2051-7_0_4_load_10 | 16 | 0.0010239 | 0.00025661 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2051-7_0_4_load_11 | 17 | 0.0011594 | 0.00029058 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2051-7_0_4_load_118 | 18 | 0.0010043 | 0.00025171 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2051-7_0_4_load_13 | 19 | 0.0011627 | 0.00029141 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2051-7_0_4_load_22 | 20 | 0.0011819 | 0.0002962 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2051-7_0_4_load_21 | 21 | 0.0012168 | 0.00030496 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2051-7_0_4_load_16 | 22 | 0.001006 | 0.00025212 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2051-7_0_4_load_17 | 23 | 0.001184 | 0.00029675 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2051-7_0_4_load_18 | 24 | 0.0011286 | 0.00028286 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2051-7_0_4_load_19 | 25 | 0.0011702 | 0.00029327 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2051-7_0_4_load_20 | 26 | 0.0011485 | 0.00028784 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2051-7_0_4_load_26 | 28 | 0.0017192 | 0.00043087 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2051-7_0_4_load_27 | 30 | 0.0027594 | 0.00069157 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2051-7_0_4_load_123 | 31 | 0.0010037 | 0.00025156 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2051-7_0_4_load_42 | 34 | 0.0013874 | 0.00034772 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2051-7_0_4_load_29 | 35 | 0.000753 | 0.00018872 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2051-7_0_4_load_31 | 37 | 0.0035318 | 0.00088516 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2051-7_0_4_load_119 | 39 | 0.003024 | 0.00075788 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2051-7_0_4_load_41 | 40 | 0.00089828 | 0.00022513 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2051-7_0_4_load_124 | 41 | 0.0023138 | 0.00057988 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2051-7_0_4_load_40 | 42 | 0.00083802 | 0.00021003 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2051-7_0_4_load_34 | 43 | 0.0005584 | 0.00013995 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2051-7_0_4_load_35 | 44 | 0.0005939 | 0.00014884 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2051-7_0_4_load_36 | 45 | 0.00079562 | 0.0001994 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2051-7_0_4_load_37 | 46 | 0.00076803 | 0.00019249 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2051-7_0_4_load_38 | 47 | 0.0011539 | 0.00028919 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2051-7_0_4_load_39 | 48 | 0.00085291 | 0.00021376 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2051-7_0_4_load_43 | 49 | 0.001088 | 0.00027267 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2051-7_0_4_load_45 | 50 | 0.0016137 | 0.00040442 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2051-7_0_4_load_46 | 51 | 0.0048305 | 0.0012106 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2051-7_0_4_load_47 | 52 | 0.0014478 | 0.00036284 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2051-7_0_4_load_48 | 53 | 0.0021467 | 0.00053802 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2051-7_0_4_load_50 | 55 | 0.00057132 | 0.00014319 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2051-7_0_4_load_51 | 56 | 0.0014618 | 0.00036637 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2051-7_0_4_load_55 | 57 | 0.0030167 | 0.00075607 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2051-7_0_4_load_56 | 59 | 0.0029843 | 0.00074794 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2051-7_0_4_load_54 | 61 | 0.0013608 | 0.00034105 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2051-7_0_4_load_60 | 62 | 0.0019778 | 0.00049568 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2051-7_0_4_load_106 | 63 | 0.0013865 | 0.00034748 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2051-7_0_4_load_112 | 64 | 0.00049311 | 0.00012359 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2051-7_0_4_load_59 | 65 | 0.0054674 | 0.0013703 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2051-7_0_4_load_105 | 66 | 0.0030585 | 0.00076653 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2051-7_0_4_load_121 | 67 | 0.0013157 | 0.00032975 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2051-7_0_4_load_57 | 68 | 0.00063291 | 0.00015862 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2051-7_0_4_load_58 | 69 | 0.00072874 | 0.00018264 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2051-7_0_4_load_62 | 71 | 0.002596 | 0.00065061 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2051-7_0_4_load_71 | 74 | 0.0018977 | 0.00047561 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2051-7_0_4_load_69 | 75 | 0.0016983 | 0.00042565 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2051-7_0_4_load_68 | 76 | 0.0023264 | 0.00058304 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2051-7_0_4_load_64 | 77 | 0.001651 | 0.00041377 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2051-7_0_4_load_70 | 79 | 0.0015212 | 0.00038124 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2051-7_0_4_load_65 | 80 | 0.0019939 | 0.00049972 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2051-7_0_4_load_113 | 82 | 0.0040722 | 0.0010206 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2051-7_0_4_load_92 | 83 | 0.0021912 | 0.00054918 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2051-7_0_4_load_115 | 84 | 0.0024699 | 0.000619 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2051-7_0_4_load_114 | 85 | 0.0059739 | 0.0014972 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2051-7_0_4_load_91 | 86 | 0.0028385 | 0.0007114 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2051-7_0_4_load_116 | 87 | 0.0024034 | 0.00060234 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2051-7_0_4_load_74 | 89 | 0.0016388 | 0.00041073 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2051-7_0_4_load_78 | 91 | 0.0025656 | 0.00064299 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2051-7_0_4_load_75 | 92 | 0.0011303 | 0.00028328 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2051-7_0_4_load_80 | 93 | 0.0018818 | 0.00047163 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2051-7_0_4_load_76 | 94 | 0.0028272 | 0.00070856 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2051-7_0_4_load_82 | 95 | 0.0046957 | 0.0011768 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2051-7_0_4_load_81 | 96 | 0.0057286 | 0.0014357 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2051-7_0_4_load_77 | 97 | 0.00099695 | 0.00024986 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2051-7_0_4_load_83 | 98 | 0.0047461 | 0.0011895 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2051-7_0_4_load_84 | 99 | 0.0041586 | 0.0010422 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2051-7_0_4_load_88 | 101 | 0.0036968 | 0.00092651 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2051-7_0_4_load_89 | 102 | 0.001478 | 0.00037043 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2051-7_0_4_load_90 | 103 | 0.0039957 | 0.0010014 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2051-7_0_4_load_93 | 104 | 0.0025556 | 0.00064049 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2051-7_0_4_load_94 | 105 | 0.0020937 | 0.00052474 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2051-7_0_4_load_98 | 108 | 0.0014364 | 0.00035999 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2051-7_0_4_load_101 | 109 | 0.0031158 | 0.0007809 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2051-7_0_4_load_99 | 110 | 0.00050335 | 0.00012615 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2051-7_0_4_load_100 | 112 | 0.0029698 | 0.0007443 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2051-7_0_4_load_109 | 113 | 0.0020722 | 0.00051933 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2051-7_0_4_load_103 | 116 | 0.0017269 | 0.00043281 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2051-7_0_4_load_104 | 117 | 0.0018669 | 0.00046789 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2051-7_0_4_load_107 | 118 | 0.0013221 | 0.00033135 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2051-7_0_4_load_108 | 119 | 0.0029268 | 0.00073352 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2051-7_0_4_load_122 | 120 | 0.0025022 | 0.00062712 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2051-7_0_4_load_117 | 121 | 0.0026356 | 0.00066055 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 101 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2051-7_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2051-7_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.018634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2051-7_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.047439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_2051-7_0_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.06398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_2051-7_0_4_line_4 | NAYY 4x150 SE | 2 | 6 | 0.0098796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2051-7_0_4_line_5 | NAYY 4x150 SE | 3 | 7 | 0.012018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2051-7_0_4_line_6 | NAYY 4x150 SE | 3 | 8 | 0.0058275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_2051-7_0_4_line_7 | NAYY 4x150 SE | 4 | 5 | 0.053778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_2051-7_0_4_line_8 | NAYY 4x150 SE | 5 | 100 | 0.040539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_2051-7_0_4_line_9 | NAYY 4x150 SE | 6 | 9 | 0.040991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2051-7_0_4_line_10 | NAYY 4x150 SE | 7 | 10 | 0.032756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2051-7_0_4_line_11 | NAYY 4x150 SE | 7 | 11 | 0.029744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2051-7_0_4_line_12 | NAYY 4x150 SE | 8 | 12 | 0.023931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_2051-7_0_4_line_13 | NAYY 4x150 SE | 10 | 20 | 0.0039192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2051-7_0_4_line_14 | NAYY 4x150 SE | 11 | 19 | 0.0058059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2051-7_0_4_line_15 | NAYY 4x150 SE | 12 | 27 | 0.022697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_2051-7_0_4_line_16 | NAYY 4x150 SE | 12 | 28 | 0.015514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2051-7_0_4_line_17 | NAYY 4x150 SE | 13 | 14 | 0.0058577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2051-7_0_4_line_18 | NAYY 4x150 SE | 13 | 15 | 0.017001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2051-7_0_4_line_19 | NAYY 4x150 SE | 14 | 16 | 0.0058526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2051-7_0_4_line_20 | NAYY 4x150 SE | 15 | 17 | 0.0057893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2051-7_0_4_line_21 | NAYY 4x150 SE | 16 | 18 | 0.0038595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2051-7_0_4_line_22 | NAYY 4x150 SE | 17 | 19 | 0.0057822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2051-7_0_4_line_23 | NAYY 4x150 SE | 20 | 21 | 0.0061994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2051-7_0_4_line_24 | NAYY 4x150 SE | 21 | 26 | 0.0061132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2051-7_0_4_line_25 | NAYY 4x150 SE | 22 | 23 | 0.016923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2051-7_0_4_line_26 | NAYY 4x150 SE | 22 | 24 | 0.01009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2051-7_0_4_line_27 | NAYY 4x150 SE | 23 | 25 | 0.0065217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2051-7_0_4_line_28 | NAYY 4x150 SE | 25 | 26 | 0.016528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2051-7_0_4_line_29 | NAYY 4x150 SE | 27 | 29 | 0.021795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_2051-7_0_4_line_30 | NAYY 4x150 SE | 27 | 30 | 0.014302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2051-7_0_4_line_31 | NAYY 4x150 SE | 29 | 31 | 0.018371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2051-7_0_4_line_32 | NAYY 4x150 SE | 29 | 32 | 0.003634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_2051-7_0_4_line_33 | NAYY 4x150 SE | 32 | 33 | 0.014793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_2051-7_0_4_line_34 | NAYY 4x150 SE | 32 | 34 | 0.014757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2051-7_0_4_line_35 | NAYY 4x150 SE | 33 | 41 | 0.008876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2051-7_0_4_line_36 | NAYY 4x150 SE | 33 | 36 | 0.016201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2051-7_0_4_line_37 | NAYY 4x150 SE | 34 | 49 | 0.0080288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2051-7_0_4_line_38 | NAYY 4x150 SE | 35 | 36 | 0.016426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2051-7_0_4_line_39 | NAYY 4x150 SE | 35 | 37 | 0.024578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2051-7_0_4_line_40 | NAYY 4x150 SE | 36 | 38 | 0.002067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2051-7_0_4_line_41 | NAYY 4x150 SE | 38 | 39 | 0.008726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2051-7_0_4_line_42 | NAYY 4x150 SE | 38 | 40 | 0.034389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2051-7_0_4_line_43 | NAYY 4x150 SE | 40 | 42 | 0.00033458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2051-7_0_4_line_44 | NAYY 4x150 SE | 42 | 48 | 0.0050037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2051-7_0_4_line_45 | NAYY 4x150 SE | 43 | 44 | 0.00093839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2051-7_0_4_line_46 | NAYY 4x150 SE | 44 | 45 | 0.002345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2051-7_0_4_line_47 | NAYY 4x150 SE | 45 | 46 | 0.000454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2051-7_0_4_line_48 | NAYY 4x150 SE | 46 | 47 | 0.0011417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2051-7_0_4_line_49 | NAYY 4x150 SE | 47 | 48 | 0.013714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2051-7_0_4_line_50 | NAYY 4x150 SE | 49 | 50 | 0.016149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2051-7_0_4_line_51 | NAYY 4x150 SE | 50 | 51 | 0.0061389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2051-7_0_4_line_52 | NAYY 4x150 SE | 52 | 53 | 0.023822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2051-7_0_4_line_53 | NAYY 4x150 SE | 52 | 54 | 0.051729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2051-7_0_4_line_54 | NAYY 4x150 SE | 53 | 55 | 0.022652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2051-7_0_4_line_55 | NAYY 4x150 SE | 54 | 56 | 0.033156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2051-7_0_4_line_56 | NAYY 4x150 SE | 55 | 57 | 0.001853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2051-7_0_4_line_57 | NAYY 4x150 SE | 56 | 58 | 0.032196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2051-7_0_4_line_58 | NAYY 4x150 SE | 57 | 59 | 0.02515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2051-7_0_4_line_59 | NAYY 4x150 SE | 58 | 60 | 0.00192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2051-7_0_4_line_60 | NAYY 4x150 SE | 58 | 61 | 0.035154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2051-7_0_4_line_61 | NAYY 4x150 SE | 59 | 68 | 0.0252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2051-7_0_4_line_62 | NAYY 4x150 SE | 60 | 62 | 0.048545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2051-7_0_4_line_63 | NAYY 4x150 SE | 60 | 63 | 0.013275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2051-7_0_4_line_64 | NAYY 4x150 SE | 61 | 64 | 0.0042434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2051-7_0_4_line_65 | NAYY 4x150 SE | 62 | 65 | 0.039211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2051-7_0_4_line_66 | NAYY 4x150 SE | 63 | 66 | 0.009134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2051-7_0_4_line_67 | NAYY 4x150 SE | 64 | 67 | 0.040136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2051-7_0_4_line_68 | NAYY 4x150 SE | 65 | 70 | 0.0061328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2051-7_0_4_line_69 | NAYY 4x150 SE | 66 | 116 | 0.015245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2051-7_0_4_line_70 | NAYY 4x150 SE | 67 | 120 | 0.040264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2051-7_0_4_line_71 | NAYY 4x150 SE | 68 | 69 | 0.035085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2051-7_0_4_line_72 | NAYY 4x150 SE | 70 | 71 | 0.0084233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_2051-7_0_4_line_73 | NAYY 4x150 SE | 70 | 72 | 0.008689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_2051-7_0_4_line_74 | NAYY 4x150 SE | 71 | 73 | 0.017582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_2051-7_0_4_line_75 | NAYY 4x150 SE | 72 | 74 | 0.042833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_2051-7_0_4_line_76 | NAYY 4x150 SE | 72 | 75 | 0.016756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2051-7_0_4_line_77 | NAYY 4x150 SE | 73 | 76 | 0.011847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2051-7_0_4_line_78 | NAYY 4x150 SE | 73 | 77 | 0.0002739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_2051-7_0_4_line_79 | NAYY 4x150 SE | 74 | 78 | 0.0072534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
80 | LV_2051-7_0_4_line_80 | NAYY 4x150 SE | 75 | 79 | 0.012088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2051-7_0_4_line_81 | NAYY 4x150 SE | 76 | 84 | 0.012692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2051-7_0_4_line_82 | NAYY 4x150 SE | 77 | 80 | 0.041144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_2051-7_0_4_line_83 | NAYY 4x150 SE | 78 | 88 | 0.024589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2051-7_0_4_line_84 | NAYY 4x150 SE | 78 | 89 | 0.0088758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_2051-7_0_4_line_85 | NAYY 4x150 SE | 80 | 81 | 0.012277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_2051-7_0_4_line_86 | NAYY 4x150 SE | 81 | 82 | 0.023578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2051-7_0_4_line_87 | NAYY 4x150 SE | 81 | 83 | 0.016754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_2051-7_0_4_line_88 | NAYY 4x150 SE | 82 | 85 | 0.012442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2051-7_0_4_line_89 | NAYY 4x150 SE | 83 | 86 | 0.029285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_2051-7_0_4_line_90 | NAYY 4x150 SE | 84 | 87 | 0.01283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2051-7_0_4_line_91 | NAYY 4x150 SE | 86 | 102 | 0.017226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_2051-7_0_4_line_92 | NAYY 4x150 SE | 87 | 121 | 0.013003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2051-7_0_4_line_93 | NAYY 4x150 SE | 88 | 90 | 0.005459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2051-7_0_4_line_94 | NAYY 4x150 SE | 88 | 91 | 0.029665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2051-7_0_4_line_95 | NAYY 4x150 SE | 89 | 92 | 0.019687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_2051-7_0_4_line_96 | NAYY 4x150 SE | 90 | 93 | 0.027954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2051-7_0_4_line_97 | NAYY 4x150 SE | 92 | 94 | 0.0094208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_2051-7_0_4_line_98 | NAYY 4x150 SE | 93 | 97 | 0.044083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2051-7_0_4_line_99 | NAYY 4x150 SE | 94 | 95 | 0.029768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_2051-7_0_4_line_100 | NAYY 4x150 SE | 95 | 96 | 0.0043137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_2051-7_0_4_line_101 | NAYY 4x150 SE | 96 | 98 | 0.025599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_2051-7_0_4_line_102 | NAYY 4x150 SE | 98 | 99 | 0.0064519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_2051-7_0_4_line_103 | NAYY 4x150 SE | 99 | 100 | 0.022832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_2051-7_0_4_line_104 | NAYY 4x150 SE | 101 | 102 | 0.003747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_2051-7_0_4_line_105 | NAYY 4x150 SE | 101 | 103 | 0.033224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2051-7_0_4_line_106 | NAYY 4x150 SE | 104 | 105 | 0.0040443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2051-7_0_4_line_107 | NAYY 4x150 SE | 104 | 106 | 0.020655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2051-7_0_4_line_108 | NAYY 4x150 SE | 106 | 107 | 0.004729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2051-7_0_4_line_109 | NAYY 4x150 SE | 106 | 108 | 0.021277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2051-7_0_4_line_110 | NAYY 4x150 SE | 107 | 109 | 0.028379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2051-7_0_4_line_111 | NAYY 4x150 SE | 107 | 110 | 0.017389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2051-7_0_4_line_112 | NAYY 4x150 SE | 109 | 111 | 0.015518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2051-7_0_4_line_113 | NAYY 4x150 SE | 111 | 116 | 0.016387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2051-7_0_4_line_114 | NAYY 4x150 SE | 111 | 117 | 0.014118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2051-7_0_4_line_115 | NAYY 4x150 SE | 112 | 113 | 0.045553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2051-7_0_4_line_116 | NAYY 4x150 SE | 113 | 114 | 0.06505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2051-7_0_4_line_117 | NAYY 4x150 SE | 114 | 115 | 0.065507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2051-7_0_4_line_118 | NAYY 4x150 SE | 115 | 120 | 0.050708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2051-7_0_4_line_119 | NAYY 4x150 SE | 117 | 118 | 0.028856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2051-7_0_4_line_120 | NAYY 4x150 SE | 118 | 119 | 0.017275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2051-7_0_4_trafo_88 | 0.25 MVA 20/0.4 kV | 122 | 101 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2563032.9538 | 1196290.5761 | 2563038.1671 | 1196294.7238 | 2563050.5443 | 1196305.1395
1 | 2563032.9538 | 1196290.5761 | 2563018.4402 | 1196302.2621
2 | 2562997.1854 | 1196259.3029 | 2563032.9538 | 1196290.5761
3 | 2563074.519 | 1196241.9363 | 2563032.9538 | 1196290.5761
4 | 2563010.745 | 1196308.4582 | 2563018.4402 | 1196302.2621
5 | 2562997.1854 | 1196259.3029 | 2562988.1085 | 1196267.208
6 | 2562997.1854 | 1196259.3029 | 2562992.7804 | 1196255.4878
7 | 2563074.519 | 1196241.9363 | 2563082.8932 | 1196246.02 | 2563091.7442 | 1196243.4305 | 2563117.6416 | 1196255.3101 | 2563123.0387 | 1196259.3591
8 | 2563156.1504 | 1196282.6538 | 2563147.0068 | 1196277.3407 | 2563123.0387 | 1196259.3591
9 | 2563010.745 | 1196308.4582 | 2562978.8173 | 1196334.1658
10 | 2562988.1085 | 1196267.208 | 2562963.302 | 1196245.817
11 | 2562988.1085 | 1196267.208 | 2562968.4956 | 1196284.7839 | 2562966.2507 | 1196287.3487
12 | 2562974.6913 | 1196239.8207 | 2562992.7804 | 1196255.4878
13 | 2562963.302 | 1196245.817 | 2562963.302 | 1196245.817 | 2562960.6743 | 1196248.7248
14 | 2562966.2507 | 1196287.3487 | 2562962.4267 | 1196291.7174
15 | 2562957.5047 | 1196224.9415 | 2562974.6913 | 1196239.8207
16 | 2562984.9025 | 1196228.1176 | 2562974.6913 | 1196239.8207
17 | 2562941.1475 | 1196309.7737 | 2562937.2441 | 1196314.1413
18 | 2562941.1475 | 1196309.7737 | 2562943.4511 | 1196307.1962 | 2562951.8625 | 1196303.7866 | 2562954.8053 | 1196300.4246
19 | 2562933.3441 | 1196318.5051 | 2562937.2441 | 1196314.1413
20 | 2562954.8053 | 1196300.4246 | 2562958.6183 | 1196296.0683
21 | 2562930.7722 | 1196321.3828 | 2562933.3441 | 1196318.5051
22 | 2562958.6183 | 1196296.0683 | 2562962.4267 | 1196291.7174
23 | 2562960.6743 | 1196248.7248 | 2562956.5179 | 1196253.3245
24 | 2562952.4193 | 1196257.8601 | 2562956.5179 | 1196253.3245
25 | 2562925.619 | 1196287.5181 | 2562936.9655 | 1196274.9618
26 | 2562925.619 | 1196287.5181 | 2562918.8542 | 1196295.0043
27 | 2562936.9655 | 1196274.9618 | 2562941.338 | 1196270.123
28 | 2562952.4193 | 1196257.8601 | 2562941.338 | 1196270.123
29 | 2562941.0228 | 1196210.6805 | 2562945.6028 | 1196214.6431 | 2562957.5047 | 1196224.9415
30 | 2562957.5047 | 1196224.9415 | 2562967.7697 | 1196214.9823
31 | 2562941.0228 | 1196210.6805 | 2562947.1031 | 1196203.5499 | 2562944.8093 | 1196194.8371
32 | 2562941.0228 | 1196210.6805 | 2562938.2732 | 1196208.2962
33 | 2562927.0757 | 1196198.5938 | 2562938.2732 | 1196208.2962
34 | 2562938.2732 | 1196208.2962 | 2562928.4277 | 1196219.2892
35 | 2562927.0757 | 1196198.5938 | 2562920.953 | 1196205.0354
36 | 2562927.0757 | 1196198.5938 | 2562914.806 | 1196187.9754
37 | 2562923.0725 | 1196225.271 | 2562926.0478 | 1196221.9464 | 2562928.4277 | 1196219.2892
38 | 2562914.806 | 1196187.9754 | 2562903.9211 | 1196200.2769
39 | 2562887.6342 | 1196218.6835 | 2562903.9211 | 1196200.2769
40 | 2562914.806 | 1196187.9754 | 2562913.2436 | 1196186.6177
41 | 2562913.2436 | 1196186.6177 | 2562919.0611 | 1196180.1002
42 | 2562913.2436 | 1196186.6177 | 2562887.2445 | 1196164.1084
43 | 2562886.9916 | 1196163.8894 | 2562887.2445 | 1196164.1084
44 | 2562883.2087 | 1196160.6143 | 2562886.9916 | 1196163.8894
45 | 2562869.1518 | 1196148.4442 | 2562869.8612 | 1196149.0584
46 | 2562869.8612 | 1196149.0584 | 2562871.6341 | 1196150.5933
47 | 2562871.6341 | 1196150.5933 | 2562871.9773 | 1196150.8905
48 | 2562872.8405 | 1196151.6378 | 2562871.9773 | 1196150.8905
49 | 2562872.8405 | 1196151.6378 | 2562883.2087 | 1196160.6143
50 | 2562923.0725 | 1196225.271 | 2562912.3032 | 1196237.3049
51 | 2562908.2093 | 1196241.8794 | 2562912.3032 | 1196237.3049
52 | 2563199.8685 | 1196032.9882 | 2563214.7866 | 1196049.8973 | 2563215.6289 | 1196050.852
53 | 2563166.4836 | 1195993.5533 | 2563170.9048 | 1196000.163 | 2563181.6681 | 1196012.3588 | 2563199.8685 | 1196032.9882
54 | 2563215.6289 | 1196050.852 | 2563225.7416 | 1196062.3143 | 2563230.3784 | 1196068.0387
55 | 2563166.4836 | 1195993.5533 | 2563160.1297 | 1195999.6404 | 2563145.5053 | 1196019.1179
56 | 2563230.3784 | 1196068.0387 | 2563231.5447 | 1196069.4786
57 | 2563126.1742 | 1196044.8639 | 2563145.5053 | 1196019.1179
58 | 2563245.9754 | 1196090.0438 | 2563245.6622 | 1196089.4509 | 2563235.9742 | 1196074.9471 | 2563231.5447 | 1196069.4786
59 | 2563126.1742 | 1196044.8639 | 2563125.0564 | 1196046.4273
60 | 2563126.1742 | 1196044.8639 | 2563104.09 | 1196017.5128
61 | 2563245.9754 | 1196090.0438 | 2563257.7479 | 1196112.3254
62 | 2563125.0564 | 1196046.4273 | 2563142.3964 | 1196065.1637 | 2563149.6207 | 1196072.9678 | 2563158.5234 | 1196081.5724
63 | 2563125.0564 | 1196046.4273 | 2563117.3555 | 1196057.2402
64 | 2563101.4242 | 1196014.2113 | 2563104.09 | 1196017.5128
65 | 2563183.4901 | 1196111.42 | 2563180.1598 | 1196104.8634 | 2563172.1136 | 1196094.7075 | 2563158.5234 | 1196081.5724
66 | 2563112.0568 | 1196064.6801 | 2563117.3555 | 1196057.2402
67 | 2563101.4242 | 1196014.2113 | 2563076.979 | 1195982.3784
68 | 2563186.2674 | 1196116.8878 | 2563183.4901 | 1196111.42
69 | 2563112.0568 | 1196064.6801 | 2563103.2132 | 1196077.0975
70 | 2563076.979 | 1195982.3784 | 2563036.7163 | 1195982.1277
71 | 2563257.7479 | 1196112.3254 | 2563267.19 | 1196130.1962 | 2563272.451 | 1196144.1079
72 | 2563186.2674 | 1196116.8878 | 2563182.1082 | 1196124.2126
73 | 2563190.4054 | 1196124.5332 | 2563186.2674 | 1196116.8878
74 | 2563173.4264 | 1196139.5018 | 2563182.1082 | 1196124.2126
75 | 2563190.4054 | 1196124.5332 | 2563209.7163 | 1196162.7662
76 | 2563190.4054 | 1196124.5332 | 2563205.0918 | 1196116.4668
77 | 2563173.4264 | 1196139.5018 | 2563163.7658 | 1196132.6442
78 | 2563173.2973 | 1196139.7433 | 2563173.4264 | 1196139.5018
79 | 2563212.9864 | 1196169.2406 | 2563209.7163 | 1196162.7662
80 | 2563215.6871 | 1196110.6473 | 2563205.0918 | 1196116.4668
81 | 2563163.7658 | 1196132.6442 | 2563153.4159 | 1196125.2974
82 | 2563173.2973 | 1196139.7433 | 2563153.9088 | 1196176.0332
83 | 2563212.9864 | 1196169.2406 | 2563214.2656 | 1196171.6229 | 2563224.6457 | 1196190.9028
84 | 2563212.9864 | 1196169.2406 | 2563208.9874 | 1196177.1645
85 | 2563148.1233 | 1196186.8619 | 2563153.9088 | 1196176.0332
86 | 2563148.1233 | 1196186.8619 | 2563136.7424 | 1196207.5118
87 | 2563148.1233 | 1196186.8619 | 2563133.6803 | 1196178.3703
88 | 2563130.7367 | 1196218.4089 | 2563136.7424 | 1196207.5118
89 | 2563108.4351 | 1196163.5277 | 2563133.6803 | 1196178.3703
90 | 2563153.4159 | 1196125.2974 | 2563142.9535 | 1196117.8706
91 | 2563098.6952 | 1196177.7364 | 2563108.4351 | 1196163.5277 | 2563108.4351 | 1196163.5277
92 | 2563142.9535 | 1196117.8706 | 2563132.3506 | 1196110.3441
93 | 2563227.2349 | 1196195.7117 | 2563224.6457 | 1196190.9028
94 | 2563224.6457 | 1196190.9028 | 2563250.3827 | 1196176.1506
95 | 2563208.9874 | 1196177.1645 | 2563200.1174 | 1196194.7405
96 | 2563227.2349 | 1196195.7117 | 2563251.6407 | 1196182.0824
97 | 2563195.8729 | 1196203.1509 | 2563200.1174 | 1196194.7405
98 | 2563251.6407 | 1196182.0824 | 2563282.4599 | 1196213.6021
99 | 2563195.8729 | 1196203.1509 | 2563182.4613 | 1196229.7261
100 | 2563180.5178 | 1196233.5772 | 2563182.4613 | 1196229.7261
101 | 2563180.5178 | 1196233.5772 | 2563168.9844 | 1196256.4307
102 | 2563166.0775 | 1196262.1907 | 2563168.9844 | 1196256.4307
103 | 2563156.1504 | 1196282.6538 | 2563157.2049 | 1196280.724 | 2563157.9957 | 1196279.2628 | 2563160.1425 | 1196275.3362 | 2563160.578 | 1196273.0879 | 2563166.0775 | 1196262.1907
104 | 2563096.5766 | 1196180.827 | 2563098.6952 | 1196177.7364
105 | 2563077.7915 | 1196208.2308 | 2563096.5766 | 1196180.827
106 | 2563053.6312 | 1196146.9634 | 2563051.3089 | 1196150.2745
107 | 2563065.4919 | 1196130.0529 | 2563053.6312 | 1196146.9634
108 | 2563065.4919 | 1196130.0529 | 2563068.241 | 1196126.2004
109 | 2563082.8383 | 1196142.4412 | 2563065.4919 | 1196130.0529
110 | 2563068.241 | 1196126.2004 | 2563081.4421 | 1196107.6641 | 2563084.704 | 1196103.0847
111 | 2563068.241 | 1196126.2004 | 2563057.3079 | 1196112.6784
112 | 2563093.7069 | 1196090.4454 | 2563084.704 | 1196103.0847
113 | 2563093.7069 | 1196090.4454 | 2563103.2132 | 1196077.0975
114 | 2563093.7069 | 1196090.4454 | 2563084.8652 | 1196079.4393
115 | 2563015.6246 | 1196061.1241 | 2562988.1322 | 1196024.803
116 | 2562948.3915 | 1195973.3042 | 2562980.378 | 1196014.7506 | 2562988.1322 | 1196024.803
117 | 2562948.3915 | 1195973.3042 | 2562968.8524 | 1195962.0932 | 2562977.0824 | 1195957.5841 | 2563005.9632 | 1195941.7517
118 | 2563036.7163 | 1195982.1277 | 2563005.9632 | 1195941.7517
119 | 2563084.8652 | 1196079.4393 | 2563066.7933 | 1196056.9433
120 | 2563055.9739 | 1196043.4754 | 2563066.7933 | 1196056.9433

## bus_geodata
| x | y | coords
0 | 2563050.5443 | 1196305.1395
1 | 2563032.9538 | 1196290.5761
2 | 2563018.4402 | 1196302.2621
3 | 2562997.1854 | 1196259.3029
4 | 2563074.519 | 1196241.9363
5 | 2563123.0387 | 1196259.3591
6 | 2563010.745 | 1196308.4582
7 | 2562988.1085 | 1196267.208
8 | 2562992.7804 | 1196255.4878
9 | 2562978.8173 | 1196334.1658
10 | 2562963.302 | 1196245.817
11 | 2562966.2507 | 1196287.3487
12 | 2562974.6913 | 1196239.8207
13 | 2562941.1475 | 1196309.7737
14 | 2562937.2441 | 1196314.1413
15 | 2562954.8053 | 1196300.4246
16 | 2562933.3441 | 1196318.5051
17 | 2562958.6183 | 1196296.0683
18 | 2562930.7722 | 1196321.3828
19 | 2562962.4267 | 1196291.7174
20 | 2562960.6743 | 1196248.7248
21 | 2562956.5179 | 1196253.3245
22 | 2562925.619 | 1196287.5181
23 | 2562936.9655 | 1196274.9618
24 | 2562918.8542 | 1196295.0043
25 | 2562941.338 | 1196270.123
26 | 2562952.4193 | 1196257.8601
27 | 2562957.5047 | 1196224.9415
28 | 2562984.9025 | 1196228.1176
29 | 2562941.0228 | 1196210.6805
30 | 2562967.7697 | 1196214.9823
31 | 2562944.8093 | 1196194.8371
32 | 2562938.2732 | 1196208.2962
33 | 2562927.0757 | 1196198.5938
34 | 2562928.4277 | 1196219.2892
35 | 2562903.9211 | 1196200.2769
36 | 2562914.806 | 1196187.9754
37 | 2562887.6342 | 1196218.6835
38 | 2562913.2436 | 1196186.6177
39 | 2562919.0611 | 1196180.1002
40 | 2562887.2445 | 1196164.1084
41 | 2562920.953 | 1196205.0354
42 | 2562886.9916 | 1196163.8894
43 | 2562869.1518 | 1196148.4441
44 | 2562869.8612 | 1196149.0584
45 | 2562871.6341 | 1196150.5933
46 | 2562871.9773 | 1196150.8905
47 | 2562872.8405 | 1196151.6378
48 | 2562883.2087 | 1196160.6143
49 | 2562923.0725 | 1196225.271
50 | 2562912.3032 | 1196237.3049
51 | 2562908.2093 | 1196241.8794
52 | 2563199.8685 | 1196032.9882
53 | 2563215.6289 | 1196050.852
54 | 2563166.4836 | 1195993.5533
55 | 2563230.3784 | 1196068.0387
56 | 2563145.5053 | 1196019.1179
57 | 2563231.5447 | 1196069.4786
58 | 2563126.1742 | 1196044.8639
59 | 2563245.9754 | 1196090.0438
60 | 2563125.0564 | 1196046.4273
61 | 2563104.09 | 1196017.5128
62 | 2563158.5234 | 1196081.5724
63 | 2563117.3555 | 1196057.2402
64 | 2563101.4242 | 1196014.2113
65 | 2563183.4901 | 1196111.42
66 | 2563112.0568 | 1196064.6801
67 | 2563076.979 | 1195982.3784
68 | 2563257.7479 | 1196112.3254
69 | 2563272.451 | 1196144.1079
70 | 2563186.2674 | 1196116.8878
71 | 2563182.1082 | 1196124.2126
72 | 2563190.4054 | 1196124.5332
73 | 2563173.4264 | 1196139.5018
74 | 2563209.7163 | 1196162.7662
75 | 2563205.0918 | 1196116.4668
76 | 2563163.7658 | 1196132.6442
77 | 2563173.2973 | 1196139.7433
78 | 2563212.9864 | 1196169.2406
79 | 2563215.6871 | 1196110.6473
80 | 2563153.9088 | 1196176.0332
81 | 2563148.1233 | 1196186.8619
82 | 2563136.7424 | 1196207.5118
83 | 2563133.6803 | 1196178.3703
84 | 2563153.4159 | 1196125.2974
85 | 2563130.7367 | 1196218.4089
86 | 2563108.4351 | 1196163.5277
87 | 2563142.9535 | 1196117.8706
88 | 2563224.6457 | 1196190.9028
89 | 2563208.9874 | 1196177.1645
90 | 2563227.2349 | 1196195.7117
91 | 2563250.3827 | 1196176.1506
92 | 2563200.1174 | 1196194.7405
93 | 2563251.6407 | 1196182.0824
94 | 2563195.8729 | 1196203.1509
95 | 2563182.4613 | 1196229.7261
96 | 2563180.5178 | 1196233.5772
97 | 2563282.4599 | 1196213.6021
98 | 2563168.9844 | 1196256.4307
99 | 2563166.0775 | 1196262.1907
100 | 2563156.1504 | 1196282.6538
101 | 2563096.5766 | 1196180.827
102 | 2563098.6952 | 1196177.7364
103 | 2563077.7915 | 1196208.2308
104 | 2563053.6312 | 1196146.9634
105 | 2563051.3089 | 1196150.2745
106 | 2563065.4919 | 1196130.0529
107 | 2563068.241 | 1196126.2004
108 | 2563082.8383 | 1196142.4412
109 | 2563084.704 | 1196103.0847
110 | 2563057.3079 | 1196112.6784
111 | 2563093.7069 | 1196090.4454
112 | 2563015.6246 | 1196061.1241
113 | 2562988.1322 | 1196024.803
114 | 2562948.3915 | 1195973.3042
115 | 2563005.9632 | 1195941.7517
116 | 2563103.2132 | 1196077.0975
117 | 2563084.8652 | 1196079.4393
118 | 2563066.7933 | 1196056.9433
119 | 2563055.9739 | 1196043.4754
120 | 2563036.7163 | 1195982.1277
121 | 2563132.3506 | 1196110.3441
122 | 2563077.7915 | 1196208.2308

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97535 | -0.1732 | 0.0014119 | 0.00035387
1 | 0.9754 | -0.17286 | 0 | 0
2 | 0.97526 | -0.17386 | 0.0012206 | 0.0003059
3 | 0.97417 | -0.18166 | 0 | 0
4 | 0.97725 | -0.15959 | 0 | 0
5 | 0.97881 | -0.14846 | 0.0053994 | 0.0013532
6 | 0.97521 | -0.17426 | 0.0013958 | 0.00034981
7 | 0.97386 | -0.18393 | 0 | 0
8 | 0.97408 | -0.18237 | 0.0044127 | 0.0011059
9 | 0.97506 | -0.17532 | 0.0024583 | 0.00061611
10 | 0.97341 | -0.18713 | 0.0012152 | 0.00030457
11 | 0.97348 | -0.18667 | 0.0011681 | 0.00029275
12 | 0.97372 | -0.18493 | 0 | 0
13 | 0.97321 | -0.18857 | 0.0010258 | 0.0002571
14 | 0.97319 | -0.18876 | 0.0010201 | 0.00025566
15 | 0.97331 | -0.18784 | 0.0011658 | 0.00029219
16 | 0.97317 | -0.18889 | 0.0010239 | 0.00025661
17 | 0.97336 | -0.18752 | 0.0011594 | 0.00029058
18 | 0.97316 | -0.18893 | 0.0010043 | 0.00025171
19 | 0.97341 | -0.18713 | 0.0011627 | 0.00029141
20 | 0.97337 | -0.18746 | 0.0011819 | 0.0002962
21 | 0.97331 | -0.18791 | 0.0012168 | 0.00030496
22 | 0.97306 | -0.18966 | 0.001006 | 0.00025212
23 | 0.97311 | -0.18928 | 0.001184 | 0.00029675
24 | 0.97305 | -0.18978 | 0.0011286 | 0.00028286
25 | 0.97315 | -0.18905 | 0.0011702 | 0.00029327
26 | 0.97326 | -0.18827 | 0.0011485 | 0.00028784
27 | 0.9734 | -0.18723 | 0 | 0
28 | 0.97368 | -0.18522 | 0.0017192 | 0.00043087
29 | 0.97312 | -0.18922 | 0 | 0
30 | 0.97334 | -0.18764 | 0.0027594 | 0.00069157
31 | 0.9731 | -0.18942 | 0.0010037 | 0.00025156
32 | 0.97308 | -0.18954 | 0 | 0
33 | 0.9729 | -0.1908 | 0 | 0
34 | 0.97289 | -0.19093 | 0.0013874 | 0.00034772
35 | 0.97247 | -0.19389 | 0.000753 | 0.00018872
36 | 0.97258 | -0.19315 | 0 | 0
37 | 0.97235 | -0.19481 | 0.0035318 | 0.00088516
38 | 0.97255 | -0.19336 | 0 | 0
39 | 0.97251 | -0.19364 | 0.003024 | 0.00075788
40 | 0.97222 | -0.1957 | 0.00089828 | 0.00022513
41 | 0.97287 | -0.19101 | 0.0023138 | 0.00057988
42 | 0.97222 | -0.19572 | 0.00083802 | 0.00021003
43 | 0.9721 | -0.19661 | 0.0005584 | 0.00013995
44 | 0.9721 | -0.1966 | 0.0005939 | 0.00014884
45 | 0.9721 | -0.19658 | 0.00079562 | 0.0001994
46 | 0.9721 | -0.19657 | 0.00076803 | 0.00019249
47 | 0.97211 | -0.19653 | 0.0011539 | 0.00028919
48 | 0.97219 | -0.19597 | 0.00085291 | 0.00021376
49 | 0.9728 | -0.19157 | 0.001088 | 0.00027267
50 | 0.97264 | -0.19266 | 0.0016137 | 0.00040442
51 | 0.9726 | -0.19298 | 0.0048305 | 0.0012106
52 | 0.97923 | -0.14574 | 0.0014478 | 0.00036284
53 | 0.97888 | -0.14825 | 0.0021467 | 0.00053802
54 | 0.98009 | -0.13953 | 0 | 0
55 | 0.97861 | -0.15012 | 0.00057132 | 0.00014319
56 | 0.98065 | -0.13556 | 0.0014618 | 0.00036637
57 | 0.97859 | -0.15026 | 0.0030167 | 0.00075607
58 | 0.98126 | -0.13121 | 0 | 0
59 | 0.97844 | -0.15141 | 0.0029843 | 0.00074794
60 | 0.98133 | -0.13074 | 0 | 0
61 | 0.98071 | -0.13513 | 0.0013608 | 0.00034105
62 | 0.98455 | -0.10779 | 0.0019778 | 0.00049568
63 | 0.9809 | -0.13377 | 0.0013865 | 0.00034748
64 | 0.98065 | -0.13554 | 0.00049311 | 0.00012359
65 | 0.98727 | -0.088558 | 0.0054674 | 0.0013703
66 | 0.98063 | -0.13573 | 0.0030585 | 0.00076653
67 | 0.98014 | -0.13925 | 0.0013157 | 0.00032975
68 | 0.97839 | -0.15176 | 0.00063291 | 0.00015862
69 | 0.97835 | -0.15203 | 0.00072874 | 0.00018264
70 | 0.98775 | -0.085218 | 0 | 0
71 | 0.98838 | -0.080806 | 0.002596 | 0.00065061
72 | 0.98732 | -0.088195 | 0 | 0
73 | 0.98971 | -0.071462 | 0 | 0
74 | 0.9853 | -0.10244 | 0.0018977 | 0.00047561
75 | 0.98725 | -0.088748 | 0.0016983 | 0.00042565
76 | 0.98954 | -0.07265 | 0.0023264 | 0.00058304
77 | 0.98973 | -0.071307 | 0.001651 | 0.00041377
78 | 0.98497 | -0.1048 | 0 | 0
79 | 0.98722 | -0.088936 | 0.0015212 | 0.00038124
80 | 0.99307 | -0.047942 | 0.0019939 | 0.00049972
81 | 0.99408 | -0.040918 | 0 | 0
82 | 0.99374 | -0.043311 | 0.0040722 | 0.0010206
83 | 0.99554 | -0.03079 | 0.0021912 | 0.00054918
84 | 0.9894 | -0.073622 | 0.0024699 | 0.000619
85 | 0.99364 | -0.044063 | 0.0059739 | 0.0014972
86 | 0.99812 | -0.012942 | 0.0028385 | 0.0007114
87 | 0.98931 | -0.074281 | 0.0024034 | 0.00060234
88 | 0.98477 | -0.10619 | 0 | 0
89 | 0.98458 | -0.10754 | 0.0016388 | 0.00041073
90 | 0.98475 | -0.10635 | 0 | 0
91 | 0.98466 | -0.10697 | 0.0025656 | 0.00064299
92 | 0.98374 | -0.11351 | 0.0011303 | 0.00028328
93 | 0.98463 | -0.10718 | 0.0018818 | 0.00047163
94 | 0.98334 | -0.11633 | 0.0028272 | 0.00070856
95 | 0.98212 | -0.12497 | 0.0046957 | 0.0011768
96 | 0.98195 | -0.12615 | 0.0057286 | 0.0014357
97 | 0.98457 | -0.10763 | 0.00099695 | 0.00024986
98 | 0.98103 | -0.13267 | 0.0047461 | 0.0011895
99 | 0.98081 | -0.13421 | 0.0041586 | 0.0010422
100 | 0.98009 | -0.13934 | 0 | 0
101 | 1 | 0 | -0.19438 | -0.048947
102 | 0.99966 | -0.0023238 | 0.001478 | 0.00037043
103 | 0.99981 | -0.0013257 | 0.0039957 | 0.0010014
104 | 0.97919 | -0.14602 | 0.0025556 | 0.00064049
105 | 0.97918 | -0.14611 | 0.0020937 | 0.00052474
106 | 0.97933 | -0.14502 | 0 | 0
107 | 0.97937 | -0.14472 | 0 | 0
108 | 0.97928 | -0.14534 | 0.0014364 | 0.00035999
109 | 0.97964 | -0.14277 | 0.0031158 | 0.0007809
110 | 0.97936 | -0.14481 | 0.00050335 | 0.00012615
111 | 0.97986 | -0.1412 | 0 | 0
112 | 0.97817 | -0.15337 | 0.0029698 | 0.0007443
113 | 0.97836 | -0.15196 | 0.0020722 | 0.00051933
114 | 0.97884 | -0.14853 | 0 | 0
115 | 0.97932 | -0.14508 | 0 | 0
116 | 0.98024 | -0.13851 | 0.0017269 | 0.00043281
117 | 0.97974 | -0.1421 | 0.0018669 | 0.00046789
118 | 0.97956 | -0.14338 | 0.0013221 | 0.00033135
119 | 0.97948 | -0.1439 | 0.0029268 | 0.00073352
120 | 0.97969 | -0.14241 | 0.0025022 | 0.00062712
121 | 0.98926 | -0.074631 | 0.0026356 | 0.00066055
122 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0014119 | -0.00035387 | 0.001412 | 0.00035361 | 6.6125e-08 | -2.5962e-07 | 0.0021541 | 0.002154 | 0.0021541 | 0.97535 | -0.1732 | 0.9754 | -0.17286 | 0.79781
1 | 0.0050759 | 0.0012714 | -0.0050752 | -0.0012714 | 6.9716e-07 | 3.5594e-08 | 0.0077433 | 0.0077434 | 0.0077434 | 0.9754 | -0.17286 | 0.97526 | -0.17386 | 2.8679
2 | 0.053005 | 0.013291 | -0.052941 | -0.013268 | 6.4524e-05 | 2.3043e-05 | 0.080865 | 0.080865 | 0.080865 | 0.9754 | -0.17286 | 0.97417 | -0.18166 | 9.9834
3 | -0.059493 | -0.014916 | 0.059603 | 0.014956 | 0.00010963 | 3.9763e-05 | 0.090762 | 0.090761 | 0.090762 | 0.9754 | -0.17286 | 0.97725 | -0.15959 | 11.2052
4 | 0.0038547 | 0.00096551 | -0.0038544 | -0.00096555 | 2.1323e-07 | -4.1262e-08 | 0.0058811 | 0.0058811 | 0.0058811 | 0.97526 | -0.17386 | 0.97521 | -0.17426 | 2.1782
5 | 0.017998 | 0.0045105 | -0.017992 | -0.0045085 | 5.6676e-06 | 2.0303e-06 | 0.027491 | 0.027491 | 0.027491 | 0.97417 | -0.18166 | 0.97386 | -0.18393 | 10.1819
6 | 0.034943 | 0.0087577 | -0.034939 | -0.0087566 | 3.4531e-06 | 1.1105e-06 | 0.053374 | 0.053374 | 0.053374 | 0.97417 | -0.18166 | 0.97408 | -0.18237 | 6.5894
7 | -0.059603 | -0.014956 | 0.059695 | 0.014989 | 9.2143e-05 | 3.3415e-05 | 0.090761 | 0.09076 | 0.090761 | 0.97725 | -0.15959 | 0.97881 | -0.14846 | 11.2051
8 | -0.065094 | -0.016343 | 0.065177 | 0.016373 | 8.2589e-05 | 3.0235e-05 | 0.098969 | 0.098968 | 0.098969 | 0.97881 | -0.14846 | 0.98009 | -0.13934 | 12.2183
9 | 0.0024587 | 0.00061574 | -0.0024583 | -0.00061611 | 3.5999e-07 | -3.729e-07 | 0.0037514 | 0.0037516 | 0.0037516 | 0.97521 | -0.17426 | 0.97506 | -0.17532 | 1.3895
10 | 0.0092571 | 0.0023196 | -0.009253 | -0.0023184 | 4.0892e-06 | 1.1654e-06 | 0.014144 | 0.014144 | 0.014144 | 0.97386 | -0.18393 | 0.97341 | -0.18713 | 5.2387
11 | 0.0087352 | 0.0021889 | -0.0087319 | -0.002188 | 3.3064e-06 | 9.0174e-07 | 0.013347 | 0.013347 | 0.013347 | 0.97386 | -0.18393 | 0.97348 | -0.18667 | 4.9433
12 | 0.030527 | 0.0076506 | -0.030516 | -0.0076474 | 1.0825e-05 | 3.27e-06 | 0.046633 | 0.046634 | 0.046634 | 0.97408 | -0.18237 | 0.97372 | -0.18493 | 5.7572
13 | 0.0080377 | 0.0020139 | -0.0080374 | -0.0020138 | 3.692e-07 | 9.3281e-08 | 0.012287 | 0.012287 | 0.012287 | 0.97341 | -0.18713 | 0.97337 | -0.18746 | 4.5506
14 | 0.0075638 | 0.0018953 | -0.0075633 | -0.0018951 | 4.8427e-07 | 1.1408e-07 | 0.011562 | 0.011562 | 0.011562 | 0.97348 | -0.18667 | 0.97341 | -0.18713 | 4.2821
15 | 0.028797 | 0.0072167 | -0.028787 | -0.007214 | 9.1425e-06 | 2.6696e-06 | 0.044006 | 0.044007 | 0.044007 | 0.97372 | -0.18493 | 0.9734 | -0.18723 | 5.4329
16 | 0.0017193 | 0.00043071 | -0.0017192 | -0.00043087 | 6.6824e-08 | -1.6727e-07 | 0.0026273 | 0.0026274 | 0.0026274 | 0.97372 | -0.18493 | 0.97368 | -0.18522 | 0.97309
17 | 0.0030485 | 0.00076384 | -0.0030484 | -0.00076388 | 7.9407e-08 | -4.2244e-08 | 0.0046609 | 0.004661 | 0.004661 | 0.97321 | -0.18857 | 0.97319 | -0.18876 | 1.7263
18 | -0.0040743 | -0.0010209 | 0.0040747 | 0.0010209 | 4.1167e-07 | -5.294e-08 | 0.0062294 | 0.0062293 | 0.0062294 | 0.97321 | -0.18857 | 0.97331 | -0.18784 | 2.3072
19 | 0.0020283 | 0.00050822 | -0.0020282 | -0.00050828 | 3.5124e-08 | -5.9209e-08 | 0.0031012 | 0.0031012 | 0.0031012 | 0.97319 | -0.18876 | 0.97317 | -0.18889 | 1.1486
20 | -0.0052405 | -0.0013131 | 0.0052408 | 0.0013131 | 2.3188e-07 | 1.7228e-08 | 0.0080117 | 0.0080117 | 0.0080117 | 0.97331 | -0.18784 | 0.97336 | -0.18752 | 2.9673
21 | 0.0010043 | 0.00025166 | -0.0010043 | -0.00025171 | 5.6796e-09 | -4.5769e-08 | 0.0015357 | 0.0015357 | 0.0015357 | 0.97317 | -0.18889 | 0.97316 | -0.18893 | 0.56877
22 | -0.0064002 | -0.0016037 | 0.0064006 | 0.0016037 | 3.454e-07 | 6.0972e-08 | 0.0097842 | 0.0097841 | 0.0097842 | 0.97336 | -0.18752 | 0.97341 | -0.18713 | 3.6238
23 | 0.0068555 | 0.0017176 | -0.0068551 | -0.0017175 | 4.2487e-07 | 8.636e-08 | 0.01048 | 0.01048 | 0.01048 | 0.97337 | -0.18746 | 0.97331 | -0.18791 | 3.8815
24 | 0.0056383 | 0.0014125 | -0.005638 | -0.0014125 | 2.8343e-07 | 3.3038e-08 | 0.0086197 | 0.0086198 | 0.0086198 | 0.97331 | -0.18791 | 0.97326 | -0.18827 | 3.1925
25 | -0.0021346 | -0.00053485 | 0.0021347 | 0.00053469 | 1.1252e-07 | -1.6696e-07 | 0.0032642 | 0.0032641 | 0.0032642 | 0.97306 | -0.18966 | 0.97311 | -0.18928 | 1.209
26 | 0.0011286 | 0.00028274 | -0.0011286 | -0.00028286 | 1.8754e-08 | -1.1812e-07 | 0.0017259 | 0.0017259 | 0.0017259 | 0.97306 | -0.18966 | 0.97305 | -0.18978 | 0.63923
27 | -0.0033187 | -0.00083144 | 0.0033188 | 0.0008314 | 1.048e-07 | -4.0716e-08 | 0.0050747 | 0.0050746 | 0.0050747 | 0.97311 | -0.18928 | 0.97315 | -0.18905 | 1.8795
28 | -0.004489 | -0.0011247 | 0.0044895 | 0.0011247 | 4.859e-07 | -1.8485e-08 | 0.0068639 | 0.0068639 | 0.0068639 | 0.97315 | -0.18905 | 0.97326 | -0.18827 | 2.5422
29 | 0.026028 | 0.0065225 | -0.026021 | -0.0065206 | 7.1769e-06 | 1.9478e-06 | 0.039788 | 0.039788 | 0.039788 | 0.9734 | -0.18723 | 0.97312 | -0.18922 | 4.9121
30 | 0.0027596 | 0.00069146 | -0.0027594 | -0.00069157 | 1.5882e-07 | -1.1669e-07 | 0.0042184 | 0.0042185 | 0.0042185 | 0.9734 | -0.18723 | 0.97334 | -0.18764 | 1.5624
31 | 0.0010038 | 0.00025134 | -0.0010037 | -0.00025156 | 2.7004e-08 | -2.1784e-07 | 0.0015348 | 0.0015349 | 0.0015349 | 0.97312 | -0.18922 | 0.9731 | -0.18942 | 0.56846
32 | 0.025017 | 0.0062692 | -0.025016 | -0.006269 | 1.1061e-06 | 2.8999e-07 | 0.038254 | 0.038254 | 0.038254 | 0.97312 | -0.18922 | 0.97308 | -0.18954 | 4.7227
33 | 0.016093 | 0.0040327 | -0.01609 | -0.004032 | 2.7951e-06 | 7.0756e-07 | 0.024609 | 0.024609 | 0.024609 | 0.97308 | -0.18954 | 0.9729 | -0.1908 | 4.5572
34 | 0.0089231 | 0.0022363 | -0.0089214 | -0.0022358 | 1.7145e-06 | 4.7614e-07 | 0.013645 | 0.013645 | 0.013645 | 0.97308 | -0.18954 | 0.97289 | -0.19093 | 5.0537
35 | 0.0023138 | 0.0005798 | -0.0023138 | -0.00057988 | 6.9365e-08 | -8.354e-08 | 0.0035389 | 0.0035389 | 0.0035389 | 0.9729 | -0.1908 | 0.97287 | -0.19101 | 1.3107
36 | 0.013776 | 0.0034522 | -0.013772 | -0.0034507 | 4.488e-06 | 1.525e-06 | 0.02107 | 0.02107 | 0.02107 | 0.9729 | -0.1908 | 0.97258 | -0.19315 | 7.8037
37 | 0.0075339 | 0.0018881 | -0.0075333 | -0.0018879 | 6.6522e-07 | 1.5617e-07 | 0.011523 | 0.011523 | 0.011523 | 0.97289 | -0.19093 | 0.9728 | -0.19157 | 4.2678
38 | -0.0042853 | -0.0010737 | 0.0042857 | 0.0010737 | 4.4067e-07 | -3.433e-08 | 0.0065569 | 0.0065569 | 0.0065569 | 0.97247 | -0.19389 | 0.97258 | -0.19315 | 2.4285
39 | 0.0035323 | 0.00088502 | -0.0035318 | -0.00088516 | 4.4801e-07 | -1.3258e-07 | 0.0054047 | 0.0054049 | 0.0054049 | 0.97247 | -0.19389 | 0.97235 | -0.19481 | 2.0018
40 | 0.009486 | 0.002377 | -0.0094857 | -0.0023769 | 2.7167e-07 | 7.884e-08 | 0.014513 | 0.014513 | 0.014513 | 0.97258 | -0.19315 | 0.97255 | -0.19336 | 5.3752
41 | 0.0030241 | 0.00075782 | -0.003024 | -0.00075788 | 1.1657e-07 | -6.3442e-08 | 0.0046269 | 0.0046269 | 0.0046269 | 0.97255 | -0.19336 | 0.97251 | -0.19364 | 1.7137
42 | 0.0064616 | 0.0016191 | -0.0064595 | -0.0016187 | 2.0974e-06 | 3.801e-07 | 0.0098863 | 0.0098864 | 0.0098864 | 0.97255 | -0.19336 | 0.97222 | -0.1957 | 3.6616
43 | 0.0055612 | 0.0013936 | -0.0055612 | -0.0013935 | 1.5125e-08 | 1.6685e-09 | 0.0085116 | 0.0085116 | 0.0085116 | 0.97222 | -0.1957 | 0.97222 | -0.19572 | 3.1524
44 | 0.0047232 | 0.0011835 | -0.0047231 | -0.0011835 | 1.6317e-07 | 7.0976e-10 | 0.007229 | 0.007229 | 0.007229 | 0.97222 | -0.19572 | 0.97219 | -0.19597 | 2.6774
45 | -0.0005584 | -0.00013995 | 0.0005584 | 0.00013994 | 4.279e-10 | -1.1469e-08 | 0.00085476 | 0.00085476 | 0.00085476 | 0.9721 | -0.19661 | 0.9721 | -0.1966 | 0.31658
46 | -0.0011523 | -0.00028878 | 0.0011523 | 0.00028875 | 4.5526e-09 | -2.7321e-08 | 0.0017638 | 0.0017638 | 0.0017638 | 0.9721 | -0.1966 | 0.9721 | -0.19658 | 0.65328
47 | -0.0019479 | -0.00048816 | 0.0019479 | 0.00048815 | 2.5186e-09 | -4.6598e-09 | 0.0029817 | 0.0029817 | 0.0029817 | 0.9721 | -0.19658 | 0.9721 | -0.19657 | 1.1043
48 | -0.002716 | -0.00068064 | 0.002716 | 0.00068063 | 1.2313e-08 | -9.4185e-09 | 0.0041573 | 0.0041573 | 0.0041573 | 0.9721 | -0.19657 | 0.97211 | -0.19653 | 1.5398
49 | -0.0038698 | -0.00096982 | 0.0038701 | 0.00096976 | 3.0027e-07 | -5.4546e-08 | 0.0059236 | 0.0059235 | 0.0059236 | 0.97211 | -0.19653 | 0.97219 | -0.19597 | 2.1939
50 | 0.0064453 | 0.0016152 | -0.0064443 | -0.0016151 | 9.7947e-07 | 1.7626e-07 | 0.0098589 | 0.009859 | 0.009859 | 0.9728 | -0.19157 | 0.97264 | -0.19266 | 3.6515
51 | 0.0048307 | 0.0012106 | -0.0048305 | -0.0012106 | 2.0922e-07 | 4.2799e-09 | 0.0073903 | 0.0073903 | 0.0073903 | 0.97264 | -0.19266 | 0.9726 | -0.19298 | 2.7372
52 | 0.010087 | 0.0025273 | -0.010084 | -0.0025262 | 3.4926e-06 | 1.0437e-06 | 0.015328 | 0.015328 | 0.015328 | 0.97923 | -0.14574 | 0.97888 | -0.14825 | 5.6771
53 | -0.011535 | -0.0028901 | 0.011545 | 0.0028933 | 9.917e-06 | 3.1629e-06 | 0.017528 | 0.017528 | 0.017528 | 0.97923 | -0.14574 | 0.98009 | -0.13953 | 6.4919
54 | 0.007937 | 0.0019882 | -0.007935 | -0.0019877 | 2.0576e-06 | 5.0668e-07 | 0.012065 | 0.012065 | 0.012065 | 0.97888 | -0.14825 | 0.97861 | -0.15012 | 4.4685
55 | -0.011545 | -0.0028933 | 0.011551 | 0.0028953 | 6.3562e-06 | 2.0266e-06 | 0.017528 | 0.017528 | 0.017528 | 0.98009 | -0.13953 | 0.98065 | -0.13556 | 6.4918
56 | 0.0073636 | 0.0018445 | -0.0073635 | -0.0018445 | 1.4494e-07 | 3.2467e-08 | 0.011196 | 0.011196 | 0.011196 | 0.97861 | -0.15012 | 0.97859 | -0.15026 | 4.1468
57 | -0.013013 | -0.0032617 | 0.013021 | 0.0032643 | 7.833e-06 | 2.6063e-06 | 0.019746 | 0.019746 | 0.019746 | 0.98065 | -0.13556 | 0.98126 | -0.13121 | 7.3133
58 | 0.0043468 | 0.0010884 | -0.0043461 | -0.0010885 | 6.8552e-07 | -5.226e-08 | 0.0066092 | 0.0066093 | 0.0066093 | 0.97859 | -0.15026 | 0.97844 | -0.15141 | 2.4479
59 | -0.023756 | -0.0059533 | 0.023758 | 0.0059539 | 1.5548e-06 | 5.7375e-07 | 0.036024 | 0.036024 | 0.036024 | 0.98126 | -0.13121 | 0.98133 | -0.13074 | 13.3424
60 | 0.010735 | 0.002689 | -0.010729 | -0.0026872 | 5.8131e-06 | 1.792e-06 | 0.016279 | 0.016279 | 0.016279 | 0.98126 | -0.13121 | 0.98071 | -0.13513 | 6.0292
61 | 0.0013617 | 0.00034054 | -0.0013617 | -0.00034083 | 6.7429e-08 | -2.9056e-07 | 0.0020707 | 0.0020708 | 0.0020708 | 0.97844 | -0.15141 | 0.97839 | -0.15176 | 0.76697
62 | -0.045784 | -0.011476 | 0.04593 | 0.011532 | 0.000146 | 5.5539e-05 | 0.069425 | 0.069425 | 0.069425 | 0.98133 | -0.13074 | 0.98455 | -0.10779 | 25.7129
63 | 0.022027 | 0.0055221 | -0.022017 | -0.0055187 | 9.241e-06 | 3.3866e-06 | 0.0334 | 0.0334 | 0.0334 | 0.98133 | -0.13074 | 0.9809 | -0.13377 | 12.3705
64 | 0.0093686 | 0.0023462 | -0.0093681 | -0.002346 | 5.3499e-07 | 1.5222e-07 | 0.014214 | 0.014214 | 0.014214 | 0.98071 | -0.13513 | 0.98065 | -0.13554 | 5.2645
65 | -0.047908 | -0.012027 | 0.048036 | 0.012076 | 0.0001283 | 4.8847e-05 | 0.072414 | 0.072414 | 0.072414 | 0.98455 | -0.10779 | 0.98727 | -0.088558 | 26.8199
66 | 0.020631 | 0.0051712 | -0.020625 | -0.0051692 | 5.5828e-06 | 2.032e-06 | 0.031297 | 0.031297 | 0.031297 | 0.9809 | -0.13377 | 0.98063 | -0.13573 | 11.5915
67 | 0.008875 | 0.0022224 | -0.0088704 | -0.0022212 | 4.5415e-06 | 1.2406e-06 | 0.013466 | 0.013466 | 0.013466 | 0.98065 | -0.13554 | 0.98014 | -0.13925 | 4.9875
68 | -0.053504 | -0.013446 | 0.053529 | 0.013456 | 2.4894e-05 | 9.4961e-06 | 0.080654 | 0.080654 | 0.080654 | 0.98727 | -0.088558 | 0.98775 | -0.085218 | 29.8718
69 | 0.017567 | 0.0044027 | -0.01756 | -0.0044003 | 6.7593e-06 | 2.4075e-06 | 0.026656 | 0.026656 | 0.026656 | 0.98063 | -0.13573 | 0.98024 | -0.13851 | 9.8727
70 | 0.0075547 | 0.0018914 | -0.0075514 | -0.0018907 | 3.3047e-06 | 7.6381e-07 | 0.011469 | 0.011469 | 0.011469 | 0.98014 | -0.13925 | 0.97969 | -0.14241 | 4.2477
71 | 0.00072877 | 0.00018221 | -0.00072874 | -0.00018264 | 2.6892e-08 | -4.3025e-07 | 0.0011082 | 0.0011084 | 0.0011084 | 0.97839 | -0.15176 | 0.97835 | -0.15203 | 0.41051
72 | -0.15485 | -0.038966 | 0.15495 | 0.039003 | 9.5389e-05 | 3.6364e-05 | 0.23333 | 0.23333 | 0.23333 | 0.98775 | -0.085218 | 0.98838 | -0.080806 | 28.8066
73 | 0.10132 | 0.02551 | -0.10128 | -0.025495 | 4.213e-05 | 1.587e-05 | 0.15268 | 0.15268 | 0.15268 | 0.98775 | -0.085218 | 0.98732 | -0.088195 | 18.8493
74 | -0.15754 | -0.039653 | 0.15775 | 0.039732 | 0.00020583 | 7.849e-05 | 0.23724 | 0.23724 | 0.23724 | 0.98838 | -0.080806 | 0.98971 | -0.071462 | 29.289
75 | 0.098059 | 0.024688 | -0.097865 | -0.024615 | 0.00019469 | 7.3242e-05 | 0.14783 | 0.14783 | 0.14783 | 0.98732 | -0.088195 | 0.9853 | -0.10244 | 18.2503
76 | 0.0032198 | 0.00080663 | -0.0032196 | -0.00080675 | 2.462e-07 | -1.1958e-07 | 0.0048525 | 0.0048526 | 0.0048526 | 0.98732 | -0.088195 | 0.98725 | -0.088748 | 1.7973
77 | 0.0098384 | 0.0024655 | -0.0098368 | -0.0024651 | 1.6175e-06 | 4.699e-07 | 0.014792 | 0.014792 | 0.014792 | 0.98971 | -0.071462 | 0.98954 | -0.07265 | 5.4785
78 | -0.16759 | -0.042197 | 0.16759 | 0.042199 | 3.6189e-06 | 1.3813e-06 | 0.25203 | 0.25203 | 0.25203 | 0.98971 | -0.071462 | 0.98973 | -0.071307 | 31.1152
79 | 0.095967 | 0.024139 | -0.095935 | -0.024127 | 3.1704e-05 | 1.1917e-05 | 0.14496 | 0.14496 | 0.14496 | 0.9853 | -0.10244 | 0.98497 | -0.1048 | 17.8965
80 | 0.0015212 | 0.0003811 | -0.0015212 | -0.00038124 | 3.9654e-08 | -1.3932e-07 | 0.0022928 | 0.0022928 | 0.0022928 | 0.98725 | -0.088748 | 0.98722 | -0.088936 | 0.8492
81 | 0.0075104 | 0.001882 | -0.0075094 | -0.0018818 | 1.0102e-06 | 2.2551e-07 | 0.011294 | 0.011294 | 0.011294 | 0.98954 | -0.07265 | 0.9894 | -0.073622 | 4.1829
82 | -0.16924 | -0.042612 | 0.16979 | 0.042824 | 0.00055437 | 0.00021163 | 0.25452 | 0.25451 | 0.25452 | 0.98973 | -0.071307 | 0.99307 | -0.047942 | 31.4216
83 | 0.0054461 | 0.0013635 | -0.0054451 | -0.0013634 | 1.0385e-06 | 8.6533e-08 | 0.0082271 | 0.0082272 | 0.0082272 | 0.98497 | -0.1048 | 0.98477 | -0.10619 | 3.0471
84 | 0.090489 | 0.022764 | -0.090454 | -0.022751 | 3.4516e-05 | 1.2937e-05 | 0.13673 | 0.13673 | 0.13673 | 0.98497 | -0.1048 | 0.98458 | -0.10754 | 16.8808
85 | -0.17179 | -0.043324 | 0.17196 | 0.043388 | 0.00016933 | 6.4649e-05 | 0.2575 | 0.2575 | 0.2575 | 0.99307 | -0.047942 | 0.99408 | -0.040918 | 31.7904
86 | 0.01005 | 0.0025189 | -0.010047 | -0.0025179 | 3.3298e-06 | 9.7511e-07 | 0.015044 | 0.015044 | 0.015044 | 0.99408 | -0.040918 | 0.99374 | -0.043311 | 5.5718
87 | -0.18201 | -0.045907 | 0.18227 | 0.046006 | 0.00025886 | 9.891e-05 | 0.27255 | 0.27255 | 0.27255 | 0.99408 | -0.040918 | 0.99554 | -0.03079 | 33.6476
88 | 0.0059746 | 0.0014973 | -0.0059739 | -0.0014972 | 6.214e-07 | 7.7816e-08 | 0.0089462 | 0.0089462 | 0.0089462 | 0.99374 | -0.043311 | 0.99364 | -0.044063 | 3.3134
89 | -0.18446 | -0.046555 | 0.18492 | 0.046732 | 0.00046341 | 0.00017709 | 0.27582 | 0.27582 | 0.27582 | 0.99554 | -0.03079 | 0.99812 | -0.012942 | 34.0519
90 | 0.0050396 | 0.0012628 | -0.0050391 | -0.0012628 | 4.5991e-07 | 1.2128e-08 | 0.0075792 | 0.0075793 | 0.0075793 | 0.9894 | -0.073622 | 0.98931 | -0.074281 | 2.8071
91 | -0.18776 | -0.047444 | 0.18804 | 0.047551 | 0.00028102 | 0.00010741 | 0.28005 | 0.28005 | 0.28005 | 0.99812 | -0.012942 | 0.99966 | -0.0023238 | 34.5743
92 | 0.0026358 | 0.00066043 | -0.0026356 | -0.00066055 | 1.2752e-07 | -1.179e-07 | 0.0039644 | 0.0039644 | 0.0039644 | 0.98931 | -0.074281 | 0.98926 | -0.074631 | 1.4683
93 | 0.0028792 | 0.00072068 | -0.0028792 | -0.00072072 | 6.4465e-08 | -4.4658e-08 | 0.0043502 | 0.0043503 | 0.0043503 | 0.98477 | -0.10619 | 0.98475 | -0.10635 | 1.6112
94 | 0.0025658 | 0.00064272 | -0.0025656 | -0.00064299 | 2.7824e-07 | -2.7037e-07 | 0.0038769 | 0.0038771 | 0.0038771 | 0.98477 | -0.10619 | 0.98466 | -0.10697 | 1.436
95 | 0.088816 | 0.02234 | -0.088742 | -0.022312 | 7.3813e-05 | 2.7639e-05 | 0.13426 | 0.13426 | 0.13426 | 0.98458 | -0.10754 | 0.98374 | -0.11351 | 16.5751
96 | 0.0028792 | 0.00072072 | -0.0028788 | -0.00072095 | 3.3011e-07 | -2.2862e-07 | 0.0043503 | 0.0043504 | 0.0043504 | 0.98475 | -0.10635 | 0.98463 | -0.10718 | 1.6113
97 | 0.087612 | 0.022029 | -0.087577 | -0.022016 | 3.4427e-05 | 1.2882e-05 | 0.13255 | 0.13255 | 0.13255 | 0.98374 | -0.11351 | 0.98334 | -0.11633 | 16.364
98 | 0.00099701 | 0.00024932 | -0.00099695 | -0.00024986 | 6.2441e-08 | -5.3665e-07 | 0.0015065 | 0.0015067 | 0.0015067 | 0.98463 | -0.10718 | 0.98457 | -0.10763 | 0.55805
99 | 0.08475 | 0.021308 | -0.084648 | -0.02127 | 0.00010187 | 3.8051e-05 | 0.12827 | 0.12827 | 0.12827 | 0.98334 | -0.11633 | 0.98212 | -0.12497 | 15.8359
100 | 0.079952 | 0.020093 | -0.079939 | -0.020088 | 1.3171e-05 | 4.9019e-06 | 0.12116 | 0.12116 | 0.12116 | 0.98212 | -0.12497 | 0.98195 | -0.12615 | 14.9576
101 | 0.074211 | 0.018652 | -0.074143 | -0.018627 | 6.736e-05 | 2.4937e-05 | 0.11248 | 0.11248 | 0.11248 | 0.98195 | -0.12615 | 0.98103 | -0.13267 | 13.8859
102 | 0.069397 | 0.017438 | -0.069382 | -0.017432 | 1.4874e-05 | 5.4763e-06 | 0.10528 | 0.10528 | 0.10528 | 0.98103 | -0.13267 | 0.98081 | -0.13421 | 12.9971
103 | 0.065224 | 0.01639 | -0.065177 | -0.016373 | 4.6516e-05 | 1.7027e-05 | 0.098968 | 0.098968 | 0.098968 | 0.98081 | -0.13421 | 0.98009 | -0.13934 | 12.2183
104 | 0.18958 | 0.047945 | -0.18952 | -0.047922 | 6.209e-05 | 2.3733e-05 | 0.28225 | 0.28225 | 0.28225 | 1 | 0 | 0.99966 | -0.0023238 | 34.8459
105 | 0.0039964 | 0.0010013 | -0.0039957 | -0.0010014 | 7.3314e-07 | -1.5382e-07 | 0.0059466 | 0.0059468 | 0.0059468 | 1 | 0 | 0.99981 | -0.0013257 | 2.2025
106 | 0.0020938 | 0.0005247 | -0.0020937 | -0.00052474 | 2.5548e-08 | -4.1046e-08 | 0.0031818 | 0.0031818 | 0.0031818 | 0.97919 | -0.14602 | 0.97918 | -0.14611 | 1.1784
107 | -0.0046493 | -0.0011652 | 0.00465 | 0.0011652 | 6.4339e-07 | -1.2401e-08 | 0.0070653 | 0.0070652 | 0.0070653 | 0.97919 | -0.14602 | 0.97933 | -0.14502 | 2.6168
108 | -0.0060864 | -0.0015249 | 0.0060867 | 0.001525 | 2.5236e-07 | 3.7556e-08 | 0.0092477 | 0.0092477 | 0.0092477 | 0.97933 | -0.14502 | 0.97937 | -0.14472 | 3.4251
109 | 0.0014364 | 0.00035975 | -0.0014364 | -0.00035999 | 6.3244e-08 | -2.4338e-07 | 0.0021825 | 0.0021826 | 0.0021826 | 0.97933 | -0.14502 | 0.97928 | -0.14534 | 0.80836
110 | -0.00659 | -0.0016509 | 0.0065918 | 0.0016512 | 1.7752e-06 | 3.2557e-07 | 0.010012 | 0.010012 | 0.010012 | 0.97937 | -0.14472 | 0.97964 | -0.14277 | 3.7083
111 | 0.00050336 | 0.00012594 | -0.00050335 | -0.00012615 | 6.3459e-09 | -2.1637e-07 | 0.00076471 | 0.00076479 | 0.00076479 | 0.97937 | -0.14472 | 0.97936 | -0.14481 | 0.28325
112 | -0.0097077 | -0.0024321 | 0.0097098 | 0.0024327 | 2.1053e-06 | 6.143e-07 | 0.014745 | 0.014745 | 0.014745 | 0.97964 | -0.14277 | 0.97986 | -0.1412 | 5.4611
113 | -0.015827 | -0.0039654 | 0.015833 | 0.0039675 | 5.907e-06 | 2.0654e-06 | 0.024035 | 0.024035 | 0.024035 | 0.97986 | -0.1412 | 0.98024 | -0.13851 | 8.9018
114 | 0.0061175 | 0.0015327 | -0.0061167 | -0.0015325 | 7.6027e-07 | 1.146e-07 | 0.0092898 | 0.0092899 | 0.0092899 | 0.97986 | -0.1412 | 0.97974 | -0.1421 | 3.4407
115 | -0.0029698 | -0.0007443 | 0.0029704 | 0.00074395 | 5.8013e-07 | -3.488e-07 | 0.0045178 | 0.0045175 | 0.0045178 | 0.97817 | -0.15337 | 0.97836 | -0.15196 | 1.6732
116 | -0.0050425 | -0.0012633 | 0.0050449 | 0.0012634 | 2.3873e-06 | 1.0092e-07 | 0.0076691 | 0.0076688 | 0.0076691 | 0.97836 | -0.15196 | 0.97884 | -0.14853 | 2.8404
117 | -0.0050449 | -0.0012634 | 0.0050473 | 0.0012635 | 2.4039e-06 | 1.0075e-07 | 0.0076688 | 0.0076685 | 0.0076688 | 0.97884 | -0.14853 | 0.97932 | -0.14508 | 2.8403
118 | -0.0050473 | -0.0012635 | 0.0050492 | 0.0012636 | 1.8607e-06 | 7.7382e-08 | 0.0076685 | 0.0076683 | 0.0076685 | 0.97932 | -0.14508 | 0.97969 | -0.14241 | 2.8402
119 | 0.0042498 | 0.0010647 | -0.0042491 | -0.0010647 | 7.5015e-07 | -7.4798e-08 | 0.0064544 | 0.0064546 | 0.0064546 | 0.97974 | -0.1421 | 0.97956 | -0.14338 | 2.3906
120 | 0.002927 | 0.00073338 | -0.0029268 | -0.00073352 | 2.1311e-07 | -1.3549e-07 | 0.0044462 | 0.0044463 | 0.0044463 | 0.97956 | -0.14338 | 0.97948 | -0.1439 | 1.6468

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19807 | 0.049873

## res_load
| p_mw | q_mvar
0 | 0.0014119 | 0.00035387
1 | 0.0012206 | 0.0003059
2 | 0.0053994 | 0.0013532
3 | 0.0013958 | 0.00034981
4 | 0.0044127 | 0.0011059
5 | 0.0024583 | 0.00061611
6 | 0.0012152 | 0.00030457
7 | 0.0011681 | 0.00029275
8 | 0.0010258 | 0.0002571
9 | 0.0010201 | 0.00025566
10 | 0.0011658 | 0.00029219
11 | 0.0010239 | 0.00025661
12 | 0.0011594 | 0.00029058
13 | 0.0010043 | 0.00025171
14 | 0.0011627 | 0.00029141
15 | 0.0011819 | 0.0002962
16 | 0.0012168 | 0.00030496
17 | 0.001006 | 0.00025212
18 | 0.001184 | 0.00029675
19 | 0.0011286 | 0.00028286
20 | 0.0011702 | 0.00029327
21 | 0.0011485 | 0.00028784
22 | 0.0017192 | 0.00043087
23 | 0.0027594 | 0.00069157
24 | 0.0010037 | 0.00025156
25 | 0.0013874 | 0.00034772
26 | 0.000753 | 0.00018872
27 | 0.0035318 | 0.00088516
28 | 0.003024 | 0.00075788
29 | 0.00089828 | 0.00022513
30 | 0.0023138 | 0.00057988
31 | 0.00083802 | 0.00021003
32 | 0.0005584 | 0.00013995
33 | 0.0005939 | 0.00014884
34 | 0.00079562 | 0.0001994
35 | 0.00076803 | 0.00019249
36 | 0.0011539 | 0.00028919
37 | 0.00085291 | 0.00021376
38 | 0.001088 | 0.00027267
39 | 0.0016137 | 0.00040442
40 | 0.0048305 | 0.0012106
41 | 0.0014478 | 0.00036284
42 | 0.0021467 | 0.00053802
43 | 0.00057132 | 0.00014319
44 | 0.0014618 | 0.00036637
45 | 0.0030167 | 0.00075607
46 | 0.0029843 | 0.00074794
47 | 0.0013608 | 0.00034105
48 | 0.0019778 | 0.00049568
49 | 0.0013865 | 0.00034748
50 | 0.00049311 | 0.00012359
51 | 0.0054674 | 0.0013703
52 | 0.0030585 | 0.00076653
53 | 0.0013157 | 0.00032975
54 | 0.00063291 | 0.00015862
55 | 0.00072874 | 0.00018264
56 | 0.002596 | 0.00065061
57 | 0.0018977 | 0.00047561
58 | 0.0016983 | 0.00042565
59 | 0.0023264 | 0.00058304
60 | 0.001651 | 0.00041377
61 | 0.0015212 | 0.00038124
62 | 0.0019939 | 0.00049972
63 | 0.0040722 | 0.0010206
64 | 0.0021912 | 0.00054918
65 | 0.0024699 | 0.000619
66 | 0.0059739 | 0.0014972
67 | 0.0028385 | 0.0007114
68 | 0.0024034 | 0.00060234
69 | 0.0016388 | 0.00041073
70 | 0.0025656 | 0.00064299
71 | 0.0011303 | 0.00028328
72 | 0.0018818 | 0.00047163
73 | 0.0028272 | 0.00070856
74 | 0.0046957 | 0.0011768
75 | 0.0057286 | 0.0014357
76 | 0.00099695 | 0.00024986
77 | 0.0047461 | 0.0011895
78 | 0.0041586 | 0.0010422
79 | 0.0036968 | 0.00092651
80 | 0.001478 | 0.00037043
81 | 0.0039957 | 0.0010014
82 | 0.0025556 | 0.00064049
83 | 0.0020937 | 0.00052474
84 | 0.0014364 | 0.00035999
85 | 0.0031158 | 0.0007809
86 | 0.00050335 | 0.00012615
87 | 0.0029698 | 0.0007443
88 | 0.0020722 | 0.00051933
89 | 0.0017269 | 0.00043281
90 | 0.0018669 | 0.00046789
91 | 0.0013221 | 0.00033135
92 | 0.0029268 | 0.00073352
93 | 0.0025022 | 0.00062712
94 | 0.0026356 | 0.00066055

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1