## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2053-15_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2053-15_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2053-15_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2053-15_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2053-15_0_3_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_2053-15_0_3_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_2053-15_0_3_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_2053-15_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2053-15_0_3_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_2053-15_0_3_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_2053-15_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2053-15_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_2053-15_0_3_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_2053-15_0_3_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_2053-15_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2053-15_0_3_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_2053-15_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2053-15_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2053-15_0_3_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_2053-15_0_3_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_2053-15_0_3_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_2053-15_0_3_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_2053-15_0_3_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_2053-15_0_3_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2053-15_0_3_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_2053-15_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_2053-15_0_3_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_2053-15_0_3_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_2053-15_0_3_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_2053-15_0_3_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_2053-15_0_3_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_2053-15_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_2053-15_0_3_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_2053-15_0_3_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_2053-15_0_3_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_2053-15_0_3_node_39 | 0.4 | n |  | TRUE
36 | bus_MV_377_1_node_70 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2053-15_0_3_load_0 | 0 | 0.008546 | 0.0021418 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2053-15_0_3_load_1 | 1 | 0.0068681 | 0.0017213 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2053-15_0_3_load_16 | 5 | 0.014551 | 0.0036469 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2053-15_0_3_load_5 | 7 | 0.012911 | 0.0032358 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2053-15_0_3_load_15 | 8 | 0.0023177 | 0.00058087 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2053-15_0_3_load_4 | 9 | 0.0040634 | 0.0010184 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2053-15_0_3_load_11 | 11 | 0.0046719 | 0.0011709 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2053-15_0_3_load_26 | 13 | 0.0027594 | 0.00069157 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2053-15_0_3_load_10 | 14 | 0.020025 | 0.0050186 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2053-15_0_3_load_17 | 15 | 0.0035722 | 0.00089529 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2053-15_0_3_load_12 | 16 | 0.011529 | 0.0028895 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2053-15_0_3_load_13 | 17 | 0.0138 | 0.0034586 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2053-15_0_3_load_18 | 18 | 0.0032744 | 0.00082065 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2053-15_0_3_load_29 | 20 | 0.0032801 | 0.00082208 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2053-15_0_3_load_27 | 21 | 0.0018866 | 0.00047283 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2053-15_0_3_load_35 | 22 | 0.0051797 | 0.0012981 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2053-15_0_3_load_28 | 23 | 0.01091 | 0.0027342 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2053-15_0_3_load_24 | 24 | 0.0076801 | 0.0019248 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2053-15_0_3_load_22 | 25 | 0.00089483 | 0.00022427 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2053-15_0_3_load_23 | 26 | 0.0019333 | 0.00048454 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2053-15_0_3_load_25 | 27 | 0.0084565 | 0.0021194 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2053-15_0_3_load_30 | 29 | 0.0033953 | 0.00085094 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2053-15_0_3_load_31 | 30 | 0.00752 | 0.0018847 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2053-15_0_3_load_32 | 31 | 0.0047396 | 0.0011879 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2053-15_0_3_load_36 | 33 | 0.0013312 | 0.00033362 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2053-15_0_3_load_37 | 34 | 0.00092054 | 0.00023071 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2053-15_0_3_load_39 | 35 | 0.015637 | 0.003919 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2053-15_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.00032943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2053-15_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.020781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2053-15_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.013081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2053-15_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.012861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2053-15_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.017412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2053-15_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.032884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2053-15_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.022814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2053-15_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.023878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2053-15_0_3_line_8 | NAYY 4x150 SE | 6 | 13 | 0.021072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_2053-15_0_3_line_9 | NAYY 4x150 SE | 6 | 12 | 0.015442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2053-15_0_3_line_10 | NAYY 4x150 SE | 7 | 9 | 0.0024912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2053-15_0_3_line_11 | NAYY 4x150 SE | 8 | 17 | 0.018658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2053-15_0_3_line_12 | NAYY 4x150 SE | 10 | 11 | 0.00026049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2053-15_0_3_line_13 | NAYY 4x150 SE | 10 | 12 | 0.02249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2053-15_0_3_line_14 | NAYY 4x150 SE | 11 | 14 | 0.01911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2053-15_0_3_line_15 | NAYY 4x150 SE | 12 | 15 | 0.021671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2053-15_0_3_line_16 | NAYY 4x150 SE | 13 | 24 | 0.0033978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2053-15_0_3_line_17 | NAYY 4x150 SE | 15 | 18 | 0.0092456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2053-15_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.0038856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2053-15_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.0117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2053-15_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.0033062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2053-15_0_3_line_21 | NAYY 4x150 SE | 19 | 21 | 0.017224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2053-15_0_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.029643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2053-15_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.0082403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2053-15_0_3_line_24 | NAYY 4x150 SE | 22 | 28 | 0.010058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2053-15_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.03226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2053-15_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.002549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2053-15_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.045398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2053-15_0_3_line_28 | NAYY 4x150 SE | 28 | 32 | 0.016324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2053-15_0_3_line_29 | NAYY 4x150 SE | 28 | 31 | 0.025056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2053-15_0_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.032932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2053-15_0_3_line_31 | NAYY 4x150 SE | 30 | 31 | 0.0025941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2053-15_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.019187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2053-15_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.029605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2053-15_0_3_line_34 | NAYY 4x150 SE | 34 | 35 | 0.039455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2053-15_0_3_trafo_26 | 0.25 MVA 20/0.4 kV | 36 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2567551.4664 | 1190721.2735 | 2567551.2778 | 1190721.5436
1 | 2567539.3774 | 1190738.5798 | 2567551.2778 | 1190721.5436
2 | 2567539.3774 | 1190738.5798 | 2567529.2902 | 1190730.2191
3 | 2567519.5306 | 1190721.8121 | 2567529.2902 | 1190730.2191
4 | 2567529.2902 | 1190730.2191 | 2567526.3769 | 1190734.2927 | 2567519.165 | 1190744.3841
5 | 2567494.58 | 1190700.3142 | 2567502.2713 | 1190706.9425 | 2567519.5306 | 1190721.8121
6 | 2567519.5306 | 1190721.8121 | 2567524.4308 | 1190715.76 | 2567531.1993 | 1190708.3414 | 2567530.3967 | 1190703.4214
7 | 2567519.165 | 1190744.3841 | 2567505.2814 | 1190763.8111
8 | 2567494.58 | 1190700.3142 | 2567491.8148 | 1190703.5977 | 2567487.5875 | 1190708.6012 | 2567481.0715 | 1190716.4858
9 | 2567494.58 | 1190700.3142 | 2567483.185 | 1190689.8595
10 | 2567529.9956 | 1190700.9627 | 2567530.3967 | 1190703.4214
11 | 2567517.1795 | 1190774.849 | 2567503.7971 | 1190765.8881 | 2567505.2814 | 1190763.8111
12 | 2567498.2518 | 1190672.7775 | 2567498.0755 | 1190672.9693
13 | 2567498.0755 | 1190672.9693 | 2567496.1053 | 1190675.2035 | 2567485.4053 | 1190687.3349 | 2567483.185 | 1190689.8595
14 | 2567498.2518 | 1190672.7775 | 2567511.179 | 1190658.7037
15 | 2567483.185 | 1190689.8595 | 2567467.8589 | 1190675.7799 | 2567467.2047 | 1190675.2234
16 | 2567481.0715 | 1190716.4858 | 2567478.9069 | 1190719.105
17 | 2567460.1626 | 1190669.2326 | 2567467.2047 | 1190675.2234
18 | 2567517.1795 | 1190774.849 | 2567520.4082 | 1190777.0109
19 | 2567451.2514 | 1190661.6518 | 2567460.1626 | 1190669.2326
20 | 2567451.2514 | 1190661.6518 | 2567448.7333 | 1190659.5093
21 | 2567451.2514 | 1190661.6518 | 2567440.5306 | 1190675.1328
22 | 2567448.7333 | 1190659.5093 | 2567426.1562 | 1190640.2999
23 | 2567435.4016 | 1190681.5823 | 2567440.5306 | 1190675.1328
24 | 2567418.4958 | 1190633.7822 | 2567426.1562 | 1190640.2999
25 | 2567478.9069 | 1190719.105 | 2567458.356 | 1190743.9721
26 | 2567458.356 | 1190743.9721 | 2567456.7322 | 1190745.937
27 | 2567427.8118 | 1190780.9315 | 2567456.7322 | 1190745.937
28 | 2567405.8355 | 1190623.4346 | 2567418.4958 | 1190633.7822
29 | 2567418.4958 | 1190633.7822 | 2567435.4227 | 1190615.3078
30 | 2567460.3744 | 1190590.0483 | 2567446.3509 | 1190603.3805 | 2567437.1751 | 1190613.3951
31 | 2567435.4227 | 1190615.3078 | 2567437.1751 | 1190613.3951
32 | 2567405.8355 | 1190623.4346 | 2567394.0082 | 1190638.5422
33 | 2567375.8289 | 1190661.9082 | 2567384.4297 | 1190650.7774 | 2567394.0082 | 1190638.5422
34 | 2567375.8289 | 1190661.9082 | 2567362.3836 | 1190699.0016

## bus_geodata
| x | y | coords
0 | 2567551.2778 | 1190721.5436
1 | 2567551.4664 | 1190721.2735
2 | 2567539.3774 | 1190738.5798
3 | 2567529.2902 | 1190730.2191
4 | 2567519.5306 | 1190721.8121
5 | 2567519.165 | 1190744.3841
6 | 2567494.58 | 1190700.3142
7 | 2567530.3967 | 1190703.4214
8 | 2567505.2814 | 1190763.8112
9 | 2567529.9956 | 1190700.9627
10 | 2567498.0755 | 1190672.9693
11 | 2567498.2518 | 1190672.7775
12 | 2567483.185 | 1190689.8595
13 | 2567481.0715 | 1190716.4858
14 | 2567511.179 | 1190658.7037
15 | 2567467.2047 | 1190675.2234
16 | 2567520.4082 | 1190777.0109
17 | 2567517.1795 | 1190774.849
18 | 2567460.1626 | 1190669.2326
19 | 2567451.2514 | 1190661.6518
20 | 2567448.7333 | 1190659.5093
21 | 2567440.5306 | 1190675.1328
22 | 2567426.1562 | 1190640.2999
23 | 2567435.4016 | 1190681.5823
24 | 2567478.9069 | 1190719.105
25 | 2567458.356 | 1190743.9721
26 | 2567456.7322 | 1190745.937
27 | 2567427.8118 | 1190780.9315
28 | 2567418.4958 | 1190633.7822
29 | 2567460.3744 | 1190590.0483
30 | 2567437.1751 | 1190613.3951
31 | 2567435.4227 | 1190615.3078
32 | 2567405.8355 | 1190623.4346
33 | 2567394.0082 | 1190638.5422
34 | 2567375.8289 | 1190661.9082
35 | 2567362.3836 | 1190699.0016
36 | 2567494.58 | 1190700.3142

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99222 | -0.05444 | 0.008546 | 0.0021418
1 | 0.99222 | -0.054463 | 0.0068681 | 0.0017213
2 | 0.99268 | -0.051194 | 0 | 0
3 | 0.99297 | -0.049152 | 0 | 0
4 | 0.99404 | -0.041659 | 0 | 0
5 | 0.99191 | -0.056598 | 0.014551 | 0.0036469
6 | 0.99756 | -0.016968 | 0 | 0
7 | 0.99348 | -0.045573 | 0.012911 | 0.0032358
8 | 0.99096 | -0.063302 | 0.0023177 | 0.00058087
9 | 0.99347 | -0.045675 | 0.0040634 | 0.0010184
10 | 0.99485 | -0.035968 | 0 | 0
11 | 0.99484 | -0.036033 | 0.0046719 | 0.0011709
12 | 0.99564 | -0.030371 | 0 | 0
13 | 1 | 0 | -0.18206 | -0.045603
14 | 0.99429 | -0.039894 | 0.020025 | 0.0050186
15 | 0.99372 | -0.043852 | 0.0035722 | 0.00089529
16 | 0.99022 | -0.068564 | 0.011529 | 0.0028895
17 | 0.99028 | -0.068108 | 0.0138 | 0.0034586
18 | 0.99295 | -0.049285 | 0.0032744 | 0.00082065
19 | 0.99202 | -0.055784 | 0 | 0
20 | 0.99182 | -0.057193 | 0.0032801 | 0.00082208
21 | 0.99171 | -0.05802 | 0.0018866 | 0.00047283
22 | 0.99017 | -0.068864 | 0.0051797 | 0.0012981
23 | 0.99158 | -0.058932 | 0.01091 | 0.0027342
24 | 0.99991 | -0.00064345 | 0.0076801 | 0.0019248
25 | 0.99939 | -0.0042813 | 0.00089483 | 0.00022427
26 | 0.99935 | -0.0045461 | 0.0019333 | 0.00048454
27 | 0.9988 | -0.0083857 | 0.0084565 | 0.0021194
28 | 0.98968 | -0.072302 | 0 | 0
29 | 0.98891 | -0.077732 | 0.0033953 | 0.00085094
30 | 0.98908 | -0.076591 | 0.00752 | 0.0018847
31 | 0.98912 | -0.076302 | 0.0047396 | 0.0011879
32 | 0.98926 | -0.07528 | 0 | 0
33 | 0.98876 | -0.078783 | 0.0013312 | 0.00033362
34 | 0.98806 | -0.083793 | 0.00092054 | 0.00023071
35 | 0.98717 | -0.090106 | 0.015637 | 0.003919
36 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0068681 | 0.0017213 | -0.0068681 | -0.0017213 | 2.1809e-08 | 4.133e-09 | 0.0103 | 0.0103 | 0.0103 | 0.99222 | -0.05444 | 0.99222 | -0.054463 | 3.8148
1 | -0.015414 | -0.0038631 | 0.015421 | 0.0038655 | 6.9293e-06 | 2.3966e-06 | 0.023116 | 0.023116 | 0.023116 | 0.99222 | -0.05444 | 0.99268 | -0.051194 | 8.5616
2 | -0.015421 | -0.0038655 | 0.015425 | 0.0038671 | 4.3617e-06 | 1.5084e-06 | 0.023116 | 0.023116 | 0.023116 | 0.99268 | -0.051194 | 0.99297 | -0.049152 | 8.5616
3 | -0.05771 | -0.014475 | 0.05777 | 0.014498 | 6.0027e-05 | 2.2921e-05 | 0.086486 | 0.086486 | 0.086486 | 0.99297 | -0.049152 | 0.99404 | -0.041659 | 32.0318
4 | 0.042285 | 0.010608 | -0.042241 | -0.010592 | 4.3631e-05 | 1.6556e-05 | 0.06337 | 0.06337 | 0.06337 | 0.99297 | -0.049152 | 0.99191 | -0.056598 | 23.4703
5 | -0.074754 | -0.018756 | 0.075011 | 0.018854 | 0.00025698 | 9.8411e-05 | 0.11191 | 0.11191 | 0.11191 | 0.99404 | -0.041659 | 0.99756 | -0.016968 | 41.448
6 | 0.016983 | 0.0042574 | -0.016974 | -0.0042541 | 9.2018e-06 | 3.2436e-06 | 0.025424 | 0.025424 | 0.025424 | 0.99404 | -0.041659 | 0.99348 | -0.045573 | 9.4162
7 | 0.02769 | 0.006945 | -0.027664 | -0.0069354 | 2.5712e-05 | 9.5813e-06 | 0.041541 | 0.041541 | 0.041541 | 0.99191 | -0.056598 | 0.99096 | -0.063302 | 15.3856
8 | -0.1619 | -0.040699 | 0.16228 | 0.040846 | 0.00038356 | 0.00014697 | 0.24154 | 0.24154 | 0.24154 | 0.99756 | -0.016968 | 1 | 0 | 44.7296
9 | 0.086888 | 0.021845 | -0.086726 | -0.021783 | 0.00016192 | 6.2076e-05 | 0.12963 | 0.12963 | 0.12963 | 0.99756 | -0.016968 | 0.99564 | -0.030371 | 48.0113
10 | 0.0040635 | 0.0010184 | -0.0040634 | -0.0010184 | 5.7582e-08 | -1.0111e-08 | 0.0060862 | 0.0060862 | 0.0060862 | 0.99348 | -0.045573 | 0.99347 | -0.045675 | 2.2541
11 | 0.025347 | 0.0063545 | -0.02533 | -0.0063483 | 1.6866e-05 | 6.2467e-06 | 0.038061 | 0.038061 | 0.038061 | 0.99096 | -0.063302 | 0.99028 | -0.068108 | 14.0966
12 | 0.024707 | 0.0061935 | -0.024707 | -0.0061934 | 2.22e-07 | 8.2001e-08 | 0.036956 | 0.036956 | 0.036956 | 0.99485 | -0.035968 | 0.99484 | -0.036033 | 13.6873
13 | -0.024707 | -0.0061935 | 0.024727 | 0.0062006 | 1.9166e-05 | 7.0794e-06 | 0.036956 | 0.036956 | 0.036956 | 0.99485 | -0.035968 | 0.99564 | -0.030371 | 13.6873
14 | 0.020035 | 0.0050225 | -0.020025 | -0.0050186 | 1.0709e-05 | 3.8709e-06 | 0.029968 | 0.029968 | 0.029968 | 0.99484 | -0.036033 | 0.99429 | -0.039894 | 11.0992
15 | 0.061999 | 0.015582 | -0.061883 | -0.015538 | 0.00011614 | 4.4387e-05 | 0.092675 | 0.092675 | 0.092675 | 0.99564 | -0.030371 | 0.99372 | -0.043852 | 34.324
16 | 0.018977 | 0.0047566 | -0.018975 | -0.004756 | 1.6907e-06 | 6.0569e-07 | 0.028238 | 0.028238 | 0.028238 | 1 | 0 | 0.99991 | -0.00064345 | 10.4586
17 | 0.058311 | 0.014643 | -0.058267 | -0.014626 | 4.3995e-05 | 1.6802e-05 | 0.087326 | 0.087326 | 0.087326 | 0.99372 | -0.043852 | 0.99295 | -0.049285 | 32.3429
18 | -0.011529 | -0.0028895 | 0.01153 | 0.0028897 | 7.2777e-07 | 2.2992e-07 | 0.017325 | 0.017325 | 0.017325 | 0.99022 | -0.068564 | 0.99028 | -0.068108 | 6.4167
19 | 0.054992 | 0.013805 | -0.054943 | -0.013786 | 4.9591e-05 | 1.8922e-05 | 0.082419 | 0.082419 | 0.082419 | 0.99295 | -0.049285 | 0.99202 | -0.055784 | 30.5255
20 | 0.042141 | 0.010577 | -0.042133 | -0.010574 | 8.2446e-06 | 3.1283e-06 | 0.063217 | 0.063217 | 0.063217 | 0.99202 | -0.055784 | 0.99182 | -0.057193 | 23.4136
21 | 0.012801 | 0.0032087 | -0.012798 | -0.0032074 | 3.963e-06 | 1.3019e-06 | 0.019202 | 0.019202 | 0.019202 | 0.99202 | -0.055784 | 0.99171 | -0.05802 | 7.1119
22 | 0.038853 | 0.0097522 | -0.03879 | -0.0097284 | 6.2861e-05 | 2.3796e-05 | 0.058296 | 0.058296 | 0.058296 | 0.99182 | -0.057193 | 0.99017 | -0.068864 | 21.591
23 | 0.010911 | 0.0027346 | -0.01091 | -0.0027342 | 1.3782e-06 | 4.2375e-07 | 0.016371 | 0.016371 | 0.016371 | 0.99171 | -0.05802 | 0.99158 | -0.058932 | 6.0635
24 | 0.03361 | 0.0084303 | -0.033594 | -0.0084243 | 1.6013e-05 | 6.0297e-06 | 0.050512 | 0.050512 | 0.050512 | 0.99017 | -0.068864 | 0.98968 | -0.072302 | 18.7081
25 | 0.011295 | 0.0028312 | -0.01129 | -0.0028295 | 5.6878e-06 | 1.7647e-06 | 0.016809 | 0.016809 | 0.016809 | 0.99991 | -0.00064345 | 0.99939 | -0.0042813 | 6.2257
26 | 0.010395 | 0.0026052 | -0.010394 | -0.0026051 | 3.8101e-07 | 1.1314e-07 | 0.015477 | 0.015477 | 0.015477 | 0.99939 | -0.0042813 | 0.99935 | -0.0045461 | 5.7322
27 | 0.008461 | 0.0021205 | -0.0084565 | -0.0021194 | 4.4963e-06 | 1.1349e-06 | 0.012598 | 0.012599 | 0.012599 | 0.99935 | -0.0045461 | 0.9988 | -0.0083857 | 4.6661
28 | 0.01793 | 0.0044978 | -0.017922 | -0.0044952 | 7.4035e-06 | 2.6378e-06 | 0.02696 | 0.02696 | 0.02696 | 0.98968 | -0.072302 | 0.98926 | -0.07528 | 9.985
29 | 0.015665 | 0.0039264 | -0.015656 | -0.0039234 | 8.6731e-06 | 3.014e-06 | 0.023552 | 0.023552 | 0.023552 | 0.98968 | -0.072302 | 0.98912 | -0.076302 | 8.7231
30 | -0.0033953 | -0.00085094 | 0.0033958 | 0.00085072 | 5.3634e-07 | -2.163e-07 | 0.0051089 | 0.0051087 | 0.0051089 | 0.98891 | -0.077732 | 0.98908 | -0.076591 | 1.8922
31 | -0.010916 | -0.0027354 | 0.010916 | 0.0027355 | 4.3655e-07 | 1.3461e-07 | 0.016422 | 0.016422 | 0.016422 | 0.98908 | -0.076591 | 0.98912 | -0.076302 | 6.0823
32 | 0.017922 | 0.0044952 | -0.017914 | -0.0044921 | 8.7018e-06 | 3.1006e-06 | 0.02696 | 0.02696 | 0.02696 | 0.98926 | -0.07528 | 0.98876 | -0.078783 | 9.9851
33 | 0.016583 | 0.0041585 | -0.016571 | -0.0041544 | 1.1506e-05 | 4.0459e-06 | 0.024956 | 0.024957 | 0.024957 | 0.98876 | -0.078783 | 0.98806 | -0.083793 | 9.2431
34 | 0.015651 | 0.0039237 | -0.015637 | -0.003919 | 1.3678e-05 | 4.7558e-06 | 0.02357 | 0.02357 | 0.02357 | 0.98806 | -0.083793 | 0.98717 | -0.090106 | 8.7298

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18482 | 0.046294

## res_load
| p_mw | q_mvar
0 | 0.008546 | 0.0021418
1 | 0.0068681 | 0.0017213
2 | 0.014551 | 0.0036469
3 | 0.012911 | 0.0032358
4 | 0.0023177 | 0.00058087
5 | 0.0040634 | 0.0010184
6 | 0.0046719 | 0.0011709
7 | 0.0027594 | 0.00069157
8 | 0.020025 | 0.0050186
9 | 0.0035722 | 0.00089529
10 | 0.011529 | 0.0028895
11 | 0.0138 | 0.0034586
12 | 0.0032744 | 0.00082065
13 | 0.0032801 | 0.00082208
14 | 0.0018866 | 0.00047283
15 | 0.0051797 | 0.0012981
16 | 0.01091 | 0.0027342
17 | 0.0076801 | 0.0019248
18 | 0.00089483 | 0.00022427
19 | 0.0019333 | 0.00048454
20 | 0.0084565 | 0.0021194
21 | 0.0033953 | 0.00085094
22 | 0.00752 | 0.0018847
23 | 0.0047396 | 0.0011879
24 | 0.0013312 | 0.00033362
25 | 0.00092054 | 0.00023071
26 | 0.015637 | 0.003919

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1