## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2053-25_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2053-25_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2053-25_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2053-25_0_4_node_79 | 0.4 | n |  | TRUE
4 | bus_LV_2053-25_0_4_node_63 | 0.4 | n |  | TRUE
5 | bus_LV_2053-25_0_4_node_87 | 0.4 | n |  | TRUE
6 | bus_LV_2053-25_0_4_node_84 | 0.4 | n |  | TRUE
7 | bus_LV_2053-25_0_4_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_2053-25_0_4_node_62 | 0.4 | n |  | TRUE
9 | bus_LV_2053-25_0_4_node_59 | 0.4 | n |  | TRUE
10 | bus_LV_2053-25_0_4_node_60 | 0.4 | n |  | TRUE
11 | bus_LV_2053-25_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_2053-25_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2053-25_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2053-25_0_4_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_2053-25_0_4_node_36 | 0.4 | n |  | TRUE
16 | bus_LV_2053-25_0_4_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_2053-25_0_4_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_2053-25_0_4_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_2053-25_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_2053-25_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_2053-25_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2053-25_0_4_node_131 | 0.4 | n |  | TRUE
23 | bus_LV_2053-25_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2053-25_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2053-25_0_4_node_132 | 0.4 | n |  | TRUE
26 | bus_LV_2053-25_0_4_node_44 | 0.4 | n |  | TRUE
27 | bus_LV_2053-25_0_4_node_112 | 0.4 | n |  | TRUE
28 | bus_LV_2053-25_0_4_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_2053-25_0_4_node_108 | 0.4 | n |  | TRUE
30 | bus_LV_2053-25_0_4_node_43 | 0.4 | n |  | TRUE
31 | bus_LV_2053-25_0_4_node_113 | 0.4 | n |  | TRUE
32 | bus_LV_2053-25_0_4_node_15 | 0.4 | n |  | TRUE
33 | bus_LV_2053-25_0_4_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_2053-25_0_4_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_2053-25_0_4_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_2053-25_0_4_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_2053-25_0_4_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_2053-25_0_4_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_2053-25_0_4_node_96 | 0.4 | n |  | TRUE
40 | bus_LV_2053-25_0_4_node_93 | 0.4 | n |  | TRUE
41 | bus_LV_2053-25_0_4_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_2053-25_0_4_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_2053-25_0_4_node_99 | 0.4 | n |  | TRUE
44 | bus_LV_2053-25_0_4_node_97 | 0.4 | n |  | TRUE
45 | bus_LV_2053-25_0_4_node_94 | 0.4 | n |  | TRUE
46 | bus_LV_2053-25_0_4_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_2053-25_0_4_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_2053-25_0_4_node_23 | 0.4 | n |  | TRUE
49 | bus_LV_2053-25_0_4_node_24 | 0.4 | n |  | TRUE
50 | bus_LV_2053-25_0_4_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_2053-25_0_4_node_26 | 0.4 | n |  | TRUE
52 | bus_LV_2053-25_0_4_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_2053-25_0_4_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_2053-25_0_4_node_31 | 0.4 | n |  | TRUE
55 | bus_LV_2053-25_0_4_node_28 | 0.4 | n |  | TRUE
56 | bus_LV_2053-25_0_4_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_2053-25_0_4_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_2053-25_0_4_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_2053-25_0_4_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_2053-25_0_4_node_116 | 0.4 | n |  | TRUE
61 | bus_LV_2053-25_0_4_node_101 | 0.4 | n |  | TRUE
62 | bus_LV_2053-25_0_4_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_2053-25_0_4_node_102 | 0.4 | n |  | TRUE
64 | bus_LV_2053-25_0_4_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_2053-25_0_4_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_2053-25_0_4_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_2053-25_0_4_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_2053-25_0_4_node_50 | 0.4 | n |  | TRUE
69 | bus_LV_2053-25_0_4_node_51 | 0.4 | n |  | TRUE
70 | bus_LV_2053-25_0_4_node_67 | 0.4 | n |  | TRUE
71 | bus_LV_2053-25_0_4_node_138 | 0.4 | n |  | TRUE
72 | bus_LV_2053-25_0_4_node_134 | 0.4 | n |  | TRUE
73 | bus_LV_2053-25_0_4_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_2053-25_0_4_node_135 | 0.4 | n |  | TRUE
75 | bus_LV_2053-25_0_4_node_136 | 0.4 | n |  | TRUE
76 | bus_LV_2053-25_0_4_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_2053-25_0_4_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_2053-25_0_4_node_53 | 0.4 | n |  | TRUE
79 | bus_LV_2053-25_0_4_node_54 | 0.4 | n |  | TRUE
80 | bus_LV_2053-25_0_4_node_55 | 0.4 | n |  | TRUE
81 | bus_LV_2053-25_0_4_node_57 | 0.4 | n |  | TRUE
82 | bus_LV_2053-25_0_4_node_58 | 0.4 | n |  | TRUE
83 | bus_LV_2053-25_0_4_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_2053-25_0_4_node_72 | 0.4 | n |  | TRUE
85 | bus_LV_2053-25_0_4_node_78 | 0.4 | n |  | TRUE
86 | bus_LV_2053-25_0_4_node_73 | 0.4 | n |  | TRUE
87 | bus_LV_2053-25_0_4_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_2053-25_0_4_node_64 | 0.4 | n |  | TRUE
89 | bus_LV_2053-25_0_4_node_65 | 0.4 | n |  | TRUE
90 | bus_LV_2053-25_0_4_node_66 | 0.4 | n |  | TRUE
91 | bus_LV_2053-25_0_4_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_2053-25_0_4_node_115 | 0.4 | n |  | TRUE
93 | bus_LV_2053-25_0_4_node_114 | 0.4 | n |  | TRUE
94 | bus_LV_2053-25_0_4_node_69 | 0.4 | n |  | TRUE
95 | bus_LV_2053-25_0_4_node_70 | 0.4 | n |  | TRUE
96 | bus_LV_2053-25_0_4_node_80 | 0.4 | n |  | TRUE
97 | bus_LV_2053-25_0_4_node_83 | 0.4 | n |  | TRUE
98 | bus_LV_2053-25_0_4_node_75 | 0.4 | n |  | TRUE
99 | bus_LV_2053-25_0_4_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_2053-25_0_4_node_76 | 0.4 | n |  | TRUE
101 | bus_LV_2053-25_0_4_node_77 | 0.4 | n |  | TRUE
102 | bus_LV_2053-25_0_4_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_2053-25_0_4_node_86 | 0.4 | n |  | TRUE
104 | bus_LV_2053-25_0_4_node_139 | 0.4 | n |  | TRUE
105 | bus_LV_2053-25_0_4_node_88 | 0.4 | n |  | TRUE
106 | bus_LV_2053-25_0_4_node_89 | 0.4 | n |  | TRUE
107 | bus_LV_2053-25_0_4_node_90 | 0.4 | n |  | TRUE
108 | bus_LV_2053-25_0_4_node_91 | 0.4 | n |  | TRUE
109 | bus_LV_2053-25_0_4_node_92 | 0.4 | n |  | TRUE
110 | bus_LV_2053-25_0_4_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_2053-25_0_4_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_2053-25_0_4_node_95 | 0.4 | n |  | TRUE
113 | bus_LV_2053-25_0_4_node_109 | 0.4 | n |  | TRUE
114 | bus_LV_2053-25_0_4_node_125 | 0.4 | n |  | TRUE
115 | bus_LV_2053-25_0_4_node_98 | 0.4 | n |  | TRUE
116 | bus_LV_2053-25_0_4_node_100 | 0.4 | n |  | TRUE
117 | bus_LV_2053-25_0_4_node_103 | 0.4 | n |  | TRUE
118 | bus_LV_2053-25_0_4_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_2053-25_0_4_node_106 | 0.4 | n |  | TRUE
120 | bus_LV_2053-25_0_4_node_110 | 0.4 | n |  | TRUE
121 | bus_LV_2053-25_0_4_node_137 | 0.4 | n |  | TRUE
122 | bus_LV_2053-25_0_4_node_111 | 0.4 | n |  | TRUE
123 | bus_LV_2053-25_0_4_node_126 | 0.4 | n |  | TRUE
124 | bus_LV_2053-25_0_4_node_127 | 0.4 | n |  | TRUE
125 | bus_LV_2053-25_0_4_node_128 | 0.4 | n |  | TRUE
126 | bus_LV_2053-25_0_4_node_129 | 0.4 | n |  | TRUE
127 | bus_LV_2053-25_0_4_node_130 | 0.4 | n |  | TRUE
128 | bus_LV_2053-25_0_4_node_124 | 0.4 | n |  | TRUE
129 | bus_LV_2053-25_0_4_node_117 | 0.4 | n |  | TRUE
130 | bus_LV_2053-25_0_4_node_118 | 0.4 | n |  | TRUE
131 | bus_LV_2053-25_0_4_node_119 | 0.4 | n |  | TRUE
132 | bus_LV_2053-25_0_4_node_120 | 0.4 | n |  | TRUE
133 | bus_LV_2053-25_0_4_node_133 | 0.4 | n |  | TRUE
134 | bus_LV_2053-25_0_4_node_121 | 0.4 | n |  | TRUE
135 | bus_LV_2053-25_0_4_node_122 | 0.4 | n |  | TRUE
136 | bus_LV_2053-25_0_4_node_123 | 0.4 | n |  | TRUE
137 | bus_MV_377_1_node_80 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2053-25_0_4_load_0 | 0 | 0.005632 | 0.0014115 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2053-25_0_4_load_63 | 4 | 0.0030038 | 0.00075283 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2053-25_0_4_load_87 | 5 | 0.0026702 | 0.0006692 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2053-25_0_4_load_84 | 6 | 0.0028379 | 0.00071125 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2053-25_0_4_load_62 | 8 | 0.00086974 | 0.00021798 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2053-25_0_4_load_59 | 9 | 0.00063141 | 0.00015825 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2053-25_0_4_load_5 | 11 | 0.00059547 | 0.00014924 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2053-25_0_4_load_35 | 14 | 0.00083682 | 0.00020973 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2053-25_0_4_load_36 | 15 | 0.00029818 | 7.473e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2053-25_0_4_load_33 | 16 | 0.00074989 | 0.00018794 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2053-25_0_4_load_32 | 17 | 0.0017096 | 0.00042848 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2053-25_0_4_load_8 | 18 | 0.00025088 | 6.2876e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2053-25_0_4_load_131 | 22 | 0.0017492 | 0.00043838 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2053-25_0_4_load_12 | 24 | 0.0011015 | 0.00027607 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2053-25_0_4_load_132 | 25 | 0.0035164 | 0.0008813 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2053-25_0_4_load_112 | 27 | 0.0029538 | 0.0007403 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2053-25_0_4_load_13 | 28 | 0.00031734 | 7.9532e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2053-25_0_4_load_108 | 29 | 0.0031453 | 0.00078828 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2053-25_0_4_load_113 | 31 | 0.0068558 | 0.0017182 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2053-25_0_4_load_15 | 32 | 0.0016838 | 0.00042199 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2053-25_0_4_load_18 | 35 | 0.0039304 | 0.00098505 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2053-25_0_4_load_21 | 37 | 0.00084178 | 0.00021097 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2053-25_0_4_load_22 | 38 | 0.0037677 | 0.00094426 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2053-25_0_4_load_96 | 39 | 0.0028905 | 0.00072443 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2053-25_0_4_load_93 | 40 | 0.0022857 | 0.00057285 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2053-25_0_4_load_34 | 41 | 0.0017174 | 0.00043041 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2053-25_0_4_load_99 | 43 | 0.0083779 | 0.0020997 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2053-25_0_4_load_97 | 44 | 0.0026393 | 0.00066148 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2053-25_0_4_load_94 | 45 | 0.0016776 | 0.00042045 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2053-25_0_4_load_39 | 47 | 0.0070925 | 0.0017775 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2053-25_0_4_load_23 | 48 | 0.00064211 | 0.00016093 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2053-25_0_4_load_24 | 49 | 0.0011418 | 0.00028616 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2053-25_0_4_load_25 | 50 | 0.0021038 | 0.00052727 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2053-25_0_4_load_27 | 52 | 0.0011739 | 0.00029421 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2053-25_0_4_load_31 | 54 | 0.00047935 | 0.00012014 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2053-25_0_4_load_28 | 55 | 0.00082654 | 0.00020715 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2053-25_0_4_load_40 | 57 | 0.00065918 | 0.00016521 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2053-25_0_4_load_41 | 58 | 0.00044213 | 0.00011081 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2053-25_0_4_load_116 | 60 | 0.0028287 | 0.00070894 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2053-25_0_4_load_101 | 61 | 0.0031862 | 0.00079854 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2053-25_0_4_load_42 | 62 | 0.0045516 | 0.0011407 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2053-25_0_4_load_102 | 63 | 0.0012269 | 0.00030749 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2053-25_0_4_load_46 | 64 | 0.0010344 | 0.00025924 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2053-25_0_4_load_47 | 65 | 0.00035091 | 8.7946e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2053-25_0_4_load_50 | 68 | 0.0003438 | 8.6165e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2053-25_0_4_load_67 | 70 | 0.00036317 | 9.1019e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2053-25_0_4_load_138 | 71 | 0.0031923 | 0.00080007 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2053-25_0_4_load_135 | 74 | 0.00311 | 0.00077943 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2053-25_0_4_load_136 | 75 | 0.0025454 | 0.00063794 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2053-25_0_4_load_56 | 76 | 0.0021806 | 0.00054652 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2053-25_0_4_load_52 | 77 | 0.0034754 | 0.00087102 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2053-25_0_4_load_55 | 80 | 0.0034052 | 0.00085343 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2053-25_0_4_load_57 | 81 | 0.00098084 | 0.00024582 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2053-25_0_4_load_58 | 82 | 0.008792 | 0.0022035 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2053-25_0_4_load_78 | 85 | 0.0030646 | 0.00076806 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2053-25_0_4_load_73 | 86 | 0.00052007 | 0.00013034 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2053-25_0_4_load_74 | 87 | 0.00072104 | 0.00018071 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2053-25_0_4_load_65 | 89 | 0.0023399 | 0.00058643 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2053-25_0_4_load_71 | 91 | 0.0041401 | 0.0010376 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2053-25_0_4_load_115 | 92 | 0.0034231 | 0.00085791 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2053-25_0_4_load_114 | 93 | 0.0020182 | 0.0005058 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2053-25_0_4_load_69 | 94 | 0.0020694 | 0.00051864 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2053-25_0_4_load_70 | 95 | 0.0025514 | 0.00063944 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2053-25_0_4_load_80 | 96 | 0.0024639 | 0.0006175 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2053-25_0_4_load_83 | 97 | 0.0031544 | 0.00079056 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2053-25_0_4_load_75 | 98 | 0.00039876 | 9.9939e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2053-25_0_4_load_82 | 99 | 0.0040626 | 0.0010182 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2053-25_0_4_load_76 | 100 | 0.001652 | 0.00041404 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2053-25_0_4_load_139 | 104 | 0.00080542 | 0.00020186 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2053-25_0_4_load_88 | 105 | 0.0031414 | 0.00078731 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2053-25_0_4_load_89 | 106 | 0.0030869 | 0.00077365 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2053-25_0_4_load_90 | 107 | 0.0020303 | 0.00050885 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2053-25_0_4_load_91 | 108 | 0.0027067 | 0.00067837 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2053-25_0_4_load_92 | 109 | 0.0025436 | 0.00063748 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2053-25_0_4_load_107 | 110 | 0.0042645 | 0.0010688 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2053-25_0_4_load_105 | 111 | 0.0027867 | 0.00069841 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2053-25_0_4_load_95 | 112 | 0.0016765 | 0.00042016 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2053-25_0_4_load_109 | 113 | 0.0024506 | 0.00061419 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2053-25_0_4_load_125 | 114 | 0.0022456 | 0.00056281 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2053-25_0_4_load_98 | 115 | 0.0018482 | 0.00046319 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2053-25_0_4_load_100 | 116 | 0.002601 | 0.00065187 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2053-25_0_4_load_103 | 117 | 0.0044729 | 0.001121 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2053-25_0_4_load_104 | 118 | 0.0036995 | 0.00092719 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2053-25_0_4_load_106 | 119 | 0.0032397 | 0.00081195 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2053-25_0_4_load_110 | 120 | 0.0031711 | 0.00079475 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2053-25_0_4_load_137 | 121 | 0.0034235 | 0.000858 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2053-25_0_4_load_111 | 122 | 0.0021114 | 0.00052917 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2053-25_0_4_load_126 | 123 | 0.0019295 | 0.00048358 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2053-25_0_4_load_127 | 124 | 0.0018741 | 0.00046969 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2053-25_0_4_load_128 | 125 | 0.0019871 | 0.00049802 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2053-25_0_4_load_124 | 128 | 0.0016261 | 0.00040754 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2053-25_0_4_load_117 | 129 | 0.0042848 | 0.0010739 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2053-25_0_4_load_118 | 130 | 0.0021082 | 0.00052837 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2053-25_0_4_load_119 | 131 | 0.0027505 | 0.00068934 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2053-25_0_4_load_120 | 132 | 0.0021264 | 0.00053292 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2053-25_0_4_load_133 | 133 | 0.0030782 | 0.00077146 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2053-25_0_4_load_121 | 134 | 0.0015946 | 0.00039966 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2053-25_0_4_load_122 | 135 | 0.0015824 | 0.00039658 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2053-25_0_4_load_123 | 136 | 0.0010209 | 0.00025586 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2053-25_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.060122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2053-25_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.031282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2053-25_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.058885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_2053-25_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.021459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_2053-25_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.013712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2053-25_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0056691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2053-25_0_4_line_6 | NAYY 4x150 SE | 3 | 7 | 0.046694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_2053-25_0_4_line_7 | NAYY 4x150 SE | 4 | 8 | 0.047712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_2053-25_0_4_line_8 | NAYY 4x150 SE | 6 | 102 | 0.00088953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2053-25_0_4_line_9 | NAYY 4x150 SE | 7 | 40 | 0.019899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2053-25_0_4_line_10 | NAYY 4x150 SE | 7 | 33 | 0.028481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_2053-25_0_4_line_11 | NAYY 4x150 SE | 8 | 88 | 0.017512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2053-25_0_4_line_12 | NAYY 4x150 SE | 9 | 10 | 0.0042923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2053-25_0_4_line_13 | NAYY 4x150 SE | 10 | 67 | 0.027841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2053-25_0_4_line_14 | NAYY 4x150 SE | 11 | 12 | 0.017929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2053-25_0_4_line_15 | NAYY 4x150 SE | 12 | 13 | 0.026597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2053-25_0_4_line_16 | NAYY 4x150 SE | 13 | 14 | 0.03685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2053-25_0_4_line_17 | NAYY 4x150 SE | 13 | 15 | 0.019534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2053-25_0_4_line_18 | NAYY 4x150 SE | 14 | 16 | 0.030642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2053-25_0_4_line_19 | NAYY 4x150 SE | 15 | 17 | 0.02804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2053-25_0_4_line_20 | NAYY 4x150 SE | 16 | 51 | 0.023742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2053-25_0_4_line_21 | NAYY 4x150 SE | 17 | 56 | 0.043563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2053-25_0_4_line_22 | NAYY 4x150 SE | 18 | 19 | 0.017604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2053-25_0_4_line_23 | NAYY 4x150 SE | 19 | 20 | 0.037145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2053-25_0_4_line_24 | NAYY 4x150 SE | 19 | 21 | 0.025908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_2053-25_0_4_line_25 | NAYY 4x150 SE | 20 | 22 | 0.022631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2053-25_0_4_line_26 | NAYY 4x150 SE | 21 | 23 | 0.007142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_2053-25_0_4_line_27 | NAYY 4x150 SE | 21 | 24 | 0.024275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2053-25_0_4_line_28 | NAYY 4x150 SE | 22 | 25 | 0.0028455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2053-25_0_4_line_29 | NAYY 4x150 SE | 23 | 26 | 0.006819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_2053-25_0_4_line_30 | NAYY 4x150 SE | 23 | 27 | 0.019138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2053-25_0_4_line_31 | NAYY 4x150 SE | 24 | 28 | 0.010613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2053-25_0_4_line_32 | NAYY 4x150 SE | 25 | 133 | 0.021496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2053-25_0_4_line_33 | NAYY 4x150 SE | 26 | 29 | 0.019713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2053-25_0_4_line_34 | NAYY 4x150 SE | 26 | 30 | 0.01258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_2053-25_0_4_line_35 | NAYY 4x150 SE | 27 | 31 | 0.038146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2053-25_0_4_line_36 | NAYY 4x150 SE | 30 | 59 | 0.011685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_2053-25_0_4_line_37 | NAYY 4x150 SE | 30 | 62 | 0.018574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2053-25_0_4_line_38 | NAYY 4x150 SE | 32 | 33 | 0.017823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_2053-25_0_4_line_39 | NAYY 4x150 SE | 32 | 34 | 0.011259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_2053-25_0_4_line_40 | NAYY 4x150 SE | 33 | 35 | 0.021344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_2053-25_0_4_line_41 | NAYY 4x150 SE | 33 | 36 | 0.025413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2053-25_0_4_line_42 | NAYY 4x150 SE | 34 | 37 | 0.00499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_2053-25_0_4_line_43 | NAYY 4x150 SE | 34 | 38 | 0.019859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2053-25_0_4_line_44 | NAYY 4x150 SE | 35 | 39 | 0.034415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_2053-25_0_4_line_45 | NAYY 4x150 SE | 36 | 41 | 0.0069934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2053-25_0_4_line_46 | NAYY 4x150 SE | 37 | 42 | 0.020829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_2053-25_0_4_line_47 | NAYY 4x150 SE | 38 | 43 | 0.0026125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2053-25_0_4_line_48 | NAYY 4x150 SE | 39 | 44 | 0.03454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2053-25_0_4_line_49 | NAYY 4x150 SE | 40 | 45 | 0.025521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2053-25_0_4_line_50 | NAYY 4x150 SE | 42 | 46 | 0.013011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_2053-25_0_4_line_51 | NAYY 4x150 SE | 42 | 47 | 0.018588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2053-25_0_4_line_52 | NAYY 4x150 SE | 44 | 115 | 0.015264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2053-25_0_4_line_53 | NAYY 4x150 SE | 45 | 112 | 0.0013214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2053-25_0_4_line_54 | NAYY 4x150 SE | 46 | 59 | 0.020476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_2053-25_0_4_line_55 | NAYY 4x150 SE | 46 | 60 | 0.023167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2053-25_0_4_line_56 | NAYY 4x150 SE | 48 | 49 | 0.014132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2053-25_0_4_line_57 | NAYY 4x150 SE | 48 | 50 | 0.015838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2053-25_0_4_line_58 | NAYY 4x150 SE | 49 | 51 | 0.012435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2053-25_0_4_line_59 | NAYY 4x150 SE | 50 | 52 | 0.0062452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2053-25_0_4_line_60 | NAYY 4x150 SE | 53 | 54 | 0.019835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2053-25_0_4_line_61 | NAYY 4x150 SE | 53 | 55 | 0.028595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2053-25_0_4_line_62 | NAYY 4x150 SE | 54 | 57 | 0.004858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2053-25_0_4_line_63 | NAYY 4x150 SE | 55 | 56 | 0.047136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2053-25_0_4_line_64 | NAYY 4x150 SE | 57 | 58 | 0.017099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2053-25_0_4_line_65 | NAYY 4x150 SE | 58 | 62 | 0.018559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2053-25_0_4_line_66 | NAYY 4x150 SE | 59 | 61 | 0.023564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2053-25_0_4_line_67 | NAYY 4x150 SE | 61 | 63 | 0.021133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2053-25_0_4_line_68 | NAYY 4x150 SE | 64 | 65 | 0.0080744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2053-25_0_4_line_69 | NAYY 4x150 SE | 64 | 66 | 0.0054199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2053-25_0_4_line_70 | NAYY 4x150 SE | 65 | 67 | 0.027395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2053-25_0_4_line_71 | NAYY 4x150 SE | 66 | 68 | 0.028404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2053-25_0_4_line_72 | NAYY 4x150 SE | 66 | 69 | 0.03431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2053-25_0_4_line_73 | NAYY 4x150 SE | 68 | 70 | 0.02653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2053-25_0_4_line_74 | NAYY 4x150 SE | 69 | 71 | 0.008331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2053-25_0_4_line_75 | NAYY 4x150 SE | 69 | 72 | 0.016204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2053-25_0_4_line_76 | NAYY 4x150 SE | 70 | 73 | 0.015012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2053-25_0_4_line_77 | NAYY 4x150 SE | 72 | 74 | 0.013893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2053-25_0_4_line_78 | NAYY 4x150 SE | 72 | 75 | 0.010206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2053-25_0_4_line_79 | NAYY 4x150 SE | 72 | 76 | 0.027151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2053-25_0_4_line_80 | NAYY 4x150 SE | 73 | 94 | 0.014843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2053-25_0_4_line_81 | NAYY 4x150 SE | 73 | 95 | 0.015621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2053-25_0_4_line_82 | NAYY 4x150 SE | 76 | 78 | 0.046393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2053-25_0_4_line_83 | NAYY 4x150 SE | 77 | 78 | 0.022533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2053-25_0_4_line_84 | NAYY 4x150 SE | 77 | 79 | 0.0012397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2053-25_0_4_line_85 | NAYY 4x150 SE | 78 | 80 | 0.026644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2053-25_0_4_line_86 | NAYY 4x150 SE | 79 | 81 | 0.035941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2053-25_0_4_line_87 | NAYY 4x150 SE | 79 | 82 | 0.021179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2053-25_0_4_line_88 | NAYY 4x150 SE | 81 | 83 | 0.0090887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2053-25_0_4_line_89 | NAYY 4x150 SE | 83 | 84 | 0.011368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2053-25_0_4_line_90 | NAYY 4x150 SE | 83 | 85 | 0.020472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2053-25_0_4_line_91 | NAYY 4x150 SE | 84 | 99 | 0.015502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2053-25_0_4_line_92 | NAYY 4x150 SE | 84 | 91 | 0.0097749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2053-25_0_4_line_93 | NAYY 4x150 SE | 85 | 101 | 0.024147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2053-25_0_4_line_94 | NAYY 4x150 SE | 86 | 87 | 0.0003778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2053-25_0_4_line_95 | NAYY 4x150 SE | 87 | 98 | 0.012257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2053-25_0_4_line_96 | NAYY 4x150 SE | 88 | 89 | 0.0037512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2053-25_0_4_line_97 | NAYY 4x150 SE | 88 | 90 | 0.011782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2053-25_0_4_line_98 | NAYY 4x150 SE | 89 | 91 | 0.026153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2053-25_0_4_line_99 | NAYY 4x150 SE | 90 | 92 | 0.01247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2053-25_0_4_line_100 | NAYY 4x150 SE | 90 | 93 | 0.013699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2053-25_0_4_line_101 | NAYY 4x150 SE | 94 | 96 | 0.015423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2053-25_0_4_line_102 | NAYY 4x150 SE | 95 | 97 | 0.001466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2053-25_0_4_line_103 | NAYY 4x150 SE | 96 | 98 | 0.020881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2053-25_0_4_line_104 | NAYY 4x150 SE | 100 | 101 | 0.023115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2053-25_0_4_line_105 | NAYY 4x150 SE | 102 | 103 | 0.004778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2053-25_0_4_line_106 | NAYY 4x150 SE | 103 | 104 | 0.002548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2053-25_0_4_line_107 | NAYY 4x150 SE | 105 | 106 | 0.0047142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2053-25_0_4_line_108 | NAYY 4x150 SE | 105 | 107 | 0.018065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2053-25_0_4_line_109 | NAYY 4x150 SE | 106 | 108 | 0.016731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2053-25_0_4_line_110 | NAYY 4x150 SE | 107 | 109 | 0.0026612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2053-25_0_4_line_111 | NAYY 4x150 SE | 108 | 110 | 0.02237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2053-25_0_4_line_112 | NAYY 4x150 SE | 110 | 111 | 0.0018707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2053-25_0_4_line_113 | NAYY 4x150 SE | 111 | 117 | 0.022675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2053-25_0_4_line_114 | NAYY 4x150 SE | 112 | 113 | 0.031829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2053-25_0_4_line_115 | NAYY 4x150 SE | 113 | 114 | 0.0029699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2053-25_0_4_line_116 | NAYY 4x150 SE | 114 | 128 | 0.034748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2053-25_0_4_line_117 | NAYY 4x150 SE | 115 | 116 | 0.0031196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2053-25_0_4_line_118 | NAYY 4x150 SE | 117 | 118 | 0.025129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2053-25_0_4_line_119 | NAYY 4x150 SE | 118 | 119 | 0.015447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2053-25_0_4_line_120 | NAYY 4x150 SE | 119 | 120 | 0.0096395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2053-25_0_4_line_121 | NAYY 4x150 SE | 119 | 121 | 0.05566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2053-25_0_4_line_122 | NAYY 4x150 SE | 120 | 122 | 0.0068173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2053-25_0_4_line_123 | NAYY 4x150 SE | 121 | 127 | 0.010658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2053-25_0_4_line_124 | NAYY 4x150 SE | 122 | 129 | 0.013618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_2053-25_0_4_line_125 | NAYY 4x150 SE | 123 | 124 | 0.014816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_2053-25_0_4_line_126 | NAYY 4x150 SE | 123 | 125 | 0.02969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_2053-25_0_4_line_127 | NAYY 4x150 SE | 124 | 126 | 0.05709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_2053-25_0_4_line_128 | NAYY 4x150 SE | 126 | 127 | 0.028817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_2053-25_0_4_line_129 | NAYY 4x150 SE | 128 | 135 | 0.019114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_2053-25_0_4_line_130 | NAYY 4x150 SE | 129 | 130 | 0.010911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_2053-25_0_4_line_131 | NAYY 4x150 SE | 130 | 131 | 0.019057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_2053-25_0_4_line_132 | NAYY 4x150 SE | 131 | 132 | 0.0019884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_2053-25_0_4_line_133 | NAYY 4x150 SE | 132 | 133 | 0.00056885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_2053-25_0_4_line_134 | NAYY 4x150 SE | 134 | 135 | 0.00086968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_2053-25_0_4_line_135 | NAYY 4x150 SE | 134 | 136 | 0.0048506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2053-25_0_4_trafo_96 | 0.25 MVA 20/0.4 kV | 137 | 39 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2567289.04 | 1191214.4473 | 2567280.2155 | 1191230.4932 | 2567282.4323 | 1191234.3387 | 2567259.3874 | 1191263.759
1 | 2567289.04 | 1191214.4473 | 2567265.369 | 1191193.9216
2 | 2567265.369 | 1191193.9216 | 2567269.8798 | 1191187.8825 | 2567276.6792 | 1191179.3072 | 2567280.9287 | 1191174.2701 | 2567291.0226 | 1191161.6969 | 2567278.0794 | 1191149.6391
3 | 2567265.369 | 1191193.9216 | 2567251.653 | 1191177.4179
4 | 2567268.3431 | 1191159.32 | 2567272.3241 | 1191155.3627 | 2567278.0794 | 1191149.6391
5 | 2567278.0794 | 1191149.6391 | 2567273.9 | 1191145.8087
6 | 2567278.0794 | 1191149.6391 | 2567291.0226 | 1191161.6969 | 2567309.1736 | 1191139.0741
7 | 2567221.1572 | 1191140.7242 | 2567251.653 | 1191177.4179
8 | 2567273.9 | 1191145.8087 | 2567273.2442 | 1191145.2077
9 | 2567309.1736 | 1191139.0741 | 2567306.3545 | 1191136.6327 | 2567293.8921 | 1191126.3294
10 | 2567309.1736 | 1191139.0741 | 2567324.9588 | 1191118.7879 | 2567326.6392 | 1191116.5775
11 | 2567209.9644 | 1191127.2565 | 2567221.1572 | 1191140.7242
12 | 2567171.283 | 1191277.4723 | 2567175.1355 | 1191275.5797
13 | 2567144.1623 | 1191278.4444 | 2567146.8466 | 1191277.1845 | 2567149.7948 | 1191276.7791 | 2567152.7251 | 1191277.2632 | 2567155.3704 | 1191278.605 | 2567161.9457 | 1191277.8461 | 2567171.283 | 1191277.4723
14 | 2567471.9593 | 1191248.6547 | 2567459.9377 | 1191261.9567
15 | 2567451.995 | 1191231.0207 | 2567471.9593 | 1191248.6547
16 | 2567451.995 | 1191231.0207 | 2567424.3779 | 1191206.6232
17 | 2567451.995 | 1191231.0207 | 2567461.4416 | 1191213.9228
18 | 2567401.4137 | 1191186.3361 | 2567424.3779 | 1191206.6232
19 | 2567461.4416 | 1191213.9228 | 2567475.002 | 1191189.3792
20 | 2567383.6203 | 1191170.6171 | 2567401.4137 | 1191186.3361
21 | 2567496.0692 | 1191151.2486 | 2567475.002 | 1191189.3792
22 | 2567423.8054 | 1191015.3918 | 2567436.3409 | 1191027.7513
23 | 2567423.8054 | 1191015.3918 | 2567415.5342 | 1191007.2326 | 2567421.8958 | 1190999.4047 | 2567426.9102 | 1190993.3852 | 2567431.6736 | 1190987.456
24 | 2567406.7286 | 1191018.4867 | 2567415.5342 | 1191007.2326 | 2567423.8054 | 1191015.3918
25 | 2567431.6736 | 1190987.456 | 2567428.7275 | 1190985.4933 | 2567413.3359 | 1190974.1981
26 | 2567406.7286 | 1191018.4867 | 2567402.0234 | 1191023.8709
27 | 2567406.7286 | 1191018.4867 | 2567424.0267 | 1191035.5173
28 | 2567413.3359 | 1190974.1981 | 2567411.0419 | 1190972.5146
29 | 2567397.8826 | 1191029.2964 | 2567402.0234 | 1191023.8709
30 | 2567402.0234 | 1191023.8709 | 2567386.493 | 1191012.6871
31 | 2567431.5878 | 1191042.9642 | 2567426.0993 | 1191037.5579 | 2567424.0267 | 1191035.5173
32 | 2567393.7116 | 1190959.7967 | 2567411.0419 | 1190972.5146
33 | 2567397.8826 | 1191029.2964 | 2567381.0801 | 1191018.9867
34 | 2567397.8826 | 1191029.2964 | 2567389.7773 | 1191038.9348
35 | 2567355.5379 | 1190990.3959 | 2567386.493 | 1191012.6871
36 | 2567382.3473 | 1191047.9691 | 2567389.7773 | 1191038.9348
37 | 2567389.7773 | 1191038.9348 | 2567393.7076 | 1191042.4263 | 2567402.8456 | 1191052.1128
38 | 2567326.6392 | 1191116.5775 | 2567329.8243 | 1191113.4695 | 2567338.3151 | 1191103.1386
39 | 2567345.464 | 1191094.4403 | 2567338.3151 | 1191103.1386
40 | 2567326.6392 | 1191116.5775 | 2567309.4203 | 1191103.9656
41 | 2567326.6392 | 1191116.5775 | 2567324.9588 | 1191118.7879 | 2567329.3243 | 1191122.3993 | 2567335.5696 | 1191128.1682 | 2567341.9207 | 1191133.7698
42 | 2567345.464 | 1191094.4403 | 2567348.468 | 1191090.4558
43 | 2567345.464 | 1191094.4403 | 2567328.9632 | 1191083.3895
44 | 2567281.6558 | 1191083.6297 | 2567309.4203 | 1191103.9656
45 | 2567341.9207 | 1191133.7698 | 2567347.1612 | 1191138.4005
46 | 2567361.7694 | 1191074.4292 | 2567349.2259 | 1191089.4504 | 2567348.468 | 1191090.4558
47 | 2567326.7925 | 1191081.9358 | 2567328.9632 | 1191083.3895
48 | 2567281.6558 | 1191083.6297 | 2567253.7905 | 1191063.2199
49 | 2567293.8921 | 1191126.3294 | 2567274.2229 | 1191110.0677
50 | 2567361.7694 | 1191074.4292 | 2567369.7337 | 1191064.1246
51 | 2567376.3568 | 1191086.0001 | 2567361.7694 | 1191074.4292
52 | 2567253.7905 | 1191063.2199 | 2567241.476 | 1191054.2003
53 | 2567274.2229 | 1191110.0677 | 2567273.2045 | 1191109.2258
54 | 2567369.7337 | 1191064.1246 | 2567382.3473 | 1191047.9691
55 | 2567369.7337 | 1191064.1246 | 2567357.6795 | 1191055.7193 | 2567353.3479 | 1191062.4911 | 2567353.1146 | 1191062.8556
56 | 2567400.3769 | 1191150.0013 | 2567391.4633 | 1191160.9678
57 | 2567410.3662 | 1191137.7114 | 2567400.3769 | 1191150.0013
58 | 2567383.6203 | 1191170.6171 | 2567391.4633 | 1191160.9678
59 | 2567414.3053 | 1191132.8651 | 2567410.3662 | 1191137.7114
60 | 2567444.2592 | 1191096.0125 | 2567430.6483 | 1191081.5845
61 | 2567444.2592 | 1191096.0125 | 2567463.822 | 1191116.869
62 | 2567430.6483 | 1191081.5845 | 2567427.3147 | 1191078.0508
63 | 2567496.0692 | 1191151.2486 | 2567463.822 | 1191116.869
64 | 2567415.5813 | 1191065.613 | 2567427.3147 | 1191078.0508
65 | 2567415.5813 | 1191065.613 | 2567402.8456 | 1191052.1128
66 | 2567382.3473 | 1191047.9691 | 2567363.5502 | 1191033.7597
67 | 2567363.5502 | 1191033.7597 | 2567346.6919 | 1191021.0159
68 | 2567125.5516 | 1191248.2529 | 2567129.8797 | 1191255.0694
69 | 2567122.6464 | 1191243.6775 | 2567125.5516 | 1191248.2529
70 | 2567144.1623 | 1191278.4444 | 2567141.9309 | 1191274.7324 | 2567134.1825 | 1191261.8459 | 2567129.8797 | 1191255.0694
71 | 2567122.6464 | 1191243.6775 | 2567144.3203 | 1191225.3194
72 | 2567122.6464 | 1191243.6775 | 2567105.4886 | 1191213.9449
73 | 2567144.3203 | 1191225.3194 | 2567149.161 | 1191221.2193 | 2567152.6675 | 1191207.2814 | 2567156.9986 | 1191203.4031
74 | 2567110.9277 | 1191207.6226 | 2567105.4886 | 1191213.9449
75 | 2567097.383 | 1191199.9042 | 2567105.4886 | 1191213.9449
76 | 2567168.1822 | 1191193.3886 | 2567156.9986 | 1191203.4031
77 | 2567097.383 | 1191199.9042 | 2567085.4759 | 1191207.1182
78 | 2567097.383 | 1191199.9042 | 2567104.5015 | 1191192.5722
79 | 2567097.383 | 1191199.9042 | 2567091.1638 | 1191187.832 | 2567090.9555 | 1191184.6315 | 2567091.9829 | 1191180.1567 | 2567095.7856 | 1191175.8144
80 | 2567168.1822 | 1191193.3886 | 2567179.9574 | 1191184.3522
81 | 2567168.1822 | 1191193.3886 | 2567159.1543 | 1191180.64
82 | 2567126.3495 | 1191140.9128 | 2567095.7856 | 1191175.8144
83 | 2567126.3495 | 1191140.9128 | 2567141.1933 | 1191123.9607
84 | 2567142.01 | 1191123.028 | 2567141.1933 | 1191123.9607
85 | 2567126.3495 | 1191140.9128 | 2567142.275 | 1191162.273
86 | 2567142.01 | 1191123.028 | 2567159.9587 | 1191102.5293 | 2567163.6986 | 1191101.8639 | 2567167.0636 | 1191098.3075
87 | 2567156.8613 | 1191138.1656 | 2567142.01 | 1191123.028
88 | 2567173.3101 | 1191091.7056 | 2567167.0636 | 1191098.3075
89 | 2567181.4811 | 1191099.6316 | 2567173.3101 | 1191091.7056
90 | 2567173.3101 | 1191091.7056 | 2567158.3452 | 1191077.7355
91 | 2567181.4811 | 1191099.6316 | 2567183.8003 | 1191097.1286 | 2567187.8505 | 1191093.2931 | 2567189.3375 | 1191091.9509 | 2567186.2016 | 1191088.7113
92 | 2567181.4811 | 1191099.6316 | 2567188.4979 | 1191106.4369
93 | 2567140.6938 | 1191061.2576 | 2567158.3452 | 1191077.7355
94 | 2567206.3214 | 1191225.1327 | 2567206.5264 | 1191225.45
95 | 2567199.6685 | 1191214.8386 | 2567200.4345 | 1191216.0234 | 2567206.3214 | 1191225.1327
96 | 2567209.9644 | 1191127.2565 | 2567207.2717 | 1191124.6449
97 | 2567218.4738 | 1191119.0832 | 2567215.4098 | 1191122.0238 | 2567211.6708 | 1191125.6129 | 2567209.9644 | 1191127.2565
98 | 2567207.2717 | 1191124.6449 | 2567188.4979 | 1191106.4369
99 | 2567218.4738 | 1191119.0832 | 2567209.5816 | 1191110.3162
100 | 2567218.4738 | 1191119.0832 | 2567228.7203 | 1191128.1758
101 | 2567179.9574 | 1191184.3522 | 2567188.3313 | 1191197.3038
102 | 2567159.1543 | 1191180.64 | 2567158.307 | 1191179.4436
103 | 2567199.6685 | 1191214.8386 | 2567188.3313 | 1191197.3038
104 | 2567140.6938 | 1191061.2576 | 2567124.616 | 1191044.6503
105 | 2567273.2442 | 1191145.2077 | 2567269.7421 | 1191141.9474
106 | 2567269.7421 | 1191141.9474 | 2567267.9254 | 1191140.1564
107 | 2567272.6202 | 1191005.7031 | 2567275.6764 | 1191002.1138
108 | 2567272.6202 | 1191005.7031 | 2567260.9089 | 1191019.4575
109 | 2567275.6764 | 1191002.1138 | 2567286.5228 | 1190989.3752
110 | 2567260.9089 | 1191019.4575 | 2567259.1837 | 1191021.4837
111 | 2567286.5228 | 1190989.3752 | 2567301.0252 | 1190972.343
112 | 2567301.0252 | 1190972.343 | 2567302.238 | 1190970.9186
113 | 2567316.9378 | 1190953.6544 | 2567302.238 | 1190970.9186
114 | 2567248.6734 | 1191088.9446 | 2567273.2045 | 1191109.2258
115 | 2567246.3845 | 1191087.0523 | 2567248.6734 | 1191088.9446
116 | 2567246.3845 | 1191087.0523 | 2567243.3447 | 1191084.5391 | 2567231.6965 | 1191084.8365 | 2567226.6653 | 1191084.9642 | 2567220.4448 | 1191085.1207 | 2567215.573 | 1191078.9063
117 | 2567238.9593 | 1191052.357 | 2567241.476 | 1191054.2003
118 | 2567316.9378 | 1190953.6544 | 2567333.2287 | 1190934.5216
119 | 2567343.2432 | 1190922.7601 | 2567343.2432 | 1190922.7601 | 2567333.2287 | 1190934.5216
120 | 2567343.2432 | 1190922.7601 | 2567351.0146 | 1190928.4631
121 | 2567343.2432 | 1190922.7601 | 2567373.2862 | 1190875.9038
122 | 2567356.5107 | 1190932.4965 | 2567351.0146 | 1190928.4631
123 | 2567373.2862 | 1190875.9038 | 2567379.5444 | 1190867.265
124 | 2567356.5107 | 1190932.4965 | 2567367.4898 | 1190940.5536
125 | 2567316.4132 | 1190802.9793 | 2567328.2767 | 1190811.8539
126 | 2567316.4132 | 1190802.9793 | 2567292.6391 | 1190785.1946
127 | 2567372.6666 | 1190847.6587 | 2567356.1387 | 1190832.6966 | 2567328.2767 | 1190811.8539
128 | 2567372.6666 | 1190847.6587 | 2567386.4384 | 1190857.7778 | 2567379.5444 | 1190867.265
129 | 2567203.7807 | 1191063.864 | 2567215.573 | 1191078.9063
130 | 2567376.2865 | 1190947.0091 | 2567367.4898 | 1190940.5536
131 | 2567376.2865 | 1190947.0091 | 2567391.65 | 1190958.2837
132 | 2567391.65 | 1190958.2837 | 2567393.253 | 1190959.4601
133 | 2567393.253 | 1190959.4601 | 2567393.7116 | 1190959.7967
134 | 2567203.2441 | 1191063.1796 | 2567203.7807 | 1191063.864
135 | 2567200.2515 | 1191059.3622 | 2567203.2441 | 1191063.1796

## bus_geodata
| x | y | coords
0 | 2567259.3874 | 1191263.759
1 | 2567289.04 | 1191214.4473
2 | 2567265.369 | 1191193.9216
3 | 2567278.0794 | 1191149.6391
4 | 2567251.653 | 1191177.4179
5 | 2567268.3431 | 1191159.32
6 | 2567273.9 | 1191145.8087
7 | 2567309.1736 | 1191139.0741
8 | 2567221.1572 | 1191140.7242
9 | 2567175.1355 | 1191275.5797
10 | 2567171.283 | 1191277.4723
11 | 2567459.9377 | 1191261.9567
12 | 2567471.9593 | 1191248.6547
13 | 2567451.995 | 1191231.0207
14 | 2567424.3779 | 1191206.6232
15 | 2567461.4416 | 1191213.9228
16 | 2567401.4137 | 1191186.3361
17 | 2567475.002 | 1191189.3792
18 | 2567436.3409 | 1191027.7513
19 | 2567423.8054 | 1191015.3918
20 | 2567431.6736 | 1190987.456
21 | 2567406.7286 | 1191018.4867
22 | 2567413.3359 | 1190974.1981
23 | 2567402.0234 | 1191023.8709
24 | 2567424.0267 | 1191035.5173
25 | 2567411.0419 | 1190972.5146
26 | 2567397.8826 | 1191029.2964
27 | 2567386.493 | 1191012.6871
28 | 2567431.5878 | 1191042.9642
29 | 2567381.0801 | 1191018.9867
30 | 2567389.7773 | 1191038.9348
31 | 2567355.5379 | 1190990.3959
32 | 2567338.3151 | 1191103.1386
33 | 2567326.6392 | 1191116.5775
34 | 2567345.464 | 1191094.4403
35 | 2567309.4203 | 1191103.9656
36 | 2567341.9207 | 1191133.7698
37 | 2567348.468 | 1191090.4558
38 | 2567328.9632 | 1191083.3895
39 | 2567281.6558 | 1191083.6297
40 | 2567293.8921 | 1191126.3294
41 | 2567347.1612 | 1191138.4005
42 | 2567361.7694 | 1191074.4292
43 | 2567326.7925 | 1191081.9358
44 | 2567253.7905 | 1191063.2199
45 | 2567274.2229 | 1191110.0678
46 | 2567369.7337 | 1191064.1246
47 | 2567376.3568 | 1191086.0001
48 | 2567400.3769 | 1191150.0013
49 | 2567391.4633 | 1191160.9678
50 | 2567410.3662 | 1191137.7114
51 | 2567383.6203 | 1191170.6171
52 | 2567414.3053 | 1191132.8651
53 | 2567444.2592 | 1191096.0125
54 | 2567430.6483 | 1191081.5845
55 | 2567463.822 | 1191116.869
56 | 2567496.0692 | 1191151.2486
57 | 2567427.3147 | 1191078.0508
58 | 2567415.5813 | 1191065.613
59 | 2567382.3473 | 1191047.9691
60 | 2567353.1146 | 1191062.8556
61 | 2567363.5502 | 1191033.7597
62 | 2567402.8456 | 1191052.1128
63 | 2567346.6919 | 1191021.0159
64 | 2567125.5516 | 1191248.2529
65 | 2567129.8797 | 1191255.0694
66 | 2567122.6464 | 1191243.6775
67 | 2567144.1623 | 1191278.4444
68 | 2567144.3203 | 1191225.3194
69 | 2567105.4886 | 1191213.9449
70 | 2567156.9986 | 1191203.4031
71 | 2567110.9277 | 1191207.6226
72 | 2567097.383 | 1191199.9042
73 | 2567168.1822 | 1191193.3886
74 | 2567085.4759 | 1191207.1182
75 | 2567104.5015 | 1191192.5722
76 | 2567095.7856 | 1191175.8144
77 | 2567141.1933 | 1191123.9607
78 | 2567126.3495 | 1191140.9128
79 | 2567142.01 | 1191123.028
80 | 2567142.275 | 1191162.273
81 | 2567167.0636 | 1191098.3075
82 | 2567156.8613 | 1191138.1656
83 | 2567173.3101 | 1191091.7056
84 | 2567181.4811 | 1191099.6316
85 | 2567158.3452 | 1191077.7355
86 | 2567206.5265 | 1191225.45
87 | 2567206.3214 | 1191225.1327
88 | 2567209.9644 | 1191127.2565
89 | 2567207.2717 | 1191124.6449
90 | 2567218.4738 | 1191119.0832
91 | 2567188.4979 | 1191106.4369
92 | 2567209.5816 | 1191110.3162
93 | 2567228.7203 | 1191128.1758
94 | 2567179.9574 | 1191184.3522
95 | 2567159.1543 | 1191180.64
96 | 2567188.3313 | 1191197.3038
97 | 2567158.307 | 1191179.4436
98 | 2567199.6685 | 1191214.8386
99 | 2567186.2016 | 1191088.7113
100 | 2567124.616 | 1191044.6503
101 | 2567140.6938 | 1191061.2576
102 | 2567273.2442 | 1191145.2077
103 | 2567269.7421 | 1191141.9474
104 | 2567267.9254 | 1191140.1564
105 | 2567272.6202 | 1191005.7031
106 | 2567275.6764 | 1191002.1138
107 | 2567260.9089 | 1191019.4575
108 | 2567286.5228 | 1190989.3752
109 | 2567259.1837 | 1191021.4837
110 | 2567301.0252 | 1190972.343
111 | 2567302.238 | 1190970.9186
112 | 2567273.2045 | 1191109.2258
113 | 2567248.6734 | 1191088.9446
114 | 2567246.3845 | 1191087.0523
115 | 2567241.476 | 1191054.2003
116 | 2567238.9593 | 1191052.357
117 | 2567316.9378 | 1190953.6544
118 | 2567333.2287 | 1190934.5216
119 | 2567343.2432 | 1190922.7601
120 | 2567351.0146 | 1190928.4631
121 | 2567373.2862 | 1190875.9038
122 | 2567356.5107 | 1190932.4965
123 | 2567316.4132 | 1190802.9793
124 | 2567328.2767 | 1190811.8539
125 | 2567292.6391 | 1190785.1946
126 | 2567372.6666 | 1190847.6587
127 | 2567379.5444 | 1190867.265
128 | 2567215.573 | 1191078.9063
129 | 2567367.4898 | 1190940.5536
130 | 2567376.2865 | 1190947.0091
131 | 2567391.65 | 1190958.2837
132 | 2567393.253 | 1190959.4601
133 | 2567393.7116 | 1190959.7967
134 | 2567203.2441 | 1191063.1796
135 | 2567203.7807 | 1191063.864
136 | 2567200.2515 | 1191059.3622
137 | 2567238.9593 | 1191052.357

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98801 | -0.08343 | 0.005632 | 0.0014115
1 | 0.9885 | -0.079968 | 0 | 0
2 | 0.98876 | -0.078167 | 0 | 0
3 | 0.99083 | -0.063652 | 0 | 0
4 | 0.98806 | -0.083058 | 0.0030038 | 0.00075283
5 | 0.99078 | -0.064025 | 0.0026702 | 0.0006692
6 | 0.9908 | -0.063863 | 0.0028379 | 0.00071125
7 | 0.99261 | -0.051188 | 0 | 0
8 | 0.98584 | -0.098683 | 0.00086974 | 0.00021798
9 | 0.97262 | -0.19279 | 0.00063141 | 0.00015825
10 | 0.97263 | -0.19276 | 0 | 0
11 | 0.98498 | -0.10499 | 0.00059547 | 0.00014924
12 | 0.98499 | -0.10488 | 0 | 0
13 | 0.98502 | -0.10471 | 0 | 0
14 | 0.98466 | -0.10724 | 0.00083682 | 0.00020973
15 | 0.98522 | -0.10325 | 0.00029818 | 7.473e-05
16 | 0.9844 | -0.10907 | 0.00074989 | 0.00018794
17 | 0.98553 | -0.10107 | 0.0017096 | 0.00042848
18 | 0.9863 | -0.095395 | 0.00025088 | 6.2876e-05
19 | 0.9863 | -0.09535 | 0 | 0
20 | 0.98271 | -0.12064 | 0 | 0
21 | 0.98756 | -0.086539 | 0 | 0
22 | 0.98052 | -0.13614 | 0.0017492 | 0.00043838
23 | 0.9878 | -0.084887 | 0 | 0
24 | 0.98751 | -0.086892 | 0.0011015 | 0.00027607
25 | 0.98025 | -0.13804 | 0.0035164 | 0.0008813
26 | 0.98805 | -0.083083 | 0 | 0
27 | 0.98753 | -0.086809 | 0.0029538 | 0.0007403
28 | 0.98751 | -0.086926 | 0.00031734 | 7.9532e-05
29 | 0.98796 | -0.083717 | 0.0031453 | 0.00078828
30 | 0.98855 | -0.079622 | 0 | 0
31 | 0.98715 | -0.089487 | 0.0068558 | 0.0017182
32 | 0.99284 | -0.049629 | 0.0016838 | 0.00042199
33 | 0.99392 | -0.042054 | 0 | 0
34 | 0.99216 | -0.054359 | 0 | 0
35 | 0.99623 | -0.02607 | 0.0039304 | 0.00098505
36 | 0.99386 | -0.042496 | 0 | 0
37 | 0.99189 | -0.056252 | 0.00084178 | 0.00021097
38 | 0.99181 | -0.056805 | 0.0037677 | 0.00094426
39 | 1 | 0 | -0.23857 | -0.060105
40 | 0.99215 | -0.054449 | 0.0022857 | 0.00057285
41 | 0.99384 | -0.042617 | 0.0017174 | 0.00043041
42 | 0.99076 | -0.064106 | 0 | 0
43 | 0.99178 | -0.057027 | 0.0083779 | 0.0020997
44 | 0.99965 | -0.0024456 | 0.0026393 | 0.00066148
45 | 0.99164 | -0.058044 | 0.0016776 | 0.00042045
46 | 0.99011 | -0.068708 | 0 | 0
47 | 0.99057 | -0.065447 | 0.0070925 | 0.0017775
48 | 0.98406 | -0.11153 | 0.00064211 | 0.00016093
49 | 0.98414 | -0.11096 | 0.0011418 | 0.00028616
50 | 0.98398 | -0.11207 | 0.0021038 | 0.00052727
51 | 0.98423 | -0.11031 | 0 | 0
52 | 0.98397 | -0.11214 | 0.0011739 | 0.00029421
53 | 0.98716 | -0.089475 | 0 | 0
54 | 0.98745 | -0.087421 | 0.00047935 | 0.00012014
55 | 0.98674 | -0.092437 | 0.00082654 | 0.00020715
56 | 0.98611 | -0.096923 | 0 | 0
57 | 0.98752 | -0.086894 | 0.00065918 | 0.00016521
58 | 0.9878 | -0.084926 | 0.00044213 | 0.00011081
59 | 0.9891 | -0.075764 | 0 | 0
60 | 0.99001 | -0.069375 | 0.0028287 | 0.00070894
61 | 0.98895 | -0.076826 | 0.0031862 | 0.00079854
62 | 0.98811 | -0.082706 | 0.0045516 | 0.0011407
63 | 0.98891 | -0.077091 | 0.0012269 | 0.00030749
64 | 0.97269 | -0.19231 | 0.0010344 | 0.00025924
65 | 0.97268 | -0.19239 | 0.00035091 | 8.7946e-05
66 | 0.97271 | -0.19219 | 0 | 0
67 | 0.97265 | -0.19258 | 0 | 0
68 | 0.97218 | -0.19597 | 0.0003438 | 8.6165e-05
69 | 0.97344 | -0.18691 | 0 | 0
70 | 0.97171 | -0.1994 | 0.00036317 | 9.1019e-05
71 | 0.9734 | -0.18719 | 0.0031923 | 0.00080007
72 | 0.97387 | -0.18387 | 0 | 0
73 | 0.97144 | -0.20129 | 0 | 0
74 | 0.9738 | -0.18432 | 0.00311 | 0.00077943
75 | 0.97383 | -0.18414 | 0.0025454 | 0.00063794
76 | 0.9748 | -0.17716 | 0.0021806 | 0.00054652
77 | 0.9775 | -0.15783 | 0.0034754 | 0.00087102
78 | 0.97654 | -0.16468 | 0 | 0
79 | 0.97756 | -0.15741 | 0 | 0
80 | 0.97641 | -0.16563 | 0.0034052 | 0.00085343
81 | 0.97973 | -0.14192 | 0.00098084 | 0.00024582
82 | 0.97729 | -0.15936 | 0.008792 | 0.0022035
83 | 0.98029 | -0.13793 | 0 | 0
84 | 0.98107 | -0.13238 | 0 | 0
85 | 0.98015 | -0.13893 | 0.0030646 | 0.00076806
86 | 0.97114 | -0.20346 | 0.00052007 | 0.00013034
87 | 0.97114 | -0.20346 | 0.00072104 | 0.00018071
88 | 0.98423 | -0.11004 | 0 | 0
89 | 0.98391 | -0.11227 | 0.0023399 | 0.00058643
90 | 0.98413 | -0.1107 | 0 | 0
91 | 0.9818 | -0.1272 | 0.0041401 | 0.0010376
92 | 0.98407 | -0.11114 | 0.0034231 | 0.00085791
93 | 0.98409 | -0.11099 | 0.0020182 | 0.0005058
94 | 0.97131 | -0.20226 | 0.0020694 | 0.00051864
95 | 0.97131 | -0.20223 | 0.0025514 | 0.00063944
96 | 0.97122 | -0.20293 | 0.0024639 | 0.0006175
97 | 0.97131 | -0.20228 | 0.0031544 | 0.00079056
98 | 0.97117 | -0.20329 | 0.00039876 | 9.9939e-05
99 | 0.98098 | -0.13303 | 0.0040626 | 0.0010182
100 | 0.98004 | -0.13974 | 0.001652 | 0.00041404
101 | 0.98009 | -0.13935 | 0 | 0
102 | 0.9908 | -0.06387 | 0 | 0
103 | 0.99079 | -0.063909 | 0 | 0
104 | 0.99079 | -0.06393 | 0.00080542 | 0.00020186
105 | 0.97082 | -0.20557 | 0.0031414 | 0.00078731
106 | 0.97087 | -0.20519 | 0.0030869 | 0.00077365
107 | 0.9707 | -0.20645 | 0.0020303 | 0.00050885
108 | 0.97114 | -0.20328 | 0.0027067 | 0.00067837
109 | 0.97069 | -0.20652 | 0.0025436 | 0.00063748
110 | 0.97158 | -0.20008 | 0.0042645 | 0.0010688
111 | 0.97163 | -0.19973 | 0.0027867 | 0.00069841
112 | 0.99162 | -0.058207 | 0.0016765 | 0.00042016
113 | 0.99114 | -0.06161 | 0.0024506 | 0.00061419
114 | 0.9911 | -0.061854 | 0.0022456 | 0.00056281
115 | 0.99955 | -0.0031241 | 0.0018482 | 0.00046319
116 | 0.99954 | -0.0032052 | 0.002601 | 0.00065187
117 | 0.97231 | -0.1948 | 0.0044729 | 0.001121
118 | 0.97324 | -0.18816 | 0.0036995 | 0.00092719
119 | 0.97389 | -0.18349 | 0.0032397 | 0.00081195
120 | 0.97447 | -0.17931 | 0.0031711 | 0.00079475
121 | 0.97314 | -0.1889 | 0.0034235 | 0.000858
122 | 0.97491 | -0.17613 | 0.0021114 | 0.00052917
123 | 0.97223 | -0.19542 | 0.0019295 | 0.00048358
124 | 0.97232 | -0.1948 | 0.0018741 | 0.00046969
125 | 0.97215 | -0.19604 | 0.0019871 | 0.00049802
126 | 0.9728 | -0.19131 | 0 | 0
127 | 0.97305 | -0.18955 | 0 | 0
128 | 0.99081 | -0.063912 | 0.0016261 | 0.00040754
129 | 0.97584 | -0.16949 | 0.0042848 | 0.0010739
130 | 0.97665 | -0.16368 | 0.0021082 | 0.00052837
131 | 0.97813 | -0.15315 | 0.0027505 | 0.00068934
132 | 0.97829 | -0.152 | 0.0021264 | 0.00053292
133 | 0.97834 | -0.15166 | 0.0030782 | 0.00077146
134 | 0.99069 | -0.064751 | 0.0015946 | 0.00039966
135 | 0.9907 | -0.064728 | 0.0015824 | 0.00039658
136 | 0.99069 | -0.064802 | 0.0010209 | 0.00025586
137 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.005632 | -0.0014115 | 0.0056347 | 0.0014118 | 2.6992e-06 | 2.6779e-07 | 0.0084822 | 0.008482 | 0.0084822 | 0.98801 | -0.08343 | 0.9885 | -0.079968 | 3.1416
1 | -0.0056347 | -0.0014118 | 0.0056362 | 0.0014119 | 1.4043e-06 | 1.39e-07 | 0.008482 | 0.0084818 | 0.008482 | 0.9885 | -0.079968 | 0.98876 | -0.078167 | 3.1415
2 | -0.073239 | -0.018444 | 0.073388 | 0.018499 | 0.00014888 | 5.4991e-05 | 0.11025 | 0.11025 | 0.11025 | 0.98876 | -0.078167 | 0.99083 | -0.063652 | 13.6114
3 | 0.067603 | 0.017032 | -0.067557 | -0.017015 | 4.623e-05 | 1.6956e-05 | 0.10177 | 0.10177 | 0.10177 | 0.98876 | -0.078167 | 0.98806 | -0.083058 | 12.5643
4 | 0.0026703 | 0.00066908 | -0.0026702 | -0.0006692 | 1.376e-07 | -1.2368e-07 | 0.0040102 | 0.0040102 | 0.0040102 | 0.99083 | -0.063652 | 0.99078 | -0.064025 | 1.4853
5 | 0.0036435 | 0.00091297 | -0.0036433 | -0.000913 | 1.0591e-07 | -3.228e-08 | 0.0054716 | 0.0054717 | 0.0054717 | 0.99083 | -0.063652 | 0.9908 | -0.063863 | 2.0265
6 | -0.079702 | -0.020081 | 0.079841 | 0.020133 | 0.00013923 | 5.1744e-05 | 0.11973 | 0.11973 | 0.11973 | 0.99083 | -0.063652 | 0.99261 | -0.051188 | 14.7819
7 | 0.064553 | 0.016262 | -0.064412 | -0.016209 | 0.00014078 | 5.2926e-05 | 0.097247 | 0.097247 | 0.097247 | 0.98806 | -0.083058 | 0.98584 | -0.098683 | 18.0087
8 | 0.00080543 | 0.00020175 | -0.00080543 | -0.00020177 | 8.1219e-10 | -1.1144e-08 | 0.0012096 | 0.0012096 | 0.0012096 | 0.9908 | -0.063863 | 0.9908 | -0.06387 | 0.448
9 | 0.016182 | 0.0040567 | -0.016175 | -0.0040541 | 7.3072e-06 | 2.5534e-06 | 0.024258 | 0.024259 | 0.024259 | 0.99261 | -0.051188 | 0.99215 | -0.054449 | 8.9847
10 | -0.096023 | -0.02419 | 0.096146 | 0.024236 | 0.00012282 | 4.6134e-05 | 0.14399 | 0.14399 | 0.14399 | 0.99261 | -0.051188 | 0.99392 | -0.042054 | 17.7767
11 | 0.063543 | 0.015991 | -0.063442 | -0.015953 | 0.00010057 | 3.8457e-05 | 0.095934 | 0.095935 | 0.095935 | 0.98584 | -0.098683 | 0.98423 | -0.11004 | 35.5313
12 | -0.00063141 | -0.00015825 | 0.00063141 | 0.00015819 | 2.4993e-09 | -5.231e-08 | 0.00096599 | 0.00096597 | 0.00096599 | 0.97262 | -0.19279 | 0.97263 | -0.19276 | 0.35777
13 | -0.00063141 | -0.00015819 | 0.00063143 | 0.00015785 | 1.6208e-08 | -3.3931e-07 | 0.00096597 | 0.00096585 | 0.00096597 | 0.97263 | -0.19276 | 0.97265 | -0.19258 | 0.35777
14 | -0.00059547 | -0.00014924 | 0.00059548 | 0.00014901 | 9.0529e-09 | -2.2473e-07 | 0.00089958 | 0.0008995 | 0.00089958 | 0.98498 | -0.10499 | 0.98499 | -0.10488 | 0.33318
15 | -0.00059548 | -0.00014901 | 0.00059549 | 0.00014868 | 1.3426e-08 | -3.3338e-07 | 0.0008995 | 0.00089938 | 0.0008995 | 0.98499 | -0.10488 | 0.98502 | -0.10471 | 0.33315
16 | 0.0066541 | 0.0016666 | -0.0066517 | -0.0016662 | 2.3233e-06 | 4.2467e-07 | 0.010052 | 0.010052 | 0.010052 | 0.98502 | -0.10471 | 0.98466 | -0.10724 | 3.7229
17 | -0.0072496 | -0.0018153 | 0.007251 | 0.0018156 | 1.4618e-06 | 3.1352e-07 | 0.010951 | 0.010951 | 0.010951 | 0.98502 | -0.10471 | 0.98522 | -0.10325 | 4.0559
18 | 0.0058149 | 0.0014565 | -0.0058134 | -0.0014563 | 1.4764e-06 | 1.7819e-07 | 0.0087872 | 0.0087873 | 0.0087873 | 0.98466 | -0.10724 | 0.9844 | -0.10907 | 3.2546
19 | -0.0075492 | -0.0018904 | 0.0075515 | 0.0018909 | 2.2744e-06 | 5.1759e-07 | 0.011401 | 0.011401 | 0.011401 | 0.98522 | -0.10325 | 0.98553 | -0.10107 | 4.2227
20 | 0.0050636 | 0.0012684 | -0.0050627 | -0.0012683 | 8.6789e-07 | 3.2017e-08 | 0.0076538 | 0.0076539 | 0.0076539 | 0.9844 | -0.10907 | 0.98423 | -0.11031 | 2.8348
21 | -0.0092611 | -0.0023194 | 0.0092664 | 0.0023209 | 5.3146e-06 | 1.4886e-06 | 0.013982 | 0.013982 | 0.013982 | 0.98553 | -0.10107 | 0.98611 | -0.096923 | 5.1787
22 | -0.00025088 | -6.2876e-05 | 0.00025088 | 6.2652e-05 | 1.5733e-09 | -2.2406e-07 | 0.0003785 | 0.00037842 | 0.0003785 | 0.9863 | -0.095395 | 0.9863 | -0.09535 | 0.14018
23 | 0.066891 | 0.016867 | -0.066655 | -0.016777 | 0.00023623 | 9.0386e-05 | 0.10095 | 0.10095 | 0.10095 | 0.9863 | -0.09535 | 0.98271 | -0.12064 | 37.3906
24 | -0.067142 | -0.01693 | 0.067225 | 0.016961 | 8.3002e-05 | 3.1262e-05 | 0.10133 | 0.10133 | 0.10133 | 0.9863 | -0.09535 | 0.98756 | -0.086539 | 18.7653
25 | 0.066655 | 0.016777 | -0.066511 | -0.016722 | 0.00014393 | 5.5071e-05 | 0.10095 | 0.10095 | 0.10095 | 0.98271 | -0.12064 | 0.98052 | -0.13614 | 37.3906
26 | -0.068644 | -0.017316 | 0.06866 | 0.017322 | 1.5904e-05 | 5.8428e-06 | 0.10347 | 0.10347 | 0.10347 | 0.98756 | -0.086539 | 0.9878 | -0.084887 | 12.7741
27 | 0.001419 | 0.00035519 | -0.0014189 | -0.00035547 | 6.9235e-08 | -2.8395e-07 | 0.0021379 | 0.002138 | 0.002138 | 0.98756 | -0.086539 | 0.98751 | -0.086892 | 0.79184
28 | 0.064762 | 0.016283 | -0.064745 | -0.016277 | 1.7157e-05 | 6.5631e-06 | 0.0983 | 0.0983 | 0.0983 | 0.98052 | -0.13614 | 0.98025 | -0.13804 | 36.4075
29 | -0.078475 | -0.019782 | 0.078495 | 0.019789 | 1.9835e-05 | 7.3668e-06 | 0.11826 | 0.11826 | 0.11826 | 0.9878 | -0.084887 | 0.98805 | -0.083083 | 14.5994
30 | 0.0098148 | 0.0024598 | -0.0098122 | -0.002459 | 2.6106e-06 | 7.5914e-07 | 0.014785 | 0.014785 | 0.014785 | 0.9878 | -0.084887 | 0.98753 | -0.086809 | 5.476
31 | 0.00031734 | 7.9397e-05 | -0.00031734 | -7.9532e-05 | 1.514e-09 | -1.3519e-07 | 0.00047813 | 0.00047818 | 0.00047818 | 0.98751 | -0.086892 | 0.98751 | -0.086926 | 0.1771
32 | 0.061229 | 0.015395 | -0.061113 | -0.015351 | 0.00011592 | 4.4314e-05 | 0.092962 | 0.092962 | 0.092962 | 0.98025 | -0.13804 | 0.97834 | -0.15166 | 34.4305
33 | 0.0031456 | 0.00078814 | -0.0031453 | -0.00078828 | 2.7605e-07 | -1.4629e-07 | 0.0047372 | 0.0047373 | 0.0047373 | 0.98805 | -0.083083 | 0.98796 | -0.083717 | 1.7545
34 | -0.08164 | -0.020577 | 0.08168 | 0.020592 | 3.9582e-05 | 1.474e-05 | 0.12299 | 0.12299 | 0.12299 | 0.98805 | -0.083083 | 0.98855 | -0.079622 | 15.1842
35 | 0.0068584 | 0.0017187 | -0.0068558 | -0.0017182 | 2.5421e-06 | 4.8989e-07 | 0.010334 | 0.010334 | 0.010334 | 0.98753 | -0.086809 | 0.98715 | -0.089487 | 3.8276
36 | -0.097932 | -0.024665 | 0.097985 | 0.024685 | 5.2847e-05 | 1.9876e-05 | 0.14746 | 0.14746 | 0.14746 | 0.98855 | -0.079622 | 0.9891 | -0.075764 | 18.2045
37 | 0.016252 | 0.0040733 | -0.016245 | -0.0040709 | 6.9365e-06 | 2.4299e-06 | 0.024464 | 0.024464 | 0.024464 | 0.98855 | -0.079622 | 0.98811 | -0.082706 | 9.0607
38 | -0.1274 | -0.032109 | 0.12754 | 0.032161 | 0.00013525 | 5.1328e-05 | 0.19101 | 0.19101 | 0.19101 | 0.99284 | -0.049629 | 0.99392 | -0.042054 | 23.5814
39 | 0.12572 | 0.031687 | -0.12564 | -0.031656 | 8.32e-05 | 3.1564e-05 | 0.18849 | 0.18849 | 0.18849 | 0.99284 | -0.049629 | 0.99216 | -0.054359 | 23.2698
40 | -0.2254 | -0.056826 | 0.22591 | 0.05702 | 0.00050589 | 0.00019374 | 0.33757 | 0.33757 | 0.33757 | 0.99392 | -0.042054 | 0.99623 | -0.02607 | 41.6754
41 | 0.0017175 | 0.00043004 | -0.0017174 | -0.00043033 | 1.0484e-07 | -2.8902e-07 | 0.0025712 | 0.0025713 | 0.0025713 | 0.99392 | -0.042054 | 0.99386 | -0.042496 | 0.95232
42 | 0.11349 | 0.02861 | -0.11346 | -0.028599 | 3.0089e-05 | 1.1379e-05 | 0.17026 | 0.17026 | 0.17026 | 0.99216 | -0.054359 | 0.99189 | -0.056252 | 21.0202
43 | 0.01215 | 0.0030453 | -0.012146 | -0.003044 | 4.1149e-06 | 1.3263e-06 | 0.018222 | 0.018222 | 0.018222 | 0.99216 | -0.054359 | 0.99181 | -0.056805 | 6.749
44 | -0.22984 | -0.058005 | 0.23068 | 0.058328 | 0.00084435 | 0.0003234 | 0.34344 | 0.34344 | 0.34344 | 0.99623 | -0.02607 | 1 | 0 | 42.4001
45 | 0.0017174 | 0.00043033 | -0.0017174 | -0.00043041 | 2.8852e-08 | -7.9527e-08 | 0.0025713 | 0.0025713 | 0.0025713 | 0.99386 | -0.042496 | 0.99384 | -0.042617 | 0.95233
46 | 0.11261 | 0.028388 | -0.11249 | -0.028341 | 0.00012374 | 4.6786e-05 | 0.169 | 0.169 | 0.169 | 0.99189 | -0.056252 | 0.99076 | -0.064106 | 20.8643
47 | 0.0083781 | 0.0020998 | -0.0083779 | -0.0020997 | 2.5757e-07 | 6.5351e-08 | 0.01257 | 0.01257 | 0.01257 | 0.99181 | -0.056805 | 0.99178 | -0.057027 | 4.6555
48 | 0.0070913 | 0.0017769 | -0.0070889 | -0.0017765 | 2.3998e-06 | 4.7001e-07 | 0.010552 | 0.010552 | 0.010552 | 1 | 0 | 0.99965 | -0.0024456 | 3.9082
49 | 0.013889 | 0.0034813 | -0.013882 | -0.003479 | 6.9101e-06 | 2.3283e-06 | 0.020831 | 0.020831 | 0.020831 | 0.99215 | -0.054449 | 0.99164 | -0.058044 | 7.7151
50 | 0.1054 | 0.026563 | -0.10533 | -0.026538 | 6.7857e-05 | 2.5596e-05 | 0.15835 | 0.15835 | 0.15835 | 0.99076 | -0.064106 | 0.99011 | -0.068708 | 19.549
51 | 0.0070938 | 0.0017778 | -0.0070925 | -0.0017775 | 1.3166e-06 | 2.6705e-07 | 0.010654 | 0.010654 | 0.010654 | 0.99076 | -0.064106 | 0.99057 | -0.065447 | 3.946
52 | 0.0044496 | 0.001115 | -0.0044492 | -0.001115 | 4.1785e-07 | -3.9388e-08 | 0.0066233 | 0.0066234 | 0.0066234 | 0.99965 | -0.0024456 | 0.99955 | -0.0031241 | 2.4531
53 | 0.012204 | 0.0030585 | -0.012204 | -0.0030584 | 2.7653e-07 | 8.9312e-08 | 0.018313 | 0.018313 | 0.018313 | 0.99164 | -0.058044 | 0.99162 | -0.058207 | 6.7827
54 | 0.1025 | 0.025829 | -0.1024 | -0.025791 | 0.00010113 | 3.8108e-05 | 0.1541 | 0.1541 | 0.1541 | 0.99011 | -0.068708 | 0.9891 | -0.075764 | 19.0242
55 | 0.002829 | 0.00070874 | -0.0028287 | -0.00070894 | 2.613e-07 | -1.9742e-07 | 0.0042515 | 0.0042516 | 0.0042516 | 0.99011 | -0.068708 | 0.99001 | -0.069375 | 1.5747
56 | -0.0039201 | -0.00098223 | 0.0039204 | 0.00098217 | 3.0985e-07 | -6.0382e-08 | 0.0059276 | 0.0059275 | 0.0059276 | 0.98406 | -0.11153 | 0.98414 | -0.11096 | 2.1954
57 | 0.003278 | 0.0008213 | -0.0032778 | -0.00082141 | 2.4281e-07 | -1.078e-07 | 0.0049567 | 0.0049567 | 0.0049567 | 0.98406 | -0.11153 | 0.98398 | -0.11207 | 1.8358
58 | -0.0050622 | -0.0012683 | 0.0050627 | 0.0012683 | 4.5456e-07 | 1.6815e-08 | 0.007654 | 0.0076539 | 0.007654 | 0.98414 | -0.11096 | 0.98423 | -0.11031 | 2.8348
59 | 0.0011739 | 0.00029414 | -0.0011739 | -0.00029421 | 1.2281e-08 | -7.4605e-08 | 0.0017752 | 0.0017753 | 0.0017753 | 0.98398 | -0.11207 | 0.98397 | -0.11214 | 0.6575
60 | -0.010103 | -0.0025308 | 0.010106 | 0.0025317 | 2.8702e-06 | 8.5028e-07 | 0.015228 | 0.015228 | 0.015228 | 0.98716 | -0.089475 | 0.98745 | -0.087421 | 5.6401
61 | 0.010103 | 0.0025308 | -0.010099 | -0.0025296 | 4.138e-06 | 1.2261e-06 | 0.015228 | 0.015228 | 0.015228 | 0.98716 | -0.089475 | 0.98674 | -0.092437 | 5.6402
62 | -0.010585 | -0.0026518 | 0.010586 | 0.0026521 | 7.7126e-07 | 2.3449e-07 | 0.015951 | 0.015951 | 0.015951 | 0.98745 | -0.087421 | 0.98752 | -0.086894 | 5.9076
63 | 0.0092722 | 0.0023225 | -0.0092664 | -0.0023209 | 5.7503e-06 | 1.6099e-06 | 0.013982 | 0.013982 | 0.013982 | 0.98674 | -0.092437 | 0.98611 | -0.096923 | 5.1786
64 | -0.011245 | -0.0028173 | 0.011248 | 0.0028182 | 3.0632e-06 | 9.5932e-07 | 0.016944 | 0.016944 | 0.016944 | 0.98752 | -0.086894 | 0.9878 | -0.084926 | 6.2755
65 | -0.01169 | -0.002929 | 0.011694 | 0.0029302 | 3.5913e-06 | 1.1436e-06 | 0.01761 | 0.01761 | 0.01761 | 0.9878 | -0.084926 | 0.98811 | -0.082706 | 6.5221
66 | 0.0044138 | 0.0011057 | -0.0044131 | -0.0011058 | 6.4829e-07 | -5.3046e-08 | 0.00664 | 0.0066401 | 0.0066401 | 0.9891 | -0.075764 | 0.98895 | -0.076826 | 2.4593
67 | 0.0012269 | 0.00030723 | -0.0012269 | -0.00030749 | 4.494e-08 | -2.5386e-07 | 0.001846 | 0.0018461 | 0.0018461 | 0.98895 | -0.076826 | 0.98891 | -0.077091 | 0.68374
68 | 0.00098236 | 0.00024537 | -0.00098235 | -0.00024547 | 1.1375e-08 | -9.5848e-08 | 0.0015025 | 0.0015025 | 0.0015025 | 0.97269 | -0.19231 | 0.97268 | -0.19239 | 0.5565
69 | -0.0020167 | -0.00050461 | 0.0020168 | 0.00050456 | 3.2185e-08 | -5.4897e-08 | 0.0030849 | 0.0030849 | 0.0030849 | 0.97269 | -0.19231 | 0.97271 | -0.19219 | 1.1426
70 | 0.00063144 | 0.00015752 | -0.00063143 | -0.00015785 | 1.5945e-08 | -3.3389e-07 | 0.00096572 | 0.00096585 | 0.00096585 | 0.97268 | -0.19239 | 0.97265 | -0.19258 | 0.35772
71 | 0.012603 | 0.0031592 | -0.012597 | -0.003157 | 6.5887e-06 | 2.1817e-06 | 0.019281 | 0.019281 | 0.019281 | 0.97271 | -0.19219 | 0.97218 | -0.19597 | 7.141
72 | -0.01462 | -0.0036638 | 0.014631 | 0.0036675 | 1.0709e-05 | 3.6927e-06 | 0.022365 | 0.022365 | 0.022365 | 0.97271 | -0.19219 | 0.97344 | -0.18691 | 8.2835
73 | 0.012253 | 0.0030709 | -0.012247 | -0.003069 | 5.8227e-06 | 1.9107e-06 | 0.018754 | 0.018755 | 0.018755 | 0.97218 | -0.19597 | 0.97171 | -0.1994 | 6.9461
74 | 0.0031924 | 0.00080001 | -0.0031923 | -0.00080007 | 1.238e-07 | -5.595e-08 | 0.00488 | 0.00488 | 0.00488 | 0.97344 | -0.18691 | 0.9734 | -0.18719 | 1.8074
75 | -0.017823 | -0.0044675 | 0.017831 | 0.0044702 | 7.5056e-06 | 2.6852e-06 | 0.027245 | 0.027245 | 0.027245 | 0.97344 | -0.18691 | 0.97387 | -0.18387 | 10.0908
76 | 0.011884 | 0.0029779 | -0.011881 | -0.0029769 | 3.1024e-06 | 1.0073e-06 | 0.018198 | 0.018199 | 0.018199 | 0.97171 | -0.1994 | 0.97144 | -0.20129 | 6.7402
77 | 0.0031102 | 0.00077933 | -0.00311 | -0.00077943 | 1.9578e-07 | -9.7554e-08 | 0.0047521 | 0.0047522 | 0.0047522 | 0.97387 | -0.18387 | 0.9738 | -0.18432 | 1.7601
78 | 0.0025455 | 0.00063785 | -0.0025454 | -0.00063794 | 9.6338e-08 | -8.993e-08 | 0.0038893 | 0.0038894 | 0.0038894 | 0.97387 | -0.18387 | 0.97383 | -0.18414 | 1.4405
79 | -0.023487 | -0.0058873 | 0.023508 | 0.0058954 | 2.1819e-05 | 8.0536e-06 | 0.035887 | 0.035886 | 0.035887 | 0.97387 | -0.18387 | 0.9748 | -0.17716 | 13.2913
80 | 0.0061745 | 0.0015469 | -0.0061736 | -0.0015467 | 8.2844e-07 | 1.3489e-07 | 0.0094575 | 0.0094576 | 0.0094576 | 0.97144 | -0.20129 | 0.97131 | -0.20226 | 3.5028
81 | 0.0057065 | 0.0014301 | -0.0057058 | -0.00143 | 7.4478e-07 | 9.3075e-08 | 0.008741 | 0.008741 | 0.008741 | 0.97144 | -0.20129 | 0.97131 | -0.20223 | 3.2374
82 | -0.025689 | -0.0064419 | 0.025734 | 0.0064585 | 4.4518e-05 | 1.6543e-05 | 0.039215 | 0.039215 | 0.039215 | 0.9748 | -0.17716 | 0.97654 | -0.16468 | 14.5241
83 | 0.029167 | 0.0073221 | -0.029139 | -0.0073117 | 2.7723e-05 | 1.0381e-05 | 0.044404 | 0.044404 | 0.044404 | 0.9775 | -0.15783 | 0.97654 | -0.16468 | 16.446
84 | -0.032642 | -0.0081931 | 0.032644 | 0.0081938 | 1.9103e-06 | 7.1921e-07 | 0.049695 | 0.049695 | 0.049695 | 0.9775 | -0.15783 | 0.97756 | -0.15741 | 18.4055
85 | 0.0034057 | 0.00085327 | -0.0034052 | -0.00085343 | 4.4773e-07 | -1.6109e-07 | 0.0051893 | 0.0051895 | 0.0051895 | 0.97654 | -0.16468 | 0.97641 | -0.16563 | 1.922
86 | -0.041439 | -0.010398 | 0.041528 | 0.010432 | 8.9243e-05 | 3.3873e-05 | 0.063081 | 0.063081 | 0.063081 | 0.97756 | -0.15741 | 0.97973 | -0.14192 | 23.3635
87 | 0.0087944 | 0.0022041 | -0.008792 | -0.0022035 | 2.3683e-06 | 6.4543e-07 | 0.013387 | 0.013387 | 0.013387 | 0.97756 | -0.15741 | 0.97729 | -0.15936 | 4.958
88 | -0.042509 | -0.010678 | 0.042532 | 0.010687 | 2.3646e-05 | 8.9801e-06 | 0.064571 | 0.064571 | 0.064571 | 0.97973 | -0.14192 | 0.98029 | -0.13793 | 23.9151
89 | -0.04725 | -0.011868 | 0.047286 | 0.011882 | 3.6499e-05 | 1.3895e-05 | 0.071731 | 0.071731 | 0.071731 | 0.98029 | -0.13793 | 0.98107 | -0.13238 | 26.5672
90 | 0.0047175 | 0.0011816 | -0.0047168 | -0.0011816 | 6.5501e-07 | -6.1354e-09 | 0.0071606 | 0.0071606 | 0.0071606 | 0.98029 | -0.13793 | 0.98015 | -0.13893 | 2.6521
91 | 0.004063 | 0.0010181 | -0.0040626 | -0.0010182 | 3.6736e-07 | -5.4445e-08 | 0.0061624 | 0.0061625 | 0.0061625 | 0.98107 | -0.13238 | 0.98098 | -0.13303 | 2.2824
92 | -0.051349 | -0.0129 | 0.051386 | 0.012914 | 3.7009e-05 | 1.4111e-05 | 0.077894 | 0.077894 | 0.077894 | 0.98107 | -0.13238 | 0.9818 | -0.1272 | 28.8495
93 | 0.0016522 | 0.00041351 | -0.0016521 | -0.00041378 | 9.4791e-08 | -2.6787e-07 | 0.0025081 | 0.0025082 | 0.0025082 | 0.98015 | -0.13893 | 0.98009 | -0.13935 | 0.92897
94 | -0.00052007 | -0.00013034 | 0.00052007 | 0.00013034 | 1.4944e-10 | -4.6171e-09 | 0.00079687 | 0.00079687 | 0.00079687 | 0.97114 | -0.20346 | 0.97114 | -0.20346 | 0.29514
95 | -0.0012411 | -0.00031105 | 0.0012411 | 0.00031091 | 2.7658e-08 | -1.4102e-07 | 0.0019017 | 0.0019016 | 0.0019017 | 0.97114 | -0.20346 | 0.97117 | -0.20329 | 0.70432
96 | 0.058 | 0.014589 | -0.057982 | -0.014583 | 1.8006e-05 | 6.8778e-06 | 0.087707 | 0.087707 | 0.087707 | 0.98423 | -0.11004 | 0.98391 | -0.11227 | 32.4841
97 | 0.0054421 | 0.0013635 | -0.0054416 | -0.0013635 | 4.9767e-07 | 4.1693e-08 | 0.0082275 | 0.0082276 | 0.0082276 | 0.98423 | -0.11004 | 0.98413 | -0.1107 | 3.0472
98 | 0.055642 | 0.013996 | -0.055526 | -0.013952 | 0.00011561 | 4.4135e-05 | 0.084168 | 0.084168 | 0.084168 | 0.98391 | -0.11227 | 0.9818 | -0.1272 | 31.1735
99 | 0.0034233 | 0.00085783 | -0.0034231 | -0.00085791 | 2.0847e-07 | -7.8256e-08 | 0.005176 | 0.0051761 | 0.0051761 | 0.98413 | -0.1107 | 0.98407 | -0.11114 | 1.9171
100 | 0.0020182 | 0.00050566 | -0.0020182 | -0.0005058 | 7.9602e-08 | -1.4344e-07 | 0.0030515 | 0.0030516 | 0.0030516 | 0.98413 | -0.1107 | 0.98409 | -0.11099 | 1.1302
101 | 0.0041042 | 0.0010281 | -0.0041038 | -0.0010281 | 3.8044e-07 | -4.4551e-08 | 0.0062873 | 0.0062874 | 0.0062874 | 0.97131 | -0.20226 | 0.97122 | -0.20293 | 2.3287
102 | 0.0031544 | 0.00079055 | -0.0031544 | -0.00079056 | 2.1362e-08 | -9.9289e-09 | 0.0048324 | 0.0048324 | 0.0048324 | 0.97131 | -0.20223 | 0.97131 | -0.20228 | 1.7898
103 | 0.00164 | 0.00041062 | -0.0016399 | -0.00041085 | 8.2254e-08 | -2.2675e-07 | 0.0025125 | 0.0025126 | 0.0025126 | 0.97122 | -0.20293 | 0.97117 | -0.20329 | 0.93059
104 | -0.001652 | -0.00041404 | 0.0016521 | 0.00041378 | 9.0745e-08 | -2.5638e-07 | 0.0025083 | 0.0025082 | 0.0025083 | 0.98004 | -0.13974 | 0.98009 | -0.13935 | 0.92901
105 | 0.00080543 | 0.00020177 | -0.00080542 | -0.00020183 | 4.3623e-09 | -5.9858e-08 | 0.0012096 | 0.0012096 | 0.0012096 | 0.9908 | -0.06387 | 0.99079 | -0.063909 | 0.448
106 | 0.00080542 | 0.00020183 | -0.00080542 | -0.00020186 | 2.3264e-09 | -3.192e-08 | 0.0012096 | 0.0012096 | 0.0012096 | 0.99079 | -0.063909 | 0.99079 | -0.06393 | 0.44801
107 | -0.0077159 | -0.0019336 | 0.0077163 | 0.0019337 | 4.1143e-07 | 9.995e-08 | 0.011826 | 0.011826 | 0.011826 | 0.97082 | -0.20557 | 0.97087 | -0.20519 | 4.3802
108 | 0.0045745 | 0.0011463 | -0.0045739 | -0.0011463 | 5.5416e-07 | -1.02e-08 | 0.0070114 | 0.0070115 | 0.0070115 | 0.97082 | -0.20557 | 0.9707 | -0.20645 | 2.5969
109 | -0.010803 | -0.0027074 | 0.010806 | 0.0027082 | 2.8621e-06 | 8.9386e-07 | 0.016558 | 0.016557 | 0.016558 | 0.97087 | -0.20519 | 0.97114 | -0.20328 | 6.1324
110 | 0.0025436 | 0.00063745 | -0.0025436 | -0.00063748 | 2.5247e-08 | -2.3187e-08 | 0.0038991 | 0.0038992 | 0.0038992 | 0.9707 | -0.20645 | 0.97069 | -0.20652 | 1.4441
111 | -0.013513 | -0.0033866 | 0.013519 | 0.0033886 | 5.984e-06 | 2.0246e-06 | 0.020705 | 0.020705 | 0.020705 | 0.97114 | -0.20328 | 0.97158 | -0.20008 | 7.6685
112 | -0.017783 | -0.0044574 | 0.017784 | 0.0044577 | 8.6593e-07 | 3.0988e-07 | 0.027236 | 0.027236 | 0.027236 | 0.97158 | -0.20008 | 0.97163 | -0.19973 | 10.0874
113 | -0.020571 | -0.0051561 | 0.020585 | 0.0051613 | 1.4043e-05 | 5.1199e-06 | 0.031504 | 0.031504 | 0.031504 | 0.97163 | -0.19973 | 0.97231 | -0.1948 | 11.668
114 | 0.010528 | 0.0026383 | -0.010523 | -0.0026368 | 4.9568e-06 | 1.496e-06 | 0.015798 | 0.015798 | 0.015798 | 0.99162 | -0.058207 | 0.99114 | -0.06161 | 5.851
115 | 0.0080721 | 0.0020226 | -0.0080718 | -0.0020225 | 2.7216e-07 | 6.6404e-08 | 0.012119 | 0.012119 | 0.012119 | 0.99114 | -0.06161 | 0.9911 | -0.061854 | 4.4884
116 | 0.0058262 | 0.0014597 | -0.0058245 | -0.0014595 | 1.659e-06 | 1.9042e-07 | 0.0087471 | 0.0087472 | 0.0087472 | 0.9911 | -0.061854 | 0.99081 | -0.063912 | 3.2397
117 | 0.002601 | 0.00065184 | -0.002601 | -0.00065187 | 2.9185e-08 | -2.9664e-08 | 0.0038721 | 0.0038721 | 0.0038721 | 0.99955 | -0.0031241 | 0.99954 | -0.0032052 | 1.4341
118 | -0.025058 | -0.0062823 | 0.025081 | 0.0062908 | 2.306e-05 | 8.5572e-06 | 0.038349 | 0.038349 | 0.038349 | 0.97231 | -0.1948 | 0.97324 | -0.18816 | 14.2033
119 | -0.02878 | -0.007218 | 0.028799 | 0.007225 | 1.8666e-05 | 6.987e-06 | 0.044005 | 0.044005 | 0.044005 | 0.97324 | -0.18816 | 0.97389 | -0.18349 | 16.2981
120 | -0.041265 | -0.010348 | 0.041289 | 0.010358 | 2.3913e-05 | 9.0772e-06 | 0.063052 | 0.063052 | 0.063052 | 0.97389 | -0.18349 | 0.97447 | -0.17931 | 23.3525
121 | 0.0092264 | 0.0023115 | -0.0092195 | -0.0023096 | 6.9021e-06 | 1.9626e-06 | 0.014097 | 0.014097 | 0.014097 | 0.97389 | -0.18349 | 0.97314 | -0.1889 | 5.2211
122 | -0.04446 | -0.011152 | 0.04448 | 0.01116 | 1.9609e-05 | 7.457e-06 | 0.067894 | 0.067894 | 0.067894 | 0.97447 | -0.17931 | 0.97491 | -0.17613 | 25.1459
123 | 0.005796 | 0.0014516 | -0.0057955 | -0.0014515 | 5.2233e-07 | 6.8495e-08 | 0.0088622 | 0.0088623 | 0.0088623 | 0.97314 | -0.1889 | 0.97305 | -0.18955 | 3.2823
124 | -0.046591 | -0.011689 | 0.046634 | 0.011705 | 4.2978e-05 | 1.636e-05 | 0.071117 | 0.071116 | 0.071117 | 0.97491 | -0.17613 | 0.97584 | -0.16949 | 26.3394
125 | -0.0039168 | -0.0009813 | 0.0039172 | 0.00098125 | 3.3222e-07 | -5.5965e-08 | 0.0059946 | 0.0059946 | 0.0059946 | 0.97223 | -0.19542 | 0.97232 | -0.1948 | 2.2202
126 | 0.0019873 | 0.00049772 | -0.0019871 | -0.00049802 | 1.7139e-07 | -3.0223e-07 | 0.0030415 | 0.0030416 | 0.0030416 | 0.97223 | -0.19542 | 0.97215 | -0.19604 | 1.1265
127 | -0.0057912 | -0.0014509 | 0.005794 | 0.0014513 | 2.7981e-06 | 3.6774e-07 | 0.0088626 | 0.0088624 | 0.0088626 | 0.97232 | -0.1948 | 0.9728 | -0.19131 | 3.2825
128 | -0.005794 | -0.0014513 | 0.0057955 | 0.0014515 | 1.4123e-06 | 1.8533e-07 | 0.0088624 | 0.0088623 | 0.0088624 | 0.9728 | -0.19131 | 0.97305 | -0.18955 | 3.2824
129 | 0.0041984 | 0.001052 | -0.0041979 | -0.001052 | 4.7416e-07 | -6.3773e-08 | 0.0063052 | 0.0063052 | 0.0063052 | 0.99081 | -0.063912 | 0.9907 | -0.064728 | 2.3353
130 | -0.050919 | -0.012779 | 0.05096 | 0.012795 | 4.1053e-05 | 1.5653e-05 | 0.07765 | 0.07765 | 0.07765 | 0.97584 | -0.16949 | 0.97665 | -0.16368 | 28.7593
131 | -0.053068 | -0.013323 | 0.053146 | 0.013353 | 7.7754e-05 | 2.9666e-05 | 0.080862 | 0.080862 | 0.080862 | 0.97665 | -0.16368 | 0.97813 | -0.15315 | 29.9489
132 | -0.055896 | -0.014042 | 0.055905 | 0.014046 | 8.9741e-06 | 3.4266e-06 | 0.085046 | 0.085046 | 0.085046 | 0.97813 | -0.15315 | 0.97829 | -0.152 | 31.4986
133 | -0.058032 | -0.014579 | 0.058034 | 0.01458 | 2.7664e-06 | 1.0568e-06 | 0.088281 | 0.088281 | 0.088281 | 0.97829 | -0.152 | 0.97834 | -0.15166 | 32.6965
134 | -0.0026156 | -0.00065546 | 0.0026156 | 0.00065545 | 8.3754e-09 | -7.977e-09 | 0.0039285 | 0.0039285 | 0.0039285 | 0.99069 | -0.064751 | 0.9907 | -0.064728 | 1.455
135 | 0.0010209 | 0.0002558 | -0.0010209 | -0.00025586 | 7.1168e-09 | -5.9719e-08 | 0.0015334 | 0.0015334 | 0.0015334 | 0.99069 | -0.064751 | 0.99069 | -0.064802 | 0.56793

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24146 | 0.06083

## res_load
| p_mw | q_mvar
0 | 0.005632 | 0.0014115
1 | 0.0030038 | 0.00075283
2 | 0.0026702 | 0.0006692
3 | 0.0028379 | 0.00071125
4 | 0.00086974 | 0.00021798
5 | 0.00063141 | 0.00015825
6 | 0.00059547 | 0.00014924
7 | 0.00083682 | 0.00020973
8 | 0.00029818 | 7.473e-05
9 | 0.00074989 | 0.00018794
10 | 0.0017096 | 0.00042848
11 | 0.00025088 | 6.2876e-05
12 | 0.0017492 | 0.00043838
13 | 0.0011015 | 0.00027607
14 | 0.0035164 | 0.0008813
15 | 0.0029538 | 0.0007403
16 | 0.00031734 | 7.9532e-05
17 | 0.0031453 | 0.00078828
18 | 0.0068558 | 0.0017182
19 | 0.0016838 | 0.00042199
20 | 0.0039304 | 0.00098505
21 | 0.00084178 | 0.00021097
22 | 0.0037677 | 0.00094426
23 | 0.0028905 | 0.00072443
24 | 0.0022857 | 0.00057285
25 | 0.0017174 | 0.00043041
26 | 0.0083779 | 0.0020997
27 | 0.0026393 | 0.00066148
28 | 0.0016776 | 0.00042045
29 | 0.0070925 | 0.0017775
30 | 0.00064211 | 0.00016093
31 | 0.0011418 | 0.00028616
32 | 0.0021038 | 0.00052727
33 | 0.0011739 | 0.00029421
34 | 0.00047935 | 0.00012014
35 | 0.00082654 | 0.00020715
36 | 0.00065918 | 0.00016521
37 | 0.00044213 | 0.00011081
38 | 0.0028287 | 0.00070894
39 | 0.0031862 | 0.00079854
40 | 0.0045516 | 0.0011407
41 | 0.0012269 | 0.00030749
42 | 0.0010344 | 0.00025924
43 | 0.00035091 | 8.7946e-05
44 | 0.0003438 | 8.6165e-05
45 | 0.00036317 | 9.1019e-05
46 | 0.0031923 | 0.00080007
47 | 0.00311 | 0.00077943
48 | 0.0025454 | 0.00063794
49 | 0.0021806 | 0.00054652
50 | 0.0034754 | 0.00087102
51 | 0.0034052 | 0.00085343
52 | 0.00098084 | 0.00024582
53 | 0.008792 | 0.0022035
54 | 0.0030646 | 0.00076806
55 | 0.00052007 | 0.00013034
56 | 0.00072104 | 0.00018071
57 | 0.0023399 | 0.00058643
58 | 0.0041401 | 0.0010376
59 | 0.0034231 | 0.00085791
60 | 0.0020182 | 0.0005058
61 | 0.0020694 | 0.00051864
62 | 0.0025514 | 0.00063944
63 | 0.0024639 | 0.0006175
64 | 0.0031544 | 0.00079056
65 | 0.00039876 | 9.9939e-05
66 | 0.0040626 | 0.0010182
67 | 0.001652 | 0.00041404
68 | 0.00080542 | 0.00020186
69 | 0.0031414 | 0.00078731
70 | 0.0030869 | 0.00077365
71 | 0.0020303 | 0.00050885
72 | 0.0027067 | 0.00067837
73 | 0.0025436 | 0.00063748
74 | 0.0042645 | 0.0010688
75 | 0.0027867 | 0.00069841
76 | 0.0016765 | 0.00042016
77 | 0.0024506 | 0.00061419
78 | 0.0022456 | 0.00056281
79 | 0.0018482 | 0.00046319
80 | 0.002601 | 0.00065187
81 | 0.0044729 | 0.001121
82 | 0.0036995 | 0.00092719
83 | 0.0032397 | 0.00081195
84 | 0.0031711 | 0.00079475
85 | 0.0034235 | 0.000858
86 | 0.0021114 | 0.00052917
87 | 0.0019295 | 0.00048358
88 | 0.0018741 | 0.00046969
89 | 0.0019871 | 0.00049802
90 | 0.0016261 | 0.00040754
91 | 0.0042848 | 0.0010739
92 | 0.0021082 | 0.00052837
93 | 0.0027505 | 0.00068934
94 | 0.0021264 | 0.00053292
95 | 0.0030782 | 0.00077146
96 | 0.0015946 | 0.00039966
97 | 0.0015824 | 0.00039658
98 | 0.0010209 | 0.00025586

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1