## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2053-27_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2053-27_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2053-27_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2053-27_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2053-27_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2053-27_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2053-27_0_4_node_111 | 0.4 | n |  | TRUE
7 | bus_LV_2053-27_0_4_node_40 | 0.4 | n |  | TRUE
8 | bus_LV_2053-27_0_4_node_48 | 0.4 | n |  | TRUE
9 | bus_LV_2053-27_0_4_node_110 | 0.4 | n |  | TRUE
10 | bus_LV_2053-27_0_4_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_2053-27_0_4_node_42 | 0.4 | n |  | TRUE
12 | bus_LV_2053-27_0_4_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_2053-27_0_4_node_95 | 0.4 | n |  | TRUE
14 | bus_LV_2053-27_0_4_node_113 | 0.4 | n |  | TRUE
15 | bus_LV_2053-27_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_2053-27_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_2053-27_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_2053-27_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2053-27_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2053-27_0_4_node_107 | 0.4 | n |  | TRUE
21 | bus_LV_2053-27_0_4_node_108 | 0.4 | n |  | TRUE
22 | bus_LV_2053-27_0_4_node_105 | 0.4 | n |  | TRUE
23 | bus_LV_2053-27_0_4_node_131 | 0.4 | n |  | TRUE
24 | bus_LV_2053-27_0_4_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_2053-27_0_4_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_2053-27_0_4_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_2053-27_0_4_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2053-27_0_4_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2053-27_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2053-27_0_4_node_77 | 0.4 | n |  | TRUE
31 | bus_LV_2053-27_0_4_node_84 | 0.4 | n |  | TRUE
32 | bus_LV_2053-27_0_4_node_91 | 0.4 | n |  | TRUE
33 | bus_LV_2053-27_0_4_node_78 | 0.4 | n |  | TRUE
34 | bus_LV_2053-27_0_4_node_76 | 0.4 | n |  | TRUE
35 | bus_LV_2053-27_0_4_node_83 | 0.4 | n |  | TRUE
36 | bus_LV_2053-27_0_4_node_89 | 0.4 | n |  | TRUE
37 | bus_LV_2053-27_0_4_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_2053-27_0_4_node_18 | 0.4 | n |  | TRUE
39 | bus_LV_2053-27_0_4_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_2053-27_0_4_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_2053-27_0_4_node_117 | 0.4 | n |  | TRUE
42 | bus_LV_2053-27_0_4_node_115 | 0.4 | n |  | TRUE
43 | bus_LV_2053-27_0_4_node_94 | 0.4 | n |  | TRUE
44 | bus_LV_2053-27_0_4_node_114 | 0.4 | n |  | TRUE
45 | bus_LV_2053-27_0_4_node_21 | 0.4 | n |  | TRUE
46 | bus_LV_2053-27_0_4_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_2053-27_0_4_node_23 | 0.4 | n |  | TRUE
48 | bus_LV_2053-27_0_4_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_2053-27_0_4_node_52 | 0.4 | n |  | TRUE
50 | bus_LV_2053-27_0_4_node_24 | 0.4 | n |  | TRUE
51 | bus_LV_2053-27_0_4_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_2053-27_0_4_node_139 | 0.4 | n |  | TRUE
53 | bus_LV_2053-27_0_4_node_138 | 0.4 | n |  | TRUE
54 | bus_LV_2053-27_0_4_node_26 | 0.4 | n |  | TRUE
55 | bus_LV_2053-27_0_4_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_2053-27_0_4_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_2053-27_0_4_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_2053-27_0_4_node_129 | 0.4 | n |  | TRUE
59 | bus_LV_2053-27_0_4_node_33 | 0.4 | n |  | TRUE
60 | bus_LV_2053-27_0_4_node_34 | 0.4 | n |  | TRUE
61 | bus_LV_2053-27_0_4_node_30 | 0.4 | n |  | TRUE
62 | bus_LV_2053-27_0_4_node_31 | 0.4 | n |  | TRUE
63 | bus_LV_2053-27_0_4_node_32 | 0.4 | n |  | TRUE
64 | bus_LV_2053-27_0_4_node_136 | 0.4 | n |  | TRUE
65 | bus_LV_2053-27_0_4_node_135 | 0.4 | n |  | TRUE
66 | bus_LV_2053-27_0_4_node_137 | 0.4 | n |  | TRUE
67 | bus_LV_2053-27_0_4_node_69 | 0.4 | n |  | TRUE
68 | bus_LV_2053-27_0_4_node_35 | 0.4 | n |  | TRUE
69 | bus_LV_2053-27_0_4_node_36 | 0.4 | n |  | TRUE
70 | bus_LV_2053-27_0_4_node_132 | 0.4 | n |  | TRUE
71 | bus_LV_2053-27_0_4_node_133 | 0.4 | n |  | TRUE
72 | bus_LV_2053-27_0_4_node_153 | 0.4 | n |  | TRUE
73 | bus_LV_2053-27_0_4_node_130 | 0.4 | n |  | TRUE
74 | bus_LV_2053-27_0_4_node_134 | 0.4 | n |  | TRUE
75 | bus_LV_2053-27_0_4_node_37 | 0.4 | n |  | TRUE
76 | bus_LV_2053-27_0_4_node_38 | 0.4 | n |  | TRUE
77 | bus_LV_2053-27_0_4_node_46 | 0.4 | n |  | TRUE
78 | bus_LV_2053-27_0_4_node_44 | 0.4 | n |  | TRUE
79 | bus_LV_2053-27_0_4_node_96 | 0.4 | n |  | TRUE
80 | bus_LV_2053-27_0_4_node_43 | 0.4 | n |  | TRUE
81 | bus_LV_2053-27_0_4_node_45 | 0.4 | n |  | TRUE
82 | bus_LV_2053-27_0_4_node_47 | 0.4 | n |  | TRUE
83 | bus_LV_2053-27_0_4_node_118 | 0.4 | n |  | TRUE
84 | bus_LV_2053-27_0_4_node_119 | 0.4 | n |  | TRUE
85 | bus_LV_2053-27_0_4_node_120 | 0.4 | n |  | TRUE
86 | bus_LV_2053-27_0_4_node_50 | 0.4 | n |  | TRUE
87 | bus_LV_2053-27_0_4_node_112 | 0.4 | n |  | TRUE
88 | bus_LV_2053-27_0_4_node_53 | 0.4 | n |  | TRUE
89 | bus_LV_2053-27_0_4_node_54 | 0.4 | n |  | TRUE
90 | bus_LV_2053-27_0_4_node_55 | 0.4 | n |  | TRUE
91 | bus_LV_2053-27_0_4_node_56 | 0.4 | n |  | TRUE
92 | bus_LV_2053-27_0_4_node_57 | 0.4 | n |  | TRUE
93 | bus_LV_2053-27_0_4_node_62 | 0.4 | n |  | TRUE
94 | bus_LV_2053-27_0_4_node_142 | 0.4 | n |  | TRUE
95 | bus_LV_2053-27_0_4_node_58 | 0.4 | n |  | TRUE
96 | bus_LV_2053-27_0_4_node_61 | 0.4 | n |  | TRUE
97 | bus_LV_2053-27_0_4_node_140 | 0.4 | n |  | TRUE
98 | bus_LV_2053-27_0_4_node_59 | 0.4 | n |  | TRUE
99 | bus_LV_2053-27_0_4_node_60 | 0.4 | n |  | TRUE
100 | bus_LV_2053-27_0_4_node_63 | 0.4 | n |  | TRUE
101 | bus_LV_2053-27_0_4_node_64 | 0.4 | n |  | TRUE
102 | bus_LV_2053-27_0_4_node_65 | 0.4 | n |  | TRUE
103 | bus_LV_2053-27_0_4_node_66 | 0.4 | n |  | TRUE
104 | bus_LV_2053-27_0_4_node_67 | 0.4 | n |  | TRUE
105 | bus_LV_2053-27_0_4_node_70 | 0.4 | n |  | TRUE
106 | bus_LV_2053-27_0_4_node_68 | 0.4 | n |  | TRUE
107 | bus_LV_2053-27_0_4_node_71 | 0.4 | n |  | TRUE
108 | bus_LV_2053-27_0_4_node_73 | 0.4 | n |  | TRUE
109 | bus_LV_2053-27_0_4_node_72 | 0.4 | n |  | TRUE
110 | bus_LV_2053-27_0_4_node_74 | 0.4 | n |  | TRUE
111 | bus_LV_2053-27_0_4_node_75 | 0.4 | n |  | TRUE
112 | bus_LV_2053-27_0_4_node_79 | 0.4 | n |  | TRUE
113 | bus_LV_2053-27_0_4_node_80 | 0.4 | n |  | TRUE
114 | bus_LV_2053-27_0_4_node_81 | 0.4 | n |  | TRUE
115 | bus_LV_2053-27_0_4_node_85 | 0.4 | n |  | TRUE
116 | bus_LV_2053-27_0_4_node_86 | 0.4 | n |  | TRUE
117 | bus_LV_2053-27_0_4_node_87 | 0.4 | n |  | TRUE
118 | bus_LV_2053-27_0_4_node_88 | 0.4 | n |  | TRUE
119 | bus_LV_2053-27_0_4_node_90 | 0.4 | n |  | TRUE
120 | bus_LV_2053-27_0_4_node_98 | 0.4 | n |  | TRUE
121 | bus_LV_2053-27_0_4_node_97 | 0.4 | n |  | TRUE
122 | bus_LV_2053-27_0_4_node_92 | 0.4 | n |  | TRUE
123 | bus_LV_2053-27_0_4_node_93 | 0.4 | n |  | TRUE
124 | bus_LV_2053-27_0_4_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_2053-27_0_4_node_99 | 0.4 | n |  | TRUE
126 | bus_LV_2053-27_0_4_node_100 | 0.4 | n |  | TRUE
127 | bus_LV_2053-27_0_4_node_101 | 0.4 | n |  | TRUE
128 | bus_LV_2053-27_0_4_node_102 | 0.4 | n |  | TRUE
129 | bus_LV_2053-27_0_4_node_106 | 0.4 | n |  | TRUE
130 | bus_LV_2053-27_0_4_node_103 | 0.4 | n |  | TRUE
131 | bus_LV_2053-27_0_4_node_104 | 0.4 | n |  | TRUE
132 | bus_LV_2053-27_0_4_node_121 | 0.4 | n |  | TRUE
133 | bus_LV_2053-27_0_4_node_122 | 0.4 | n |  | TRUE
134 | bus_LV_2053-27_0_4_node_123 | 0.4 | n |  | TRUE
135 | bus_LV_2053-27_0_4_node_124 | 0.4 | n |  | TRUE
136 | bus_LV_2053-27_0_4_node_125 | 0.4 | n |  | TRUE
137 | bus_LV_2053-27_0_4_node_126 | 0.4 | n |  | TRUE
138 | bus_LV_2053-27_0_4_node_127 | 0.4 | n |  | TRUE
139 | bus_LV_2053-27_0_4_node_128 | 0.4 | n |  | TRUE
140 | bus_LV_2053-27_0_4_node_146 | 0.4 | n |  | TRUE
141 | bus_LV_2053-27_0_4_node_147 | 0.4 | n |  | TRUE
142 | bus_LV_2053-27_0_4_node_148 | 0.4 | n |  | TRUE
143 | bus_LV_2053-27_0_4_node_141 | 0.4 | n |  | TRUE
144 | bus_LV_2053-27_0_4_node_143 | 0.4 | n |  | TRUE
145 | bus_LV_2053-27_0_4_node_144 | 0.4 | n |  | TRUE
146 | bus_LV_2053-27_0_4_node_145 | 0.4 | n |  | TRUE
147 | bus_LV_2053-27_0_4_node_149 | 0.4 | n |  | TRUE
148 | bus_LV_2053-27_0_4_node_152 | 0.4 | n |  | TRUE
149 | bus_MV_377_1_node_88 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2053-27_0_4_load_0 | 0 | 0.0066843 | 0.0016752 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2053-27_0_4_load_1 | 1 | 0.0046622 | 0.0011685 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2053-27_0_4_load_2 | 2 | 0.0044079 | 0.0011047 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2053-27_0_4_load_4 | 4 | 0.003437 | 0.0008614 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2053-27_0_4_load_5 | 5 | 0.0022789 | 0.00057114 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2053-27_0_4_load_111 | 6 | 0.0017512 | 0.0004389 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2053-27_0_4_load_48 | 8 | 0.00053809 | 0.00013486 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2053-27_0_4_load_110 | 9 | 0.0052506 | 0.0013159 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2053-27_0_4_load_41 | 10 | 0.0018376 | 0.00046055 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2053-27_0_4_load_39 | 12 | 0.001726 | 0.00043258 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2053-27_0_4_load_113 | 14 | 0.0028455 | 0.00071316 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2053-27_0_4_load_6 | 15 | 0.0014457 | 0.00036233 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2053-27_0_4_load_7 | 16 | 0.00057417 | 0.0001439 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2053-27_0_4_load_8 | 17 | 0.00084267 | 0.00021119 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2053-27_0_4_load_9 | 18 | 0.0014079 | 0.00035286 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2053-27_0_4_load_107 | 20 | 0.0010326 | 0.00025879 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2053-27_0_4_load_108 | 21 | 0.00089528 | 0.00022438 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2053-27_0_4_load_105 | 22 | 0.00061791 | 0.00015486 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2053-27_0_4_load_131 | 23 | 0.0022409 | 0.00056163 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2053-27_0_4_load_11 | 24 | 0.00069753 | 0.00017482 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2053-27_0_4_load_12 | 25 | 0.00090276 | 0.00022625 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2053-27_0_4_load_14 | 27 | 0.001027 | 0.00025739 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2053-27_0_4_load_16 | 29 | 0.00028721 | 7.198e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2053-27_0_4_load_84 | 31 | 0.0018048 | 0.00045231 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2053-27_0_4_load_91 | 32 | 0.00069795 | 0.00017492 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2053-27_0_4_load_78 | 33 | 0.00092725 | 0.00023239 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2053-27_0_4_load_76 | 34 | 0.0014727 | 0.0003691 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2053-27_0_4_load_83 | 35 | 0.0013269 | 0.00033256 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2053-27_0_4_load_89 | 36 | 0.00084969 | 0.00021295 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2053-27_0_4_load_17 | 37 | 0.0010752 | 0.00026947 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2053-27_0_4_load_19 | 39 | 0.00093789 | 0.00023506 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2053-27_0_4_load_117 | 41 | 0.0049718 | 0.0012461 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2053-27_0_4_load_115 | 42 | 0.002492 | 0.00062455 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2053-27_0_4_load_94 | 43 | 0.0011239 | 0.00028169 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2053-27_0_4_load_114 | 44 | 0.0010359 | 0.00025963 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2053-27_0_4_load_21 | 45 | 0.0011262 | 0.00028226 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2053-27_0_4_load_22 | 46 | 0.00046617 | 0.00011683 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2053-27_0_4_load_23 | 47 | 0.0028531 | 0.00071507 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2053-27_0_4_load_51 | 48 | 0.0031076 | 0.00077884 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2053-27_0_4_load_52 | 49 | 0.0098975 | 0.0024806 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2053-27_0_4_load_24 | 50 | 0.0018315 | 0.00045901 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2053-27_0_4_load_25 | 51 | 0.00066441 | 0.00016652 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2053-27_0_4_load_139 | 52 | 0.00059787 | 0.00014984 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2053-27_0_4_load_138 | 53 | 0.00075953 | 0.00019036 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2053-27_0_4_load_26 | 54 | 0.001918 | 0.00048069 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2053-27_0_4_load_28 | 56 | 0.00095569 | 0.00023952 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2053-27_0_4_load_29 | 57 | 0.0010383 | 0.00026022 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2053-27_0_4_load_129 | 58 | 0.001306 | 0.00032733 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2053-27_0_4_load_33 | 59 | 0.0033604 | 0.00084218 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2053-27_0_4_load_31 | 62 | 0.00062165 | 0.0001558 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2053-27_0_4_load_32 | 63 | 0.0008364 | 0.00020962 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2053-27_0_4_load_136 | 64 | 0.001095 | 0.00027443 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2053-27_0_4_load_135 | 65 | 0.00062654 | 0.00015702 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2053-27_0_4_load_137 | 66 | 0.00060655 | 0.00015202 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2053-27_0_4_load_69 | 67 | 0.00079662 | 0.00019965 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2053-27_0_4_load_35 | 68 | 0.0012119 | 0.00030373 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2053-27_0_4_load_36 | 69 | 0.0021767 | 0.00054552 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2053-27_0_4_load_132 | 70 | 0.0018903 | 0.00047375 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2053-27_0_4_load_133 | 71 | 0.001016 | 0.00025463 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2053-27_0_4_load_153 | 72 | 0.00067818 | 0.00016997 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2053-27_0_4_load_130 | 73 | 0.0012655 | 0.00031716 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2053-27_0_4_load_134 | 74 | 0.0038762 | 0.00097146 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2053-27_0_4_load_37 | 75 | 0.0023781 | 0.000596 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2053-27_0_4_load_38 | 76 | 0.001246 | 0.00031227 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2053-27_0_4_load_46 | 77 | 0.00073871 | 0.00018514 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2053-27_0_4_load_44 | 78 | 0.0015405 | 0.00038607 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2053-27_0_4_load_96 | 79 | 0.0015876 | 0.00039788 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2053-27_0_4_load_43 | 80 | 0.0038928 | 0.00097564 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2053-27_0_4_load_45 | 81 | 0.001051 | 0.00026341 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2053-27_0_4_load_47 | 82 | 0.0012689 | 0.00031802 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2053-27_0_4_load_119 | 84 | 0.00081525 | 0.00020432 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2053-27_0_4_load_120 | 85 | 0.00094415 | 0.00023663 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2053-27_0_4_load_50 | 86 | 0.00069002 | 0.00017294 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2053-27_0_4_load_112 | 87 | 0.0014076 | 0.00035278 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2053-27_0_4_load_53 | 88 | 0.0020414 | 0.00051162 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2053-27_0_4_load_54 | 89 | 0.0017933 | 0.00044944 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2053-27_0_4_load_57 | 92 | 0.00088337 | 0.00022139 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2053-27_0_4_load_62 | 93 | 0.0011869 | 0.00029745 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2053-27_0_4_load_58 | 95 | 0.00063657 | 0.00015954 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2053-27_0_4_load_61 | 96 | 0.00069634 | 0.00017452 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2053-27_0_4_load_140 | 97 | 0.00093222 | 0.00023364 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2053-27_0_4_load_59 | 98 | 0.0015482 | 0.00038802 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2053-27_0_4_load_60 | 99 | 0.00037223 | 9.3289e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2053-27_0_4_load_63 | 100 | 0.0022815 | 0.00057179 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2053-27_0_4_load_65 | 102 | 0.0014314 | 0.00035875 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2053-27_0_4_load_66 | 103 | 0.0012298 | 0.00030821 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2053-27_0_4_load_70 | 105 | 0.000885 | 0.0002218 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2053-27_0_4_load_71 | 107 | 0.0017033 | 0.00042688 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2053-27_0_4_load_73 | 108 | 0.0013666 | 0.0003425 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2053-27_0_4_load_72 | 109 | 0.001381 | 0.0003461 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2053-27_0_4_load_74 | 110 | 0.0011037 | 0.0002766 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2053-27_0_4_load_75 | 111 | 0.00060335 | 0.00015121 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2053-27_0_4_load_79 | 112 | 0.00058603 | 0.00014687 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2053-27_0_4_load_80 | 113 | 0.0010403 | 0.00026073 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2053-27_0_4_load_81 | 114 | 0.0011262 | 0.00028225 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2053-27_0_4_load_85 | 115 | 0.0022871 | 0.0005732 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2053-27_0_4_load_86 | 116 | 0.0012184 | 0.00030536 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2053-27_0_4_load_87 | 117 | 0.00084133 | 0.00021086 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2053-27_0_4_load_88 | 118 | 0.0002586 | 6.4812e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2053-27_0_4_load_90 | 119 | 0.00021919 | 5.4935e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2053-27_0_4_load_98 | 120 | 0.0014593 | 0.00036574 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2053-27_0_4_load_97 | 121 | 0.0016196 | 0.00040591 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2053-27_0_4_load_92 | 122 | 0.00080444 | 0.00020161 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2053-27_0_4_load_93 | 123 | 0.00072159 | 0.00018085 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2053-27_0_4_load_116 | 124 | 0.00077594 | 0.00019447 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2053-27_0_4_load_99 | 125 | 0.00046517 | 0.00011658 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2053-27_0_4_load_100 | 126 | 0.0017555 | 0.00043996 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2053-27_0_4_load_101 | 127 | 0.0031695 | 0.00079435 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2053-27_0_4_load_106 | 129 | 0.0022591 | 0.00056618 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2053-27_0_4_load_103 | 130 | 0.00021766 | 5.455e-05 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2053-27_0_4_load_104 | 131 | 0.00077635 | 0.00019457 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2053-27_0_4_load_121 | 132 | 0.00069095 | 0.00017317 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2053-27_0_4_load_122 | 133 | 0.0012381 | 0.00031031 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2053-27_0_4_load_123 | 134 | 0.001588 | 0.00039799 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2053-27_0_4_load_124 | 135 | 0.0010767 | 0.00026985 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2053-27_0_4_load_127 | 138 | 0.0017888 | 0.00044831 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2053-27_0_4_load_128 | 139 | 0.0022729 | 0.00056964 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2053-27_0_4_load_147 | 141 | 0.0011313 | 0.00028354 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2053-27_0_4_load_141 | 143 | 0.0009327 | 0.00023376 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2053-27_0_4_load_143 | 144 | 0.0011944 | 0.00029934 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2053-27_0_4_load_144 | 145 | 0.0010439 | 0.00026162 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2053-27_0_4_load_145 | 146 | 0.0014148 | 0.00035457 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2053-27_0_4_load_149 | 147 | 0.0003547 | 8.8896e-05 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2053-27_0_4_load_152 | 148 | 0.0084462 | 0.0021168 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2053-27_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.00050469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_2053-27_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.028296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_2053-27_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.030773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_2053-27_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.028476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_2053-27_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.02576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2053-27_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.022483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_2053-27_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.029544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_2053-27_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0012858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2053-27_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.020501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_2053-27_0_4_line_9 | NAYY 4x150 SE | 7 | 10 | 0.014167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_2053-27_0_4_line_10 | NAYY 4x150 SE | 7 | 11 | 0.036818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2053-27_0_4_line_11 | NAYY 4x150 SE | 7 | 12 | 0.041853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2053-27_0_4_line_12 | NAYY 4x150 SE | 9 | 87 | 0.019367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2053-27_0_4_line_13 | NAYY 4x150 SE | 9 | 129 | 0.018982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_2053-27_0_4_line_14 | NAYY 4x150 SE | 10 | 77 | 0.0044281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_2053-27_0_4_line_15 | NAYY 4x150 SE | 11 | 13 | 0.007134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2053-27_0_4_line_16 | NAYY 4x150 SE | 11 | 14 | 0.031426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2053-27_0_4_line_17 | NAYY 4x150 SE | 12 | 76 | 0.0054715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2053-27_0_4_line_18 | NAYY 4x150 SE | 13 | 79 | 0.028939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2053-27_0_4_line_19 | NAYY 4x150 SE | 15 | 16 | 0.01672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2053-27_0_4_line_20 | NAYY 4x150 SE | 15 | 17 | 6.0409e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2053-27_0_4_line_21 | NAYY 4x150 SE | 16 | 18 | 0.0078234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2053-27_0_4_line_22 | NAYY 4x150 SE | 17 | 19 | 0.048728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2053-27_0_4_line_23 | NAYY 4x150 SE | 18 | 20 | 0.0014677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2053-27_0_4_line_24 | NAYY 4x150 SE | 19 | 21 | 0.05897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2053-27_0_4_line_25 | NAYY 4x150 SE | 20 | 22 | 0.01426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2053-27_0_4_line_26 | NAYY 4x150 SE | 21 | 23 | 0.01867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2053-27_0_4_line_27 | NAYY 4x150 SE | 22 | 131 | 0.0006277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2053-27_0_4_line_28 | NAYY 4x150 SE | 23 | 73 | 0.026247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2053-27_0_4_line_29 | NAYY 4x150 SE | 24 | 25 | 0.0039119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2053-27_0_4_line_30 | NAYY 4x150 SE | 24 | 26 | 0.016294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2053-27_0_4_line_31 | NAYY 4x150 SE | 25 | 27 | 0.035045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2053-27_0_4_line_32 | NAYY 4x150 SE | 26 | 28 | 0.020739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2053-27_0_4_line_33 | NAYY 4x150 SE | 26 | 29 | 0.030117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2053-27_0_4_line_34 | NAYY 4x150 SE | 28 | 30 | 0.011091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2053-27_0_4_line_35 | NAYY 4x150 SE | 28 | 31 | 0.018478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2053-27_0_4_line_36 | NAYY 4x150 SE | 29 | 32 | 0.0056593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_2053-27_0_4_line_37 | NAYY 4x150 SE | 30 | 33 | 0.016878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2053-27_0_4_line_38 | NAYY 4x150 SE | 30 | 34 | 0.054593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2053-27_0_4_line_39 | NAYY 4x150 SE | 31 | 35 | 0.0099392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2053-27_0_4_line_40 | NAYY 4x150 SE | 32 | 36 | 0.007022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_2053-27_0_4_line_41 | NAYY 4x150 SE | 33 | 113 | 0.017627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2053-27_0_4_line_42 | NAYY 4x150 SE | 34 | 106 | 0.015281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2053-27_0_4_line_43 | NAYY 4x150 SE | 35 | 115 | 0.014129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2053-27_0_4_line_44 | NAYY 4x150 SE | 36 | 117 | 0.017543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_2053-27_0_4_line_45 | NAYY 4x150 SE | 37 | 38 | 0.033678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2053-27_0_4_line_46 | NAYY 4x150 SE | 37 | 39 | 0.0087447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2053-27_0_4_line_47 | NAYY 4x150 SE | 38 | 40 | 0.074248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2053-27_0_4_line_48 | NAYY 4x150 SE | 40 | 41 | 0.011686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2053-27_0_4_line_49 | NAYY 4x150 SE | 40 | 42 | 0.041437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2053-27_0_4_line_50 | NAYY 4x150 SE | 41 | 43 | 0.037036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2053-27_0_4_line_51 | NAYY 4x150 SE | 42 | 44 | 0.0089103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2053-27_0_4_line_52 | NAYY 4x150 SE | 43 | 123 | 0.0062352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2053-27_0_4_line_53 | NAYY 4x150 SE | 44 | 124 | 0.00039514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2053-27_0_4_line_54 | NAYY 4x150 SE | 45 | 46 | 0.012943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2053-27_0_4_line_55 | NAYY 4x150 SE | 46 | 47 | 0.044878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2053-27_0_4_line_56 | NAYY 4x150 SE | 47 | 50 | 0.031939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2053-27_0_4_line_57 | NAYY 4x150 SE | 48 | 49 | 0.069336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2053-27_0_4_line_58 | NAYY 4x150 SE | 49 | 88 | 0.012457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2053-27_0_4_line_59 | NAYY 4x150 SE | 50 | 51 | 0.02134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2053-27_0_4_line_60 | NAYY 4x150 SE | 51 | 54 | 0.064561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2053-27_0_4_line_61 | NAYY 4x150 SE | 52 | 53 | 0.0023777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2053-27_0_4_line_62 | NAYY 4x150 SE | 53 | 66 | 0.020435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2053-27_0_4_line_63 | NAYY 4x150 SE | 54 | 55 | 0.08955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2053-27_0_4_line_64 | NAYY 4x150 SE | 55 | 56 | 0.020432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2053-27_0_4_line_65 | NAYY 4x150 SE | 55 | 57 | 0.046947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2053-27_0_4_line_66 | NAYY 4x150 SE | 55 | 58 | 0.097102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2053-27_0_4_line_67 | NAYY 4x150 SE | 57 | 59 | 0.040624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2053-27_0_4_line_68 | NAYY 4x150 SE | 59 | 60 | 0.024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2053-27_0_4_line_69 | NAYY 4x150 SE | 60 | 68 | 0.028129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2053-27_0_4_line_70 | NAYY 4x150 SE | 60 | 69 | 0.01356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2053-27_0_4_line_71 | NAYY 4x150 SE | 61 | 62 | 0.053809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2053-27_0_4_line_72 | NAYY 4x150 SE | 61 | 63 | 0.020203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2053-27_0_4_line_73 | NAYY 4x150 SE | 62 | 64 | 0.025869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2053-27_0_4_line_74 | NAYY 4x150 SE | 63 | 65 | 0.022938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2053-27_0_4_line_75 | NAYY 4x150 SE | 64 | 66 | 0.0090805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2053-27_0_4_line_76 | NAYY 4x150 SE | 65 | 67 | 0.00042401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2053-27_0_4_line_77 | NAYY 4x150 SE | 67 | 104 | 0.037333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2053-27_0_4_line_78 | NAYY 4x150 SE | 68 | 70 | 0.033458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2053-27_0_4_line_79 | NAYY 4x150 SE | 69 | 71 | 0.011973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2053-27_0_4_line_80 | NAYY 4x150 SE | 70 | 72 | 0.036339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2053-27_0_4_line_81 | NAYY 4x150 SE | 70 | 73 | 0.017497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2053-27_0_4_line_82 | NAYY 4x150 SE | 71 | 74 | 0.06452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2053-27_0_4_line_83 | NAYY 4x150 SE | 75 | 76 | 0.0085733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2053-27_0_4_line_84 | NAYY 4x150 SE | 77 | 78 | 0.011977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_2053-27_0_4_line_85 | NAYY 4x150 SE | 78 | 80 | 0.006924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_2053-27_0_4_line_86 | NAYY 4x150 SE | 79 | 124 | 0.010764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2053-27_0_4_line_87 | NAYY 4x150 SE | 80 | 81 | 0.0794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_2053-27_0_4_line_88 | NAYY 4x150 SE | 81 | 82 | 0.027565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2053-27_0_4_line_89 | NAYY 4x150 SE | 82 | 83 | 0.042487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2053-27_0_4_line_90 | NAYY 4x150 SE | 83 | 84 | 0.064336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2053-27_0_4_line_91 | NAYY 4x150 SE | 83 | 85 | 0.014408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2053-27_0_4_line_92 | NAYY 4x150 SE | 85 | 132 | 0.007803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2053-27_0_4_line_93 | NAYY 4x150 SE | 86 | 87 | 0.022705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2053-27_0_4_line_94 | NAYY 4x150 SE | 88 | 89 | 0.015622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2053-27_0_4_line_95 | NAYY 4x150 SE | 89 | 90 | 0.02944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2053-27_0_4_line_96 | NAYY 4x150 SE | 90 | 91 | 0.066499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2053-27_0_4_line_97 | NAYY 4x150 SE | 90 | 92 | 0.013499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2053-27_0_4_line_98 | NAYY 4x150 SE | 91 | 93 | 0.018454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2053-27_0_4_line_99 | NAYY 4x150 SE | 91 | 94 | 0.041084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2053-27_0_4_line_100 | NAYY 4x150 SE | 92 | 95 | 0.034295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2053-27_0_4_line_101 | NAYY 4x150 SE | 93 | 96 | 0.0044906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2053-27_0_4_line_102 | NAYY 4x150 SE | 94 | 97 | 0.012455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2053-27_0_4_line_103 | NAYY 4x150 SE | 95 | 98 | 0.01906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2053-27_0_4_line_104 | NAYY 4x150 SE | 95 | 99 | 0.0098449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2053-27_0_4_line_105 | NAYY 4x150 SE | 97 | 143 | 0.021444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2053-27_0_4_line_106 | NAYY 4x150 SE | 98 | 100 | 0.013493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2053-27_0_4_line_107 | NAYY 4x150 SE | 99 | 101 | 0.02086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2053-27_0_4_line_108 | NAYY 4x150 SE | 101 | 102 | 0.010564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2053-27_0_4_line_109 | NAYY 4x150 SE | 101 | 103 | 0.022112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2053-27_0_4_line_110 | NAYY 4x150 SE | 102 | 104 | 0.020609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2053-27_0_4_line_111 | NAYY 4x150 SE | 103 | 105 | 0.0018492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2053-27_0_4_line_112 | NAYY 4x150 SE | 104 | 106 | 0.026887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2053-27_0_4_line_113 | NAYY 4x150 SE | 105 | 107 | 0.027738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2053-27_0_4_line_114 | NAYY 4x150 SE | 106 | 108 | 0.020032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2053-27_0_4_line_115 | NAYY 4x150 SE | 108 | 109 | 0.0029929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2053-27_0_4_line_116 | NAYY 4x150 SE | 109 | 110 | 0.015287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2053-27_0_4_line_117 | NAYY 4x150 SE | 110 | 111 | 0.012076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2053-27_0_4_line_118 | NAYY 4x150 SE | 111 | 112 | 0.005014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2053-27_0_4_line_119 | NAYY 4x150 SE | 113 | 114 | 0.011766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2053-27_0_4_line_120 | NAYY 4x150 SE | 116 | 117 | 0.012222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
121 | LV_2053-27_0_4_line_121 | NAYY 4x150 SE | 116 | 118 | 0.0066799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
122 | LV_2053-27_0_4_line_122 | NAYY 4x150 SE | 118 | 119 | 0.0087616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
123 | LV_2053-27_0_4_line_123 | NAYY 4x150 SE | 119 | 120 | 0.012898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
124 | LV_2053-27_0_4_line_124 | NAYY 4x150 SE | 120 | 121 | 0.0030938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
125 | LV_2053-27_0_4_line_125 | NAYY 4x150 SE | 121 | 125 | 0.021615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
126 | LV_2053-27_0_4_line_126 | NAYY 4x150 SE | 122 | 123 | 0.0074382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_2053-27_0_4_line_127 | NAYY 4x150 SE | 125 | 126 | 0.018257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
128 | LV_2053-27_0_4_line_128 | NAYY 4x150 SE | 126 | 127 | 0.0014999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
129 | LV_2053-27_0_4_line_129 | NAYY 4x150 SE | 127 | 128 | 0.028244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
130 | LV_2053-27_0_4_line_130 | NAYY 4x150 SE | 128 | 129 | 0.020793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
131 | LV_2053-27_0_4_line_131 | NAYY 4x150 SE | 128 | 130 | 0.031089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_2053-27_0_4_line_132 | NAYY 4x150 SE | 130 | 131 | 0.021814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_2053-27_0_4_line_133 | NAYY 4x150 SE | 132 | 133 | 0.0071025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_2053-27_0_4_line_134 | NAYY 4x150 SE | 133 | 134 | 0.011043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_2053-27_0_4_line_135 | NAYY 4x150 SE | 134 | 135 | 0.0013822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_2053-27_0_4_line_136 | NAYY 4x150 SE | 135 | 136 | 0.027817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_2053-27_0_4_line_137 | NAYY 4x150 SE | 136 | 137 | 0.027631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_2053-27_0_4_line_138 | NAYY 4x150 SE | 136 | 138 | 0.074605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_2053-27_0_4_line_139 | NAYY 4x150 SE | 137 | 139 | 0.02348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_2053-27_0_4_line_140 | NAYY 4x150 SE | 138 | 140 | 0.065096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_2053-27_0_4_line_141 | NAYY 4x150 SE | 140 | 141 | 0.045005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_2053-27_0_4_line_142 | NAYY 4x150 SE | 140 | 142 | 0.038944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_2053-27_0_4_line_143 | NAYY 4x150 SE | 142 | 147 | 0.0498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_2053-27_0_4_line_144 | NAYY 4x150 SE | 142 | 148 | 0.15607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_2053-27_0_4_line_145 | NAYY 4x150 SE | 143 | 144 | 0.011099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_2053-27_0_4_line_146 | NAYY 4x150 SE | 144 | 145 | 0.047223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_2053-27_0_4_line_147 | NAYY 4x150 SE | 145 | 146 | 0.069039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2053-27_0_4_trafo_16 | 0.25 MVA 20/0.4 kV | 149 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2565690.2553 | 1189178.9533 | 2565689.8383 | 1189178.669
1 | 2565703.6112 | 1189202.1087 | 2565698.6912 | 1189184.7054 | 2565690.2553 | 1189178.9533
2 | 2565664.45 | 1189161.2785 | 2565670.2542 | 1189165.314 | 2565672.758 | 1189167.0227 | 2565689.8383 | 1189178.669
3 | 2565703.6112 | 1189202.1087 | 2565677.8968 | 1189207.8595 | 2565675.8212 | 1189208.3224
4 | 2565703.6112 | 1189202.1087 | 2565728.5338 | 1189195.5936
5 | 2565664.45 | 1189161.2785 | 2565677.609 | 1189143.0491
6 | 2565646.9878 | 1189214.7633 | 2565658.6034 | 1189212.1617 | 2565675.8212 | 1189208.3224
7 | 2565729.7779 | 1189195.2684 | 2565728.5338 | 1189195.5936
8 | 2565689.6083 | 1189126.4262 | 2565677.609 | 1189143.0491
9 | 2565646.9878 | 1189214.7633 | 2565635.0286 | 1189222.3574
10 | 2565634.1651 | 1189189.19 | 2565644.7247 | 1189188.6178 | 2565646.9878 | 1189214.7633
11 | 2565646.9878 | 1189214.7633 | 2565644.1462 | 1189223.2508 | 2565647.2195 | 1189245.7452 | 2565651.2346 | 1189255.1211
12 | 2565689.6083 | 1189126.4262 | 2565706.2792 | 1189136.2825
13 | 2565689.6083 | 1189126.4262 | 2565673.3332 | 1189116.6569
14 | 2565631.2904 | 1189224.7311 | 2565635.0286 | 1189222.3574
15 | 2565627.0123 | 1189189.3757 | 2565634.1651 | 1189189.19
16 | 2565634.1651 | 1189189.19 | 2565620.0448 | 1189175.3638 | 2565618.0033 | 1189163.8805
17 | 2565653.3885 | 1189260.1508 | 2565653.3885 | 1189260.1508 | 2565651.2346 | 1189255.1211
18 | 2565627.0123 | 1189189.3757 | 2565601.8969 | 1189187.8862 | 2565598.1183 | 1189187.9557
19 | 2565708.5828 | 1189028.6143 | 2565699.1218 | 1189042.4005
20 | 2565708.5828 | 1189028.6143 | 2565708.617 | 1189028.5645
21 | 2565699.1218 | 1189042.4005 | 2565694.695 | 1189048.851
22 | 2565737.1658 | 1188989.146 | 2565730.278 | 1188997.0009 | 2565708.617 | 1189028.5645
23 | 2565693.8645 | 1189050.0611 | 2565694.695 | 1189048.851
24 | 2565737.1658 | 1188989.146 | 2565709.5696 | 1188962.2456 | 2565695.1723 | 1188947.748
25 | 2565693.8645 | 1189050.0611 | 2565685.7956 | 1189061.8187
26 | 2565682.0169 | 1188934.5009 | 2565695.1723 | 1188947.748
27 | 2565685.4405 | 1189062.3363 | 2565685.7956 | 1189061.8187
28 | 2565663.5217 | 1188915.8769 | 2565682.0169 | 1188934.5009
29 | 2565495.2473 | 1189030.7804 | 2565492.7182 | 1189033.7647
30 | 2565505.7821 | 1189018.3497 | 2565495.2473 | 1189030.7804
31 | 2565492.7182 | 1189033.7647 | 2565471.6788 | 1189058.5907 | 2565470.0612 | 1189060.5001
32 | 2565505.7821 | 1189018.3497 | 2565487.5495 | 1189008.3719
33 | 2565505.7821 | 1189018.3497 | 2565532.1297 | 1189032.9389
34 | 2565477.8548 | 1189002.9362 | 2565487.5495 | 1189008.3719
35 | 2565487.5495 | 1189008.3719 | 2565491.9639 | 1188990.4287
36 | 2565532.1297 | 1189032.9389 | 2565535.2091 | 1189034.644 | 2565537.0027 | 1189035.8101
37 | 2565477.8548 | 1189002.9362 | 2565467.5776 | 1189016.3249
38 | 2565477.8548 | 1189002.9362 | 2565434.0879 | 1188970.3048
39 | 2565494.3384 | 1188980.7773 | 2565491.9639 | 1188990.4287
40 | 2565542.89 | 1189039.6373 | 2565537.0027 | 1189035.8101
41 | 2565467.5776 | 1189016.3249 | 2565456.8446 | 1189030.3075
42 | 2565421.8374 | 1188961.1712 | 2565434.0879 | 1188970.3048
43 | 2565497.7137 | 1188967.0576 | 2565494.3384 | 1188980.7773
44 | 2565542.89 | 1189039.6373 | 2565557.5982 | 1189049.1988
45 | 2565464.22 | 1189174.5962 | 2565443.4326 | 1189148.0988
46 | 2565438.0351 | 1189141.2186 | 2565443.4326 | 1189148.0988
47 | 2565536.8827 | 1189184.4371 | 2565501.2904 | 1189176.7385 | 2565491.7673 | 1189174.5479 | 2565479.9932 | 1189172.1703 | 2565471.4956 | 1189171.9193 | 2565464.22 | 1189174.5962
48 | 2565536.8827 | 1189184.4371 | 2565532.1039 | 1189173.7728
49 | 2565536.8827 | 1189184.4371 | 2565555.6609 | 1189187.3303 | 2565570.1963 | 1189188.4693 | 2565578.0518 | 1189188.3248
50 | 2565532.1039 | 1189173.7728 | 2565535.3114 | 1189136.8762
51 | 2565586.9606 | 1189188.1609 | 2565578.0518 | 1189188.3248
52 | 2565535.3114 | 1189136.8762 | 2565539.6678 | 1189132.4152
53 | 2565587.3557 | 1189188.1537 | 2565586.9606 | 1189188.1609
54 | 2565340.4349 | 1188594.2779 | 2565349.6098 | 1188603.4077
55 | 2565349.6098 | 1188603.4077 | 2565360.8849 | 1188614.6273 | 2565381.4251 | 1188635.0598
56 | 2565381.4251 | 1188635.0598 | 2565404.0684 | 1188657.5843
57 | 2565227.7069 | 1188783.8315 | 2565277.7584 | 1188821.1544 | 2565282.9086 | 1188825.7474
58 | 2565282.9086 | 1188825.7474 | 2565292.2059 | 1188834.0388
59 | 2565404.0684 | 1188657.5843 | 2565418.2838 | 1188671.7252 | 2565419.2012 | 1188672.631
60 | 2565465.1409 | 1188717.9922 | 2565419.2012 | 1188672.631
61 | 2565358.7789 | 1188828.6322 | 2565360.6693 | 1188830.0743
62 | 2565360.6693 | 1188830.0743 | 2565376.9169 | 1188842.4684
63 | 2565528.8621 | 1188780.9111 | 2565465.1409 | 1188717.9922
64 | 2565528.8621 | 1188780.9111 | 2565523.0955 | 1188790.0715 | 2565517.09 | 1188797.5711
65 | 2565528.8621 | 1188780.9111 | 2565562.223 | 1188813.942
66 | 2565528.8621 | 1188780.9111 | 2565589.2341 | 1188704.8586
67 | 2565562.223 | 1188813.942 | 2565566.0127 | 1188817.6942 | 2565573.3162 | 1188825.0449 | 2565590.8816 | 1188842.7345
68 | 2565607.7925 | 1188859.7649 | 2565590.8816 | 1188842.7345
69 | 2565607.7925 | 1188859.7649 | 2565627.6146 | 1188879.7225
70 | 2565607.7925 | 1188859.7649 | 2565617.751 | 1188850.5622
71 | 2565452.4838 | 1188878.416 | 2565443.8523 | 1188869.5946 | 2565434.4187 | 1188864.502 | 2565422.6748 | 1188864.8035 | 2565412.345 | 1188866.9645 | 2565406.9281 | 1188865.3617 | 2565404.7046 | 1188863.6655
72 | 2565452.4838 | 1188878.416 | 2565440.0585 | 1188894.3466
73 | 2565384.1367 | 1188847.9758 | 2565404.7046 | 1188863.6655
74 | 2565440.0585 | 1188894.3466 | 2565425.9512 | 1188912.4336
75 | 2565384.1367 | 1188847.9758 | 2565376.9169 | 1188842.4684
76 | 2565425.9512 | 1188912.4336 | 2565425.6905 | 1188912.7679
77 | 2565402.7288 | 1188942.2051 | 2565424.5325 | 1188914.2526 | 2565425.6905 | 1188912.7679
78 | 2565627.6146 | 1188879.7225 | 2565650.4999 | 1188902.7643 | 2565651.1923 | 1188903.4616
79 | 2565627.4766 | 1188843.7448 | 2565626.4948 | 1188844.0154 | 2565620.576 | 1188847.9516 | 2565617.751 | 1188850.5622
80 | 2565651.1923 | 1188903.4616 | 2565673.6093 | 1188874.8609
81 | 2565663.5217 | 1188915.8769 | 2565651.1923 | 1188903.4616
82 | 2565672.6818 | 1188802.4496 | 2565668.6938 | 1188813.2338 | 2565657.7078 | 1188827.2934 | 2565649.1206 | 1188835.4139 | 2565643.7402 | 1188838.8022 | 2565634.4449 | 1188841.824 | 2565627.4766 | 1188843.7448
83 | 2565660.0542 | 1189265.5424 | 2565653.3885 | 1189260.1508
84 | 2565631.2904 | 1189224.7311 | 2565621.1794 | 1189231.1517
85 | 2565615.3343 | 1189234.8634 | 2565621.1794 | 1189231.1517
86 | 2565587.3557 | 1189188.1537 | 2565598.1183 | 1189187.9557
87 | 2565615.3343 | 1189234.8634 | 2565580.2402 | 1189257.1483 | 2565566.9758 | 1189292.5747
88 | 2565557.3102 | 1189318.3896 | 2565566.9758 | 1189292.5747
89 | 2565533.7954 | 1189353.7015 | 2565556.5212 | 1189320.4969 | 2565557.3102 | 1189318.3896
90 | 2565533.7954 | 1189353.7015 | 2565529.5341 | 1189338.1844 | 2565525.5752 | 1189326.1675 | 2565514.5858 | 1189301.1508 | 2565510.9723 | 1189293.7145
91 | 2565533.7954 | 1189353.7015 | 2565526.7545 | 1189366.2718
92 | 2565522.9413 | 1189373.0796 | 2565526.7545 | 1189366.2718
93 | 2565725.8235 | 1189147.8376 | 2565706.2792 | 1189136.2825
94 | 2565292.2059 | 1188834.0388 | 2565303.8649 | 1188844.4364
95 | 2565325.8372 | 1188864.0314 | 2565303.8649 | 1188844.4364
96 | 2565325.8372 | 1188864.0314 | 2565278.3788 | 1188910.7434
97 | 2565325.8372 | 1188864.0314 | 2565335.1848 | 1188873.7705
98 | 2565278.3788 | 1188910.7434 | 2565277.5705 | 1188914.7058 | 2565279.6163 | 1188920.2524 | 2565284.6039 | 1188924.0921 | 2565286.3105 | 1188925.4867
99 | 2565251.1392 | 1188941.5629 | 2565278.3788 | 1188910.7434
100 | 2565358.9328 | 1188898.5133 | 2565335.1848 | 1188873.7705
101 | 2565286.3105 | 1188925.4867 | 2565289.7877 | 1188928.3283
102 | 2565251.1392 | 1188941.5629 | 2565260.6326 | 1188949.6246
103 | 2565358.9328 | 1188898.5133 | 2565345.7631 | 1188912.2916
104 | 2565358.9328 | 1188898.5133 | 2565365.7454 | 1188905.6205
105 | 2565260.6326 | 1188949.6246 | 2565267.7949 | 1188955.7069 | 2565276.9769 | 1188963.5066
106 | 2565336.4402 | 1188922.0454 | 2565345.7631 | 1188912.2916
107 | 2565380.1806 | 1188920.6798 | 2565365.7454 | 1188905.6205
108 | 2565380.1806 | 1188920.6798 | 2565387.8217 | 1188927.9742
109 | 2565380.1806 | 1188920.6798 | 2565365.5997 | 1188937.3031
110 | 2565402.7288 | 1188942.2051 | 2565387.8217 | 1188927.9742
111 | 2565365.5997 | 1188937.3031 | 2565364.3804 | 1188938.6933
112 | 2565421.8374 | 1188961.1712 | 2565402.7288 | 1188942.2051
113 | 2565346.0894 | 1188959.5463 | 2565364.3804 | 1188938.6933
114 | 2565421.8374 | 1188961.1712 | 2565407.9998 | 1188975.6555
115 | 2565405.9323 | 1188977.8195 | 2565407.9998 | 1188975.6555
116 | 2565395.3725 | 1188988.8728 | 2565405.9323 | 1188977.8195
117 | 2565395.3725 | 1188988.8728 | 2565395.3725 | 1188988.8728 | 2565404.3275 | 1188996.9746
118 | 2565408.0456 | 1189000.3385 | 2565404.3275 | 1188996.9746
119 | 2565449.6801 | 1189039.6411 | 2565456.8446 | 1189030.3075
120 | 2565567.8456 | 1189055.8604 | 2565557.5982 | 1189049.1988
121 | 2565567.8456 | 1189055.8604 | 2565573.4461 | 1189059.5012
122 | 2565580.7919 | 1189064.2766 | 2565573.4461 | 1189059.5012
123 | 2565580.7919 | 1189064.2766 | 2565591.6054 | 1189071.3062
124 | 2565594.1993 | 1189072.9924 | 2565591.6054 | 1189071.3062
125 | 2565594.1993 | 1189072.9924 | 2565596.4686 | 1189074.4677 | 2565613.1524 | 1189083.3662
126 | 2565544.8646 | 1189127.0935 | 2565544.8646 | 1189127.0935 | 2565539.6678 | 1189132.4152
127 | 2565629.2618 | 1189091.9583 | 2565613.1524 | 1189083.3662
128 | 2565629.2618 | 1189091.9583 | 2565630.5852 | 1189092.6641
129 | 2565655.5058 | 1189105.9558 | 2565630.5852 | 1189092.6641
130 | 2565655.5058 | 1189105.9558 | 2565673.3332 | 1189116.6569
131 | 2565655.5058 | 1189105.9558 | 2565673.0971 | 1189080.3225
132 | 2565673.0971 | 1189080.3225 | 2565685.4405 | 1189062.3363
133 | 2565522.9413 | 1189373.0796 | 2565519.4704 | 1189379.2762
134 | 2565514.074 | 1189388.9105 | 2565519.4704 | 1189379.2762
135 | 2565514.074 | 1189388.9105 | 2565513.3985 | 1189390.1165
136 | 2565499.8045 | 1189414.386 | 2565513.3985 | 1189390.1165
137 | 2565499.8045 | 1189414.386 | 2565496.4956 | 1189422.465 | 2565489.4895 | 1189440.0261
138 | 2565499.8045 | 1189414.386 | 2565469.5613 | 1189385.89 | 2565467.8731 | 1189376.1945 | 2565465.2686 | 1189353.1305
139 | 2565489.4895 | 1189440.0261 | 2565470.1781 | 1189426.6694
140 | 2565418.7933 | 1189308.42 | 2565459.067 | 1189342.3606 | 2565465.2686 | 1189353.1305
141 | 2565418.7933 | 1189308.42 | 2565412.0143 | 1189315.1517 | 2565411.4258 | 1189318.8794 | 2565412.6168 | 1189321.7296 | 2565414.7323 | 1189324.8746 | 2565433.4432 | 1189341.2305
142 | 2565418.7933 | 1189308.42 | 2565410.155 | 1189302.2667 | 2565400.1561 | 1189307.4274 | 2565383.0774 | 1189306.915
143 | 2565383.0774 | 1189306.915 | 2565374.6672 | 1189303.2952 | 2565367.5919 | 1189297.0884 | 2565344.9939 | 1189277.2756 | 2565344.108 | 1189276.4986
144 | 2565383.0774 | 1189306.915 | 2565269.6548 | 1189414.1203
145 | 2565276.9769 | 1188963.5066 | 2565285.4362 | 1188970.6925
146 | 2565321.4274 | 1189001.2651 | 2565318.6968 | 1188998.9453 | 2565315.7842 | 1188996.472 | 2565285.4362 | 1188970.6925
147 | 2565321.4274 | 1189001.2651 | 2565370.5023 | 1189042.9572 | 2565374.0451 | 1189045.9615

## bus_geodata
| x | y | coords
0 | 2565690.2553 | 1189178.9533
1 | 2565689.8383 | 1189178.669
2 | 2565703.6112 | 1189202.1087
3 | 2565664.45 | 1189161.2785
4 | 2565675.8212 | 1189208.3224
5 | 2565728.5338 | 1189195.5936
6 | 2565677.609 | 1189143.0491
7 | 2565646.9878 | 1189214.7633
8 | 2565729.7779 | 1189195.2684
9 | 2565689.6083 | 1189126.4262
10 | 2565635.0286 | 1189222.3574
11 | 2565634.1651 | 1189189.19
12 | 2565651.2346 | 1189255.1211
13 | 2565627.0123 | 1189189.3757
14 | 2565618.0033 | 1189163.8805
15 | 2565708.5828 | 1189028.6143
16 | 2565699.1218 | 1189042.4005
17 | 2565708.617 | 1189028.5645
18 | 2565694.695 | 1189048.851
19 | 2565737.1658 | 1188989.146
20 | 2565693.8645 | 1189050.0611
21 | 2565695.1723 | 1188947.748
22 | 2565685.7956 | 1189061.8187
23 | 2565682.0169 | 1188934.5009
24 | 2565495.2473 | 1189030.7804
25 | 2565492.7182 | 1189033.7647
26 | 2565505.7821 | 1189018.3497
27 | 2565470.0612 | 1189060.5001
28 | 2565487.5495 | 1189008.3719
29 | 2565532.1297 | 1189032.9389
30 | 2565477.8548 | 1189002.9362
31 | 2565491.9639 | 1188990.4287
32 | 2565537.0027 | 1189035.8101
33 | 2565467.5776 | 1189016.3249
34 | 2565434.0879 | 1188970.3048
35 | 2565494.3384 | 1188980.7773
36 | 2565542.89 | 1189039.6373
37 | 2565443.4326 | 1189148.0988
38 | 2565464.22 | 1189174.5962
39 | 2565438.0351 | 1189141.2186
40 | 2565536.8827 | 1189184.4371
41 | 2565532.1039 | 1189173.7728
42 | 2565578.0518 | 1189188.3248
43 | 2565535.3114 | 1189136.8762
44 | 2565586.9606 | 1189188.1609
45 | 2565340.4349 | 1188594.2779
46 | 2565349.6098 | 1188603.4077
47 | 2565381.4251 | 1188635.0598
48 | 2565227.7069 | 1188783.8315
49 | 2565282.9086 | 1188825.7474
50 | 2565404.0684 | 1188657.5843
51 | 2565419.2012 | 1188672.631
52 | 2565358.7789 | 1188828.6322
53 | 2565360.6693 | 1188830.0743
54 | 2565465.1409 | 1188717.9922
55 | 2565528.8621 | 1188780.9111
56 | 2565517.09 | 1188797.5711
57 | 2565562.223 | 1188813.942
58 | 2565589.2341 | 1188704.8586
59 | 2565590.8816 | 1188842.7345
60 | 2565607.7925 | 1188859.7649
61 | 2565452.4838 | 1188878.416
62 | 2565404.7046 | 1188863.6655
63 | 2565440.0585 | 1188894.3466
64 | 2565384.1367 | 1188847.9758
65 | 2565425.9512 | 1188912.4336
66 | 2565376.9169 | 1188842.4684
67 | 2565425.6905 | 1188912.7679
68 | 2565627.6146 | 1188879.7225
69 | 2565617.751 | 1188850.5622
70 | 2565651.1923 | 1188903.4616
71 | 2565627.4766 | 1188843.7448
72 | 2565673.6093 | 1188874.8609
73 | 2565663.5217 | 1188915.8769
74 | 2565672.6818 | 1188802.4496
75 | 2565660.0542 | 1189265.5424
76 | 2565653.3885 | 1189260.1508
77 | 2565631.2904 | 1189224.7311
78 | 2565621.1794 | 1189231.1517
79 | 2565598.1183 | 1189187.9557
80 | 2565615.3343 | 1189234.8634
81 | 2565566.9758 | 1189292.5747
82 | 2565557.3102 | 1189318.3896
83 | 2565533.7954 | 1189353.7015
84 | 2565510.9723 | 1189293.7145
85 | 2565526.7545 | 1189366.2718
86 | 2565725.8235 | 1189147.8376
87 | 2565706.2792 | 1189136.2825
88 | 2565292.2059 | 1188834.0388
89 | 2565303.8649 | 1188844.4364
90 | 2565325.8372 | 1188864.0314
91 | 2565278.3788 | 1188910.7434
92 | 2565335.1848 | 1188873.7705
93 | 2565286.3105 | 1188925.4867
94 | 2565251.1392 | 1188941.5629
95 | 2565358.9328 | 1188898.5133
96 | 2565289.7877 | 1188928.3283
97 | 2565260.6326 | 1188949.6246
98 | 2565345.7631 | 1188912.2916
99 | 2565365.7454 | 1188905.6205
100 | 2565336.4402 | 1188922.0454
101 | 2565380.1806 | 1188920.6798
102 | 2565387.8217 | 1188927.9742
103 | 2565365.5997 | 1188937.3031
104 | 2565402.7288 | 1188942.2051
105 | 2565364.3804 | 1188938.6933
106 | 2565421.8374 | 1188961.1712
107 | 2565346.0894 | 1188959.5463
108 | 2565407.9998 | 1188975.6555
109 | 2565405.9323 | 1188977.8195
110 | 2565395.3725 | 1188988.8728
111 | 2565404.3275 | 1188996.9746
112 | 2565408.0456 | 1189000.3385
113 | 2565456.8446 | 1189030.3075
114 | 2565449.6801 | 1189039.6411
115 | 2565497.7137 | 1188967.0576
116 | 2565567.8456 | 1189055.8604
117 | 2565557.5982 | 1189049.1988
118 | 2565573.4461 | 1189059.5012
119 | 2565580.7919 | 1189064.2766
120 | 2565591.6054 | 1189071.3062
121 | 2565594.1993 | 1189072.9924
122 | 2565544.8646 | 1189127.0935
123 | 2565539.6678 | 1189132.4152
124 | 2565587.3557 | 1189188.1537
125 | 2565613.1524 | 1189083.3662
126 | 2565629.2618 | 1189091.9583
127 | 2565630.5852 | 1189092.6641
128 | 2565655.5058 | 1189105.9558
129 | 2565673.3332 | 1189116.6569
130 | 2565673.0971 | 1189080.3225
131 | 2565685.4405 | 1189062.3363
132 | 2565522.9413 | 1189373.0796
133 | 2565519.4704 | 1189379.2762
134 | 2565514.074 | 1189388.9105
135 | 2565513.3985 | 1189390.1165
136 | 2565499.8045 | 1189414.386
137 | 2565489.4895 | 1189440.0261
138 | 2565465.2686 | 1189353.1305
139 | 2565470.1781 | 1189426.6694
140 | 2565418.7933 | 1189308.42
141 | 2565433.4432 | 1189341.2305
142 | 2565383.0774 | 1189306.915
143 | 2565276.9769 | 1188963.5066
144 | 2565285.4362 | 1188970.6925
145 | 2565321.4274 | 1189001.2651
146 | 2565374.0451 | 1189045.9615
147 | 2565344.108 | 1189276.4986
148 | 2565269.6548 | 1189414.1203
149 | 2565505.7821 | 1189018.3497

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9864 | -0.095006 | 0.0066843 | 0.0016752
1 | 0.98642 | -0.094882 | 0.0046622 | 0.0011685
2 | 0.98551 | -0.10132 | 0.0044079 | 0.0011047
3 | 0.98755 | -0.086836 | 0 | 0
4 | 0.98471 | -0.10698 | 0.003437 | 0.0008614
5 | 0.9854 | -0.10207 | 0.0022789 | 0.00057114
6 | 0.98839 | -0.080968 | 0.0017512 | 0.0004389
7 | 0.98393 | -0.11251 | 0 | 0
8 | 0.9854 | -0.10207 | 0.00053809 | 0.00013486
9 | 0.98916 | -0.075504 | 0.0052506 | 0.0013159
10 | 0.98372 | -0.11401 | 0.0018376 | 0.00046055
11 | 0.98295 | -0.1195 | 0 | 0
12 | 0.98361 | -0.11482 | 0.001726 | 0.00043258
13 | 0.98279 | -0.12065 | 0 | 0
14 | 0.98282 | -0.12043 | 0.0028455 | 0.00071316
15 | 0.98588 | -0.098529 | 0.0014457 | 0.00036233
16 | 0.98669 | -0.092844 | 0.00057417 | 0.0001439
17 | 0.98588 | -0.098548 | 0.00084267 | 0.00021119
18 | 0.98707 | -0.090141 | 0.0014079 | 0.00035286
19 | 0.98369 | -0.11402 | 0 | 0
20 | 0.98714 | -0.089613 | 0.0010326 | 0.00025879
21 | 0.98103 | -0.13283 | 0.00089528 | 0.00022438
22 | 0.98789 | -0.084336 | 0.00061791 | 0.00015486
23 | 0.98022 | -0.13863 | 0.0022409 | 0.00056163
24 | 0.99738 | -0.018184 | 0.00069753 | 0.00017482
25 | 0.99737 | -0.01826 | 0.00090276 | 0.00022625
26 | 0.99744 | -0.017754 | 0 | 0
27 | 0.99732 | -0.018622 | 0.001027 | 0.00025739
28 | 0.99576 | -0.029483 | 0 | 0
29 | 1 | 0 | -0.20075 | -0.050473
30 | 0.99495 | -0.035165 | 0 | 0
31 | 0.99562 | -0.030491 | 0.0018048 | 0.00045231
32 | 0.99962 | -0.0026053 | 0.00069795 | 0.00017492
33 | 0.99487 | -0.035692 | 0.00092725 | 0.00023239
34 | 0.99118 | -0.061548 | 0.0014727 | 0.0003691
35 | 0.99556 | -0.030853 | 0.0013269 | 0.00033256
36 | 0.99916 | -0.0058242 | 0.00084969 | 0.00021295
37 | 0.98086 | -0.13444 | 0.0010752 | 0.00026947
38 | 0.98096 | -0.13373 | 0 | 0
39 | 0.98084 | -0.13452 | 0.00093789 | 0.00023506
40 | 0.98117 | -0.13218 | 0 | 0
41 | 0.98104 | -0.1331 | 0.0049718 | 0.0012461
42 | 0.98175 | -0.12803 | 0.002492 | 0.00062455
43 | 0.9809 | -0.13412 | 0.0011239 | 0.00028169
44 | 0.98191 | -0.12691 | 0.0010359 | 0.00025963
45 | 0.97201 | -0.19755 | 0.0011262 | 0.00028226
46 | 0.97203 | -0.19739 | 0.00046617 | 0.00011683
47 | 0.97213 | -0.19664 | 0.0028531 | 0.00071507
48 | 0.98233 | -0.12426 | 0.0031076 | 0.00077884
49 | 0.98264 | -0.12203 | 0.0098975 | 0.0024806
50 | 0.97234 | -0.19514 | 0.0018315 | 0.00045901
51 | 0.97254 | -0.19372 | 0.00066441 | 0.00016652
52 | 0.98751 | -0.087484 | 0.00059787 | 0.00014984
53 | 0.98751 | -0.087469 | 0.00075953 | 0.00019036
54 | 0.97319 | -0.18898 | 0.001918 | 0.00048069
55 | 0.97436 | -0.18062 | 0 | 0
56 | 0.97433 | -0.18082 | 0.00095569 | 0.00023952
57 | 0.97512 | -0.17511 | 0.0010383 | 0.00026022
58 | 0.97417 | -0.18195 | 0.001306 | 0.00032733
59 | 0.97585 | -0.16991 | 0.0033604 | 0.00084218
60 | 0.97639 | -0.166 | 0 | 0
61 | 0.98798 | -0.084162 | 0 | 0
62 | 0.98769 | -0.086192 | 0.00062165 | 0.0001558
63 | 0.98808 | -0.083399 | 0.0008364 | 0.00020962
64 | 0.98758 | -0.087002 | 0.001095 | 0.00027443
65 | 0.98823 | -0.082337 | 0.00062654 | 0.00015702
66 | 0.98755 | -0.087185 | 0.00060655 | 0.00015202
67 | 0.98824 | -0.082314 | 0.00079662 | 0.00019965
68 | 0.97732 | -0.15934 | 0.0012119 | 0.00030373
69 | 0.97625 | -0.16701 | 0.0021767 | 0.00054552
70 | 0.97848 | -0.15101 | 0.0018903 | 0.00047375
71 | 0.97617 | -0.16762 | 0.001016 | 0.00025463
72 | 0.97845 | -0.15127 | 0.00067818 | 0.00016997
73 | 0.97916 | -0.14619 | 0.0012655 | 0.00031716
74 | 0.9758 | -0.17024 | 0.0038762 | 0.00097146
75 | 0.98355 | -0.11524 | 0.0023781 | 0.000596
76 | 0.98358 | -0.11503 | 0.001246 | 0.00031227
77 | 0.98366 | -0.11445 | 0.00073871 | 0.00018514
78 | 0.98349 | -0.11561 | 0.0015405 | 0.00038607
79 | 0.98213 | -0.1253 | 0.0015876 | 0.00039788
80 | 0.9834 | -0.11625 | 0.0038928 | 0.00097564
81 | 0.98209 | -0.12557 | 0.001051 | 0.00026341
82 | 0.98122 | -0.13176 | 0.0012689 | 0.00031802
83 | 0.97996 | -0.14076 | 0 | 0
84 | 0.97988 | -0.14131 | 0.00081525 | 0.00020432
85 | 0.97955 | -0.1437 | 0.00094415 | 0.00023663
86 | 0.98908 | -0.076079 | 0.00069002 | 0.00017294
87 | 0.9891 | -0.075919 | 0.0014076 | 0.00035278
88 | 0.98288 | -0.12035 | 0.0020414 | 0.00051162
89 | 0.98322 | -0.11792 | 0.0017933 | 0.00044944
90 | 0.98394 | -0.11281 | 0 | 0
91 | 0.98322 | -0.1179 | 0 | 0
92 | 0.98441 | -0.10943 | 0.00088337 | 0.00022139
93 | 0.98317 | -0.11826 | 0.0011869 | 0.00029745
94 | 0.98289 | -0.12025 | 0 | 0
95 | 0.98566 | -0.10055 | 0.00063657 | 0.00015954
96 | 0.98317 | -0.11829 | 0.00069634 | 0.00017452
97 | 0.98279 | -0.12096 | 0.00093222 | 0.00023364
98 | 0.98555 | -0.1013 | 0.0015482 | 0.00038802
99 | 0.98608 | -0.097554 | 0.00037223 | 9.3289e-05
100 | 0.98551 | -0.10162 | 0.0022815 | 0.00057179
101 | 0.98699 | -0.091134 | 0 | 0
102 | 0.98751 | -0.087474 | 0.0014314 | 0.00035875
103 | 0.98687 | -0.092 | 0.0012298 | 0.00030821
104 | 0.98856 | -0.080043 | 0 | 0
105 | 0.98686 | -0.092049 | 0.000885 | 0.0002218
106 | 0.99016 | -0.06874 | 0 | 0
107 | 0.98679 | -0.092534 | 0.0017033 | 0.00042688
108 | 0.99001 | -0.069768 | 0.0013666 | 0.0003425
109 | 0.99 | -0.069881 | 0.001381 | 0.0003461
110 | 0.98995 | -0.070238 | 0.0011037 | 0.0002766
111 | 0.98993 | -0.070384 | 0.00060335 | 0.00015121
112 | 0.98992 | -0.070414 | 0.00058603 | 0.00014687
113 | 0.99482 | -0.036077 | 0.0010403 | 0.00026073
114 | 0.9948 | -0.036211 | 0.0011262 | 0.00028225
115 | 0.99552 | -0.031179 | 0.0022871 | 0.0005732
116 | 0.9972 | -0.019383 | 0.0012184 | 0.00030536
117 | 0.998 | -0.013829 | 0.00084133 | 0.00021086
118 | 0.99676 | -0.022395 | 0.0002586 | 6.4812e-05
119 | 0.99619 | -0.026341 | 0.00021919 | 5.4935e-05
120 | 0.99536 | -0.032149 | 0.0014593 | 0.00036574
121 | 0.99516 | -0.033529 | 0.0016196 | 0.00040591
122 | 0.98088 | -0.13428 | 0.00080444 | 0.00020161
123 | 0.98089 | -0.13422 | 0.00072159 | 0.00018085
124 | 0.98192 | -0.12686 | 0.00077594 | 0.00019447
125 | 0.99379 | -0.043064 | 0.00046517 | 0.00011658
126 | 0.99264 | -0.051109 | 0.0017555 | 0.00043996
127 | 0.99254 | -0.051762 | 0.0031695 | 0.00079435
128 | 0.99083 | -0.063775 | 0 | 0
129 | 0.98995 | -0.069978 | 0.0022591 | 0.00056618
130 | 0.98912 | -0.075734 | 0.00021766 | 5.455e-05
131 | 0.98793 | -0.0841 | 0.00077635 | 0.00019457
132 | 0.97934 | -0.14521 | 0.00069095 | 0.00017317
133 | 0.97915 | -0.14654 | 0.0012381 | 0.00031031
134 | 0.97888 | -0.14846 | 0.001588 | 0.00039799
135 | 0.97885 | -0.14867 | 0.0010767 | 0.00026985
136 | 0.97828 | -0.15274 | 0 | 0
137 | 0.97819 | -0.1534 | 0 | 0
138 | 0.977 | -0.1619 | 0.0017888 | 0.00044831
139 | 0.97811 | -0.15396 | 0.0022729 | 0.00056964
140 | 0.97606 | -0.16869 | 0 | 0
141 | 0.97598 | -0.16923 | 0.0011313 | 0.00028354
142 | 0.97556 | -0.17229 | 0 | 0
143 | 0.98265 | -0.12198 | 0.0009327 | 0.00023376
144 | 0.98259 | -0.1224 | 0.0011944 | 0.00029934
145 | 0.98242 | -0.1236 | 0.0010439 | 0.00026162
146 | 0.98228 | -0.12462 | 0.0014148 | 0.00035457
147 | 0.97553 | -0.17248 | 0.0003547 | 8.8896e-05
148 | 0.97363 | -0.18616 | 0.0084462 | 0.0021168
149 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.072097 | -0.018096 | 0.072098 | 0.018096 | 1.242e-06 | 4.5836e-07 | 0.10877 | 0.10877 | 0.10877 | 0.9864 | -0.095006 | 0.98642 | -0.094882 | 13.4284
1 | 0.065413 | 0.016421 | -0.065356 | -0.0164 | 5.732e-05 | 2.0964e-05 | 0.098687 | 0.098687 | 0.098687 | 0.9864 | -0.095006 | 0.98551 | -0.10132 | 12.1836
2 | -0.076761 | -0.019265 | 0.076847 | 0.019297 | 8.5838e-05 | 3.1835e-05 | 0.1158 | 0.1158 | 0.1158 | 0.98642 | -0.094882 | 0.98755 | -0.086836 | 14.2967
3 | 0.05813 | 0.014589 | -0.058085 | -0.014573 | 4.5637e-05 | 1.6465e-05 | 0.087778 | 0.087779 | 0.087779 | 0.98551 | -0.10132 | 0.98471 | -0.10698 | 10.8369
4 | 0.0028173 | 0.00070577 | -0.002817 | -0.00070598 | 2.9085e-07 | -2.1633e-07 | 0.0042537 | 0.0042538 | 0.0042538 | 0.98551 | -0.10132 | 0.9854 | -0.10207 | 1.5755
5 | -0.076847 | -0.019297 | 0.076909 | 0.01932 | 6.2712e-05 | 2.3256e-05 | 0.1158 | 0.1158 | 0.1158 | 0.98755 | -0.086836 | 0.98839 | -0.080968 | 14.2967
6 | 0.054648 | 0.013711 | -0.054606 | -0.013696 | 4.1912e-05 | 1.4993e-05 | 0.082585 | 0.082585 | 0.082585 | 0.98471 | -0.10698 | 0.98393 | -0.11251 | 10.1957
7 | 0.00053809 | 0.00013484 | -0.00053809 | -0.00013486 | 5.2969e-10 | -1.6176e-08 | 0.00081255 | 0.00081255 | 0.00081255 | 0.9854 | -0.10207 | 0.9854 | -0.10207 | 0.30095
8 | -0.07866 | -0.019759 | 0.07872 | 0.019781 | 5.9818e-05 | 2.2218e-05 | 0.11844 | 0.11844 | 0.11844 | 0.98839 | -0.080968 | 0.98916 | -0.075504 | 14.6221
9 | 0.030839 | 0.0077387 | -0.030832 | -0.0077367 | 6.4103e-06 | 1.9258e-06 | 0.046642 | 0.046642 | 0.046642 | 0.98393 | -0.11251 | 0.98372 | -0.11401 | 5.7582
10 | 0.018415 | 0.0046167 | -0.018397 | -0.0046103 | 1.782e-05 | 6.3866e-06 | 0.02785 | 0.02785 | 0.02785 | 0.98393 | -0.11251 | 0.98295 | -0.1195 | 10.3149
11 | 0.0053519 | 0.0013409 | -0.0053502 | -0.0013407 | 1.7109e-06 | 1.2662e-07 | 0.0080937 | 0.0080939 | 0.0080939 | 0.98393 | -0.11251 | 0.98361 | -0.11482 | 2.9977
12 | 0.0020978 | 0.00052523 | -0.0020976 | -0.00052543 | 1.2034e-07 | -2.023e-07 | 0.0031555 | 0.0031556 | 0.0031556 | 0.98916 | -0.075504 | 0.9891 | -0.075919 | 1.1687
13 | -0.086069 | -0.021622 | 0.086135 | 0.021647 | 6.6206e-05 | 2.4732e-05 | 0.12949 | 0.12949 | 0.12949 | 0.98916 | -0.075504 | 0.98995 | -0.069978 | 15.9868
14 | 0.028995 | 0.0072762 | -0.028993 | -0.0072757 | 1.772e-06 | 5.1289e-07 | 0.043862 | 0.043862 | 0.043862 | 0.98372 | -0.11401 | 0.98366 | -0.11445 | 5.4151
15 | 0.015551 | 0.0038974 | -0.015549 | -0.0038965 | 2.4672e-06 | 8.5851e-07 | 0.023542 | 0.023542 | 0.023542 | 0.98295 | -0.1195 | 0.98279 | -0.12065 | 8.7193
16 | 0.0028459 | 0.0007129 | -0.0028455 | -0.00071316 | 3.6396e-07 | -2.583e-07 | 0.0043081 | 0.0043082 | 0.0043082 | 0.98295 | -0.1195 | 0.98282 | -0.12043 | 1.5956
17 | 0.0036242 | 0.00090816 | -0.0036241 | -0.00090819 | 1.0263e-07 | -2.9972e-08 | 0.0054827 | 0.0054828 | 0.0054828 | 0.98361 | -0.11482 | 0.98358 | -0.11503 | 2.0306
18 | 0.015549 | 0.0038965 | -0.015539 | -0.003893 | 1.0008e-05 | 3.4828e-06 | 0.023542 | 0.023542 | 0.023542 | 0.98279 | -0.12065 | 0.98213 | -0.1253 | 8.7193
19 | -0.033372 | -0.0083953 | 0.033399 | 0.0084052 | 2.6483e-05 | 9.9724e-06 | 0.050381 | 0.050381 | 0.050381 | 0.98588 | -0.098529 | 0.98669 | -0.092844 | 18.6597
20 | 0.031927 | 0.0080329 | -0.031927 | -0.0080329 | 8.757e-08 | 3.2911e-08 | 0.048199 | 0.048199 | 0.048199 | 0.98588 | -0.098529 | 0.98588 | -0.098548 | 17.8516
21 | -0.033973 | -0.0085491 | 0.033986 | 0.008554 | 1.2821e-05 | 4.8311e-06 | 0.051247 | 0.051247 | 0.051247 | 0.98669 | -0.092844 | 0.98707 | -0.090141 | 18.9804
22 | 0.031084 | 0.0078217 | -0.031017 | -0.0077966 | 6.6961e-05 | 2.5134e-05 | 0.046927 | 0.046928 | 0.046928 | 0.98588 | -0.098548 | 0.98369 | -0.11402 | 17.3806
23 | -0.035394 | -0.0089068 | 0.035396 | 0.0089078 | 2.6086e-06 | 9.8454e-07 | 0.05337 | 0.053369 | 0.05337 | 0.98707 | -0.090141 | 0.98714 | -0.089613 | 19.7665
24 | 0.031017 | 0.0077966 | -0.030936 | -0.0077662 | 8.1035e-05 | 3.0421e-05 | 0.046928 | 0.046928 | 0.046928 | 0.98369 | -0.11402 | 0.98103 | -0.13283 | 17.3807
25 | -0.036429 | -0.0091666 | 0.036456 | 0.0091768 | 2.6845e-05 | 1.0142e-05 | 0.054926 | 0.054926 | 0.054926 | 0.98714 | -0.089613 | 0.98789 | -0.084336 | 20.343
26 | 0.030041 | 0.0075418 | -0.030017 | -0.0075327 | 2.4192e-05 | 9.0692e-06 | 0.04557 | 0.04557 | 0.04557 | 0.98103 | -0.13283 | 0.98022 | -0.13863 | 16.8778
27 | -0.037074 | -0.0093316 | 0.037075 | 0.0093321 | 1.222e-06 | 4.6198e-07 | 0.055857 | 0.055857 | 0.055857 | 0.98789 | -0.084336 | 0.98793 | -0.0841 | 20.6877
28 | 0.027776 | 0.0069711 | -0.027747 | -0.0069602 | 2.9123e-05 | 1.0871e-05 | 0.042168 | 0.042168 | 0.042168 | 0.98022 | -0.13863 | 0.97916 | -0.14619 | 15.6179
29 | 0.0019298 | 0.00048316 | -0.0019298 | -0.0004832 | 2.0232e-08 | -4.327e-08 | 0.002879 | 0.002879 | 0.002879 | 0.99738 | -0.018184 | 0.99737 | -0.01826 | 1.0663
30 | -0.0026273 | -0.00065798 | 0.0026275 | 0.00065782 | 1.5621e-07 | -1.5258e-07 | 0.0039196 | 0.0039196 | 0.0039196 | 0.99738 | -0.018184 | 0.99744 | -0.017754 | 1.4517
31 | 0.001027 | 0.00025695 | -0.001027 | -0.00025739 | 5.1338e-08 | -4.3758e-07 | 0.0015321 | 0.0015323 | 0.0015323 | 0.99737 | -0.01826 | 0.99732 | -0.018622 | 0.56751
32 | 0.056773 | 0.014294 | -0.05668 | -0.014259 | 9.2882e-05 | 3.5453e-05 | 0.084719 | 0.084719 | 0.084719 | 0.99744 | -0.017754 | 0.99576 | -0.029483 | 31.3773
33 | -0.0594 | -0.014952 | 0.059548 | 0.015009 | 0.00014765 | 5.6395e-05 | 0.088638 | 0.088638 | 0.088638 | 0.99744 | -0.017754 | 1 | 0 | 32.8289
34 | 0.05126 | 0.012901 | -0.051219 | -0.012886 | 4.0629e-05 | 1.5482e-05 | 0.07662 | 0.07662 | 0.07662 | 0.99576 | -0.029483 | 0.99495 | -0.035165 | 28.3777
35 | 0.0054198 | 0.0013579 | -0.0054191 | -0.0013579 | 7.5633e-07 | 5.056e-08 | 0.008099 | 0.0080991 | 0.0080991 | 0.99576 | -0.029483 | 0.99562 | -0.030491 | 2.9997
36 | 0.1404 | 0.035465 | -0.14035 | -0.035445 | 5.1424e-05 | 1.9556e-05 | 0.20901 | 0.20901 | 0.20901 | 1 | 0 | 0.99962 | -0.0026053 | 25.8041
37 | 0.0030941 | 0.00077491 | -0.0030939 | -0.00077505 | 2.2552e-07 | -1.3244e-07 | 0.0046273 | 0.0046274 | 0.0046274 | 0.99495 | -0.035165 | 0.99487 | -0.035692 | 1.7139
38 | 0.048125 | 0.012111 | -0.047949 | -0.012043 | 0.00017656 | 6.7201e-05 | 0.071992 | 0.071993 | 0.071993 | 0.99495 | -0.035165 | 0.99118 | -0.061548 | 26.6639
39 | 0.0036143 | 0.00090556 | -0.0036141 | -0.00090562 | 1.8097e-07 | -5.9644e-08 | 0.0054017 | 0.0054018 | 0.0054018 | 0.99562 | -0.030491 | 0.99556 | -0.030853 | 2.0007
40 | 0.13965 | 0.03527 | -0.13959 | -0.035246 | 6.3174e-05 | 2.4022e-05 | 0.20797 | 0.20797 | 0.20797 | 0.99962 | -0.0026053 | 0.99916 | -0.0058242 | 25.6758
41 | 0.0021667 | 0.00054266 | -0.0021666 | -0.00054284 | 1.1551e-07 | -1.8445e-07 | 0.0032405 | 0.0032406 | 0.0032406 | 0.99487 | -0.035692 | 0.99482 | -0.036077 | 1.2002
42 | 0.046476 | 0.011674 | -0.046429 | -0.011657 | 4.6431e-05 | 1.7661e-05 | 0.069782 | 0.069782 | 0.069782 | 0.99118 | -0.061548 | 0.99016 | -0.06874 | 25.8451
43 | 0.0022872 | 0.00057305 | -0.0022871 | -0.0005732 | 1.0303e-07 | -1.4408e-07 | 0.0034185 | 0.0034185 | 0.0034185 | 0.99556 | -0.030853 | 0.99552 | -0.031179 | 1.2661
44 | 0.13874 | 0.035033 | -0.13858 | -0.034974 | 0.00015591 | 5.9278e-05 | 0.20671 | 0.20671 | 0.20671 | 0.99916 | -0.0058242 | 0.998 | -0.013829 | 25.5196
45 | -0.0020131 | -0.00050442 | 0.0020133 | 0.00050407 | 1.9599e-07 | -3.4974e-07 | 0.0030539 | 0.0030538 | 0.0030539 | 0.98086 | -0.13444 | 0.98096 | -0.13373 | 1.1311
46 | 0.0009379 | 0.00023495 | -0.00093789 | -0.00023506 | 1.1047e-08 | -1.0612e-07 | 0.0014228 | 0.0014228 | 0.0014228 | 0.98086 | -0.13444 | 0.98084 | -0.13452 | 0.52698
47 | -0.0020133 | -0.00050407 | 0.0020137 | 0.0005033 | 4.3201e-07 | -7.7138e-07 | 0.0030538 | 0.0030534 | 0.0030538 | 0.98096 | -0.13373 | 0.98117 | -0.13218 | 1.131
48 | 0.0076232 | 0.0019099 | -0.0076222 | -0.0019097 | 9.7462e-07 | 2.2728e-07 | 0.011561 | 0.011561 | 0.011561 | 0.98117 | -0.13218 | 0.98104 | -0.1331 | 4.2818
49 | -0.0096369 | -0.0024132 | 0.0096424 | 0.0024148 | 5.5223e-06 | 1.6003e-06 | 0.014614 | 0.014614 | 0.014614 | 0.98117 | -0.13218 | 0.98175 | -0.12803 | 5.4127
50 | 0.0026504 | 0.00066366 | -0.00265 | -0.00066398 | 3.7345e-07 | -3.2393e-07 | 0.0040198 | 0.00402 | 0.00402 | 0.98104 | -0.1331 | 0.9809 | -0.13412 | 1.4889
51 | -0.012134 | -0.0030394 | 0.012136 | 0.00304 | 1.8806e-06 | 6.1062e-07 | 0.018391 | 0.018391 | 0.018391 | 0.98175 | -0.12803 | 0.98191 | -0.12691 | 6.8115
52 | 0.0015261 | 0.0003823 | -0.001526 | -0.00038237 | 2.0851e-08 | -7.0686e-08 | 0.0023149 | 0.002315 | 0.002315 | 0.9809 | -0.13412 | 0.98089 | -0.13422 | 0.8574
53 | -0.013172 | -0.0032996 | 0.013172 | 0.0032997 | 9.8243e-08 | 3.2788e-08 | 0.019961 | 0.019961 | 0.019961 | 0.98191 | -0.12691 | 0.98192 | -0.12686 | 7.393
54 | -0.0011262 | -0.00028226 | 0.0011262 | 0.00028211 | 2.4007e-08 | -1.512e-07 | 0.0017241 | 0.001724 | 0.0017241 | 0.97201 | -0.19755 | 0.97203 | -0.19739 | 0.63855
55 | -0.0015924 | -0.00039894 | 0.0015926 | 0.00039845 | 1.6639e-07 | -4.9236e-07 | 0.0024377 | 0.0024375 | 0.0024377 | 0.97203 | -0.19739 | 0.97213 | -0.19664 | 0.90284
56 | -0.0044457 | -0.0011135 | 0.0044466 | 0.0011135 | 9.228e-07 | -4.1144e-08 | 0.0068047 | 0.0068046 | 0.0068047 | 0.97213 | -0.19664 | 0.97234 | -0.19514 | 2.5203
57 | -0.0031076 | -0.00077884 | 0.0031086 | 0.00077833 | 9.5866e-07 | -5.0933e-07 | 0.0047073 | 0.004707 | 0.0047073 | 0.98233 | -0.12426 | 0.98264 | -0.12203 | 1.7435
58 | -0.013006 | -0.0032589 | 0.013009 | 0.0032599 | 3.0152e-06 | 1.0019e-06 | 0.019695 | 0.019695 | 0.019695 | 0.98264 | -0.12203 | 0.98288 | -0.12035 | 7.2944
59 | -0.0062781 | -0.0015725 | 0.0062794 | 0.0015727 | 1.2291e-06 | 2.0798e-07 | 0.0096074 | 0.0096073 | 0.0096074 | 0.97234 | -0.19514 | 0.97254 | -0.19372 | 3.5583
60 | -0.0069438 | -0.0017392 | 0.0069483 | 0.0017402 | 4.5468e-06 | 9.4711e-07 | 0.010624 | 0.010624 | 0.010624 | 0.97254 | -0.19372 | 0.97319 | -0.18898 | 3.9348
61 | -0.00059787 | -0.00014984 | 0.00059787 | 0.00014981 | 1.2042e-09 | -2.9956e-08 | 0.00090089 | 0.00090088 | 0.00090089 | 0.98751 | -0.087484 | 0.98751 | -0.087469 | 0.33366
62 | -0.0013574 | -0.00034017 | 0.0013575 | 0.00033993 | 5.3344e-08 | -2.4093e-07 | 0.0020454 | 0.0020453 | 0.0020454 | 0.98751 | -0.087469 | 0.98755 | -0.087185 | 0.75755
63 | -0.0088663 | -0.0022209 | 0.0088766 | 0.0022237 | 1.0269e-05 | 2.8354e-06 | 0.013556 | 0.013556 | 0.013556 | 0.97319 | -0.18898 | 0.97436 | -0.18062 | 5.0208
64 | 0.00095571 | 0.00023927 | -0.00095569 | -0.00023952 | 2.7159e-08 | -2.4403e-07 | 0.0014595 | 0.0014595 | 0.0014595 | 0.97436 | -0.18062 | 0.97433 | -0.18082 | 0.54057
65 | -0.011139 | -0.0027892 | 0.011147 | 0.0027918 | 8.4758e-06 | 2.6747e-06 | 0.01701 | 0.01701 | 0.01701 | 0.97436 | -0.18062 | 0.97512 | -0.17511 | 6.2999
66 | 0.0013063 | 0.00032621 | -0.001306 | -0.00032733 | 2.4109e-07 | -1.1165e-06 | 0.0019945 | 0.0019949 | 0.0019949 | 0.97436 | -0.18062 | 0.97417 | -0.18195 | 0.73887
67 | -0.012185 | -0.0030521 | 0.012194 | 0.0030549 | 8.7641e-06 | 2.8637e-06 | 0.018594 | 0.018594 | 0.018594 | 0.97512 | -0.17511 | 0.97585 | -0.16991 | 6.8866
68 | -0.015554 | -0.0038971 | 0.015563 | 0.0039 | 8.4245e-06 | 2.9402e-06 | 0.023718 | 0.023718 | 0.023718 | 0.97585 | -0.16991 | 0.97639 | -0.166 | 8.7844
69 | -0.022635 | -0.0056716 | 0.022655 | 0.0056793 | 2.0885e-05 | 7.6805e-06 | 0.034495 | 0.034494 | 0.034495 | 0.97639 | -0.166 | 0.97732 | -0.15934 | 12.7758
70 | 0.0070717 | 0.0017716 | -0.0070707 | -0.0017714 | 9.827e-07 | 2.0839e-07 | 0.010777 | 0.010777 | 0.010777 | 0.97639 | -0.166 | 0.97625 | -0.16701 | 3.9915
71 | 0.0036821 | 0.00092158 | -0.003681 | -0.00092187 | 1.0325e-06 | -2.9175e-07 | 0.0055452 | 0.0055454 | 0.0055454 | 0.98798 | -0.084162 | 0.98769 | -0.086192 | 2.0539
72 | -0.0036821 | -0.00092158 | 0.0036824 | 0.00092147 | 3.8765e-07 | -1.0965e-07 | 0.0055452 | 0.0055451 | 0.0055452 | 0.98798 | -0.084162 | 0.98808 | -0.083399 | 2.0538
73 | 0.0030594 | 0.00076607 | -0.003059 | -0.00076627 | 3.429e-07 | -1.9916e-07 | 0.0046089 | 0.004609 | 0.004609 | 0.98769 | -0.086192 | 0.98758 | -0.087002 | 1.707
74 | -0.0045189 | -0.0011311 | 0.0045195 | 0.0011311 | 6.6275e-07 | -3.8941e-08 | 0.0068047 | 0.0068046 | 0.0068047 | 0.98808 | -0.083399 | 0.98823 | -0.082337 | 2.5203
75 | 0.0019641 | 0.00049185 | -0.001964 | -0.00049194 | 4.9618e-08 | -9.7102e-08 | 0.0029592 | 0.0029592 | 0.0029592 | 0.98758 | -0.087002 | 0.98755 | -0.087185 | 1.096
76 | -0.0051461 | -0.0012881 | 0.0051461 | 0.0012881 | 1.5883e-08 | 6.7636e-10 | 0.007748 | 0.007748 | 0.007748 | 0.98823 | -0.082337 | 0.98824 | -0.082314 | 2.8696
77 | -0.0059427 | -0.0014877 | 0.0059445 | 0.001488 | 1.865e-06 | 2.3881e-07 | 0.0089475 | 0.0089473 | 0.0089475 | 0.98824 | -0.082314 | 0.98856 | -0.080043 | 3.3139
78 | -0.023867 | -0.005983 | 0.023895 | 0.0059932 | 2.7571e-05 | 1.0184e-05 | 0.03634 | 0.036339 | 0.03634 | 0.97732 | -0.15934 | 0.97848 | -0.15101 | 13.4591
79 | 0.004894 | 0.0012258 | -0.0048936 | -0.0012258 | 4.1571e-07 | 1.0194e-08 | 0.0074593 | 0.0074593 | 0.0074593 | 0.97625 | -0.16701 | 0.97617 | -0.16762 | 2.7627
80 | 0.00067821 | 0.00016952 | -0.00067818 | -0.00016997 | 2.4117e-08 | -4.4716e-07 | 0.0010312 | 0.0010314 | 0.0010314 | 0.97848 | -0.15101 | 0.97845 | -0.15127 | 0.38199
81 | -0.026463 | -0.0066365 | 0.026481 | 0.0066431 | 1.7684e-05 | 6.5817e-06 | 0.040245 | 0.040245 | 0.040245 | 0.97848 | -0.15101 | 0.97916 | -0.14619 | 14.9056
82 | 0.0038776 | 0.0009712 | -0.0038762 | -0.00097146 | 1.4066e-06 | -2.653e-07 | 0.0059106 | 0.0059109 | 0.0059109 | 0.97617 | -0.16762 | 0.9758 | -0.17024 | 2.1892
83 | -0.0023781 | -0.000596 | 0.0023782 | 0.00059592 | 6.9248e-08 | -8.2174e-08 | 0.0035978 | 0.0035978 | 0.0035978 | 0.98355 | -0.11524 | 0.98358 | -0.11503 | 1.3325
84 | 0.028254 | 0.0070905 | -0.02825 | -0.0070892 | 4.5519e-06 | 1.2947e-06 | 0.042745 | 0.042745 | 0.042745 | 0.98366 | -0.11445 | 0.98349 | -0.11561 | 5.2771
85 | 0.026709 | 0.0067032 | -0.026707 | -0.0067025 | 2.3523e-06 | 6.4116e-07 | 0.040414 | 0.040414 | 0.040414 | 0.98349 | -0.11561 | 0.9834 | -0.11625 | 4.9894
86 | 0.013951 | 0.0034952 | -0.013948 | -0.0034941 | 3.001e-06 | 1.018e-06 | 0.021137 | 0.021137 | 0.021137 | 0.98213 | -0.1253 | 0.98192 | -0.12686 | 7.8285
87 | 0.022814 | 0.0057269 | -0.022785 | -0.0057175 | 2.9527e-05 | 9.3446e-06 | 0.034524 | 0.034525 | 0.034525 | 0.9834 | -0.11625 | 0.98209 | -0.12557 | 6.3935
88 | 0.021734 | 0.0054541 | -0.021715 | -0.0054473 | 1.8655e-05 | 6.8264e-06 | 0.032932 | 0.032932 | 0.032932 | 0.98209 | -0.12557 | 0.98122 | -0.13176 | 12.1972
89 | 0.020446 | 0.0051293 | -0.020421 | -0.00512 | 2.5491e-05 | 9.2684e-06 | 0.031008 | 0.031008 | 0.031008 | 0.98122 | -0.13176 | 0.97996 | -0.14076 | 11.4845
90 | 0.00081531 | 0.00020353 | -0.00081525 | -0.00020432 | 6.1515e-08 | -7.8682e-07 | 0.0012377 | 0.001238 | 0.001238 | 0.97996 | -0.14076 | 0.97988 | -0.14131 | 0.45852
91 | 0.019605 | 0.0049165 | -0.019597 | -0.0049136 | 7.9682e-06 | 2.8832e-06 | 0.029771 | 0.029771 | 0.029771 | 0.97996 | -0.14076 | 0.97955 | -0.1437 | 11.0261
92 | 0.018653 | 0.004677 | -0.018649 | -0.0046756 | 3.9096e-06 | 1.4055e-06 | 0.028336 | 0.028336 | 0.028336 | 0.97955 | -0.1437 | 0.97934 | -0.14521 | 10.495
93 | -0.00069002 | -0.00017294 | 0.00069004 | 0.00017265 | 1.5266e-08 | -2.8553e-07 | 0.0010381 | 0.001038 | 0.0010381 | 0.98908 | -0.076079 | 0.9891 | -0.075919 | 0.38448
94 | -0.01505 | -0.0037715 | 0.015056 | 0.0037733 | 5.0609e-06 | 1.7485e-06 | 0.022785 | 0.022785 | 0.022785 | 0.98288 | -0.12035 | 0.98322 | -0.11792 | 8.439
95 | -0.016849 | -0.0042227 | 0.016861 | 0.0042269 | 1.1945e-05 | 4.2206e-06 | 0.025499 | 0.025499 | 0.025499 | 0.98322 | -0.11792 | 0.98394 | -0.11281 | 9.4442
96 | 0.0074102 | 0.0018547 | -0.007405 | -0.0018535 | 5.2106e-06 | 1.1601e-06 | 0.011206 | 0.011206 | 0.011206 | 0.98394 | -0.11281 | 0.98322 | -0.1179 | 4.1504
97 | -0.024271 | -0.0060816 | 0.024282 | 0.0060858 | 1.1349e-05 | 4.1933e-06 | 0.036705 | 0.036705 | 0.036705 | 0.98394 | -0.11281 | 0.98441 | -0.10943 | 13.5944
98 | 0.0018833 | 0.00047172 | -0.0018832 | -0.00047192 | 9.3542e-08 | -1.9806e-07 | 0.0028501 | 0.0028502 | 0.0028502 | 0.98322 | -0.1179 | 0.98317 | -0.11826 | 1.0556
99 | 0.0055217 | 0.0013818 | -0.0055199 | -0.0013817 | 1.79e-06 | 1.6758e-07 | 0.0083559 | 0.0083561 | 0.0083561 | 0.98322 | -0.1179 | 0.98289 | -0.12025 | 3.0949
100 | -0.025166 | -0.0063072 | 0.025197 | 0.0063187 | 3.0967e-05 | 1.1474e-05 | 0.03804 | 0.03804 | 0.03804 | 0.98441 | -0.10943 | 0.98566 | -0.10055 | 14.0889
101 | 0.00069634 | 0.00017446 | -0.00069634 | -0.00017452 | 3.1123e-09 | -5.575e-08 | 0.0010539 | 0.0010539 | 0.0010539 | 0.98317 | -0.11826 | 0.98317 | -0.11829 | 0.39033
102 | 0.0055199 | 0.0013817 | -0.0055194 | -0.0013816 | 5.4265e-07 | 5.0877e-08 | 0.0083561 | 0.0083562 | 0.0083562 | 0.98289 | -0.12025 | 0.98279 | -0.12096 | 3.0949
103 | 0.0038302 | 0.00095959 | -0.0038298 | -0.00095968 | 3.9765e-07 | -8.9967e-08 | 0.0057822 | 0.0057823 | 0.0057823 | 0.98566 | -0.10055 | 0.98555 | -0.1013 | 2.1416
104 | -0.029663 | -0.0074378 | 0.029676 | 0.0074424 | 1.232e-05 | 4.6131e-06 | 0.044783 | 0.044783 | 0.044783 | 0.98566 | -0.10055 | 0.98608 | -0.097554 | 16.5863
105 | 0.0045872 | 0.001148 | -0.0045865 | -0.001148 | 6.4537e-07 | -2.3475e-08 | 0.0069447 | 0.0069448 | 0.0069448 | 0.98279 | -0.12096 | 0.98265 | -0.12198 | 2.5722
106 | 0.0022816 | 0.00057166 | -0.0022815 | -0.00057179 | 9.9907e-08 | -1.335e-07 | 0.0034447 | 0.0034448 | 0.0034448 | 0.98555 | -0.1013 | 0.98551 | -0.10162 | 1.2758
107 | -0.030048 | -0.0075357 | 0.030075 | 0.0075457 | 2.6765e-05 | 1.0028e-05 | 0.045345 | 0.045345 | 0.045345 | 0.98608 | -0.097554 | 0.98699 | -0.091134 | 16.7944
108 | -0.033893 | -0.0085022 | 0.033911 | 0.0085087 | 1.7214e-05 | 6.4855e-06 | 0.051102 | 0.051101 | 0.051102 | 0.98699 | -0.091134 | 0.98751 | -0.087474 | 18.9265
109 | 0.0038186 | 0.00095645 | -0.0038181 | -0.00095656 | 4.5729e-07 | -1.0668e-07 | 0.0057568 | 0.0057569 | 0.0057569 | 0.98699 | -0.091134 | 0.98687 | -0.092 | 2.1322
110 | -0.035342 | -0.0088674 | 0.035379 | 0.0088812 | 3.6477e-05 | 1.3766e-05 | 0.053258 | 0.053258 | 0.053258 | 0.98751 | -0.087474 | 0.98856 | -0.080043 | 19.7253
111 | 0.0025884 | 0.00064835 | -0.0025884 | -0.00064837 | 1.7575e-08 | -1.6867e-08 | 0.0039027 | 0.0039027 | 0.0039027 | 0.98687 | -0.092 | 0.98686 | -0.092049 | 1.4454
112 | -0.041323 | -0.010369 | 0.041388 | 0.010394 | 6.4921e-05 | 2.4624e-05 | 0.062206 | 0.062206 | 0.062206 | 0.98856 | -0.080043 | 0.99016 | -0.06874 | 23.0391
113 | 0.0017034 | 0.00042657 | -0.0017033 | -0.00042688 | 1.1417e-07 | -3.1047e-07 | 0.0025683 | 0.0025684 | 0.0025684 | 0.98686 | -0.092049 | 0.98679 | -0.092534 | 0.95126
114 | 0.0050415 | 0.0012629 | -0.0050408 | -0.0012629 | 7.1748e-07 | 1.8336e-08 | 0.0075762 | 0.0075763 | 0.0075763 | 0.99016 | -0.06874 | 0.99001 | -0.069768 | 2.806
115 | 0.0036742 | 0.00092041 | -0.0036741 | -0.00092043 | 5.6952e-08 | -1.6579e-08 | 0.0055223 | 0.0055223 | 0.0055223 | 0.99001 | -0.069768 | 0.99 | -0.069881 | 2.0453
116 | 0.0022932 | 0.00057433 | -0.0022931 | -0.00057448 | 1.1332e-07 | -1.5297e-07 | 0.0034466 | 0.0034467 | 0.0034467 | 0.99 | -0.069881 | 0.98995 | -0.070238 | 1.2765
117 | 0.0011894 | 0.00029788 | -0.0011894 | -0.00029802 | 2.4085e-08 | -1.4599e-07 | 0.0017878 | 0.0017878 | 0.0017878 | 0.98995 | -0.070238 | 0.98993 | -0.070384 | 0.66215
118 | 0.00058603 | 0.00014681 | -0.00058603 | -0.00014687 | 2.4277e-09 | -6.3528e-08 | 0.00088087 | 0.00088089 | 0.00088089 | 0.98993 | -0.070384 | 0.98992 | -0.070414 | 0.32626
119 | 0.0011262 | 0.00028211 | -0.0011262 | -0.00028225 | 2.0835e-08 | -1.4475e-07 | 0.0016845 | 0.0016846 | 0.0016846 | 0.99482 | -0.036077 | 0.9948 | -0.036211 | 0.62391
120 | -0.13763 | -0.034722 | 0.13774 | 0.034763 | 0.00010731 | 4.0795e-05 | 0.20545 | 0.20545 | 0.20545 | 0.9972 | -0.019383 | 0.998 | -0.013829 | 25.3648
121 | 0.13641 | 0.034417 | -0.13636 | -0.034395 | 5.7616e-05 | 2.1899e-05 | 0.20364 | 0.20364 | 0.20364 | 0.9972 | -0.019383 | 0.99676 | -0.022395 | 25.1403
122 | 0.1361 | 0.03433 | -0.13602 | -0.034302 | 7.5285e-05 | 2.8613e-05 | 0.20325 | 0.20325 | 0.20325 | 0.99676 | -0.022395 | 0.99619 | -0.026341 | 25.0927
123 | 0.1358 | 0.034247 | -0.13569 | -0.034205 | 0.00011047 | 4.1984e-05 | 0.20292 | 0.20292 | 0.20292 | 0.99619 | -0.026341 | 0.99536 | -0.032149 | 25.0523
124 | 0.13423 | 0.033839 | -0.13421 | -0.033829 | 2.5932e-05 | 9.8532e-06 | 0.20074 | 0.20074 | 0.20074 | 0.99536 | -0.032149 | 0.99516 | -0.033529 | 24.7829
125 | 0.13259 | 0.033423 | -0.13241 | -0.033356 | 0.00017683 | 6.717e-05 | 0.19832 | 0.19832 | 0.19832 | 0.99516 | -0.033529 | 0.99379 | -0.043064 | 24.484
126 | -0.00080444 | -0.00020161 | 0.00080445 | 0.00020152 | 6.9122e-09 | -9.123e-08 | 0.0012204 | 0.0012203 | 0.0012204 | 0.98088 | -0.13428 | 0.98089 | -0.13422 | 0.45198
127 | 0.13195 | 0.033239 | -0.1318 | -0.033183 | 0.00014831 | 5.6335e-05 | 0.19762 | 0.19762 | 0.19762 | 0.99379 | -0.043064 | 0.99264 | -0.051109 | 24.398
128 | 0.13004 | 0.032743 | -0.13003 | -0.032739 | 1.1862e-05 | 4.5043e-06 | 0.19499 | 0.19499 | 0.19499 | 0.99264 | -0.051109 | 0.99254 | -0.051762 | 24.0732
129 | 0.12686 | 0.031944 | -0.12665 | -0.031864 | 0.00021261 | 8.0682e-05 | 0.19024 | 0.19024 | 0.19024 | 0.99254 | -0.051762 | 0.99083 | -0.063775 | 23.4866
130 | 0.08847 | 0.022242 | -0.088394 | -0.022213 | 7.6374e-05 | 2.8572e-05 | 0.13289 | 0.13289 | 0.13289 | 0.99083 | -0.063775 | 0.98995 | -0.069978 | 16.406
131 | 0.038177 | 0.0096221 | -0.038113 | -0.0095979 | 6.3813e-05 | 2.4144e-05 | 0.057353 | 0.057353 | 0.057353 | 0.99083 | -0.063775 | 0.98912 | -0.075734 | 21.242
132 | 0.037896 | 0.0095434 | -0.037851 | -0.0095267 | 4.4266e-05 | 1.6746e-05 | 0.057026 | 0.057026 | 0.057026 | 0.98912 | -0.075734 | 0.98793 | -0.0841 | 21.1207
133 | 0.017958 | 0.0045024 | -0.017955 | -0.0045012 | 3.2999e-06 | 1.1798e-06 | 0.027287 | 0.027287 | 0.027287 | 0.97934 | -0.14521 | 0.97915 | -0.14654 | 10.1061
134 | 0.016717 | 0.0041909 | -0.016712 | -0.0041893 | 4.4473e-06 | 1.5716e-06 | 0.025405 | 0.025405 | 0.025405 | 0.97915 | -0.14654 | 0.97888 | -0.14846 | 9.4093
135 | 0.015124 | 0.0037913 | -0.015124 | -0.0037912 | 4.5592e-07 | 1.5798e-07 | 0.022991 | 0.022991 | 0.022991 | 0.97888 | -0.14846 | 0.97885 | -0.14867 | 8.5152
136 | 0.014047 | 0.0035213 | -0.014039 | -0.0035186 | 7.9154e-06 | 2.6949e-06 | 0.021354 | 0.021354 | 0.021354 | 0.97885 | -0.14867 | 0.97828 | -0.15274 | 7.9091
137 | 0.0022733 | 0.00056914 | -0.0022731 | -0.00056941 | 2.0612e-07 | -2.6761e-07 | 0.0034575 | 0.0034577 | 0.0034577 | 0.97828 | -0.15274 | 0.97819 | -0.1534 | 1.2806
138 | 0.011766 | 0.0029495 | -0.011751 | -0.0029447 | 1.4911e-05 | 4.7997e-06 | 0.017897 | 0.017897 | 0.017897 | 0.97828 | -0.15274 | 0.977 | -0.1619 | 6.6286
139 | 0.0022731 | 0.00056941 | -0.0022729 | -0.00056964 | 1.7517e-07 | -2.2736e-07 | 0.0034577 | 0.0034578 | 0.0034578 | 0.97819 | -0.1534 | 0.97811 | -0.15396 | 1.2807
140 | 0.0099623 | 0.0024964 | -0.009953 | -0.0024936 | 9.3515e-06 | 2.7823e-06 | 0.015173 | 0.015173 | 0.015173 | 0.977 | -0.1619 | 0.97606 | -0.16869 | 5.6197
141 | 0.0011314 | 0.00028301 | -0.0011313 | -0.00028354 | 8.354e-08 | -5.3033e-07 | 0.0017246 | 0.0017248 | 0.0017248 | 0.97606 | -0.16869 | 0.97598 | -0.16923 | 0.63883
142 | 0.0088216 | 0.0022106 | -0.0088172 | -0.0022094 | 4.3953e-06 | 1.204e-06 | 0.013449 | 0.013449 | 0.013449 | 0.97606 | -0.16869 | 0.97556 | -0.17229 | 4.981
143 | 0.00035471 | 8.8278e-05 | -0.0003547 | -8.8896e-05 | 9.0926e-09 | -6.1828e-07 | 0.00054081 | 0.00054104 | 0.00054104 | 0.97556 | -0.17229 | 0.97553 | -0.17248 | 0.20038
144 | 0.0084625 | 0.0021211 | -0.0084462 | -0.0021168 | 1.6227e-05 | 4.2963e-06 | 0.012908 | 0.012909 | 0.012909 | 0.97556 | -0.17229 | 0.97363 | -0.18616 | 4.781
145 | 0.0036538 | 0.00091424 | -0.0036536 | -0.0009143 | 2.1199e-07 | -5.9063e-08 | 0.0055324 | 0.0055325 | 0.0055325 | 0.98265 | -0.12198 | 0.98259 | -0.1224 | 2.0491
146 | 0.0024593 | 0.00061496 | -0.0024589 | -0.0006154 | 4.0863e-07 | -4.4089e-07 | 0.0037238 | 0.003724 | 0.003724 | 0.98259 | -0.1224 | 0.98242 | -0.1236 | 1.3792
147 | 0.001415 | 0.00035377 | -0.0014148 | -0.00035457 | 1.9784e-07 | -7.9796e-07 | 0.0021428 | 0.0021432 | 0.0021432 | 0.98242 | -0.1236 | 0.98228 | -0.12462 | 0.79376

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20103 | 0.050545

## res_load
| p_mw | q_mvar
0 | 0.0066843 | 0.0016752
1 | 0.0046622 | 0.0011685
2 | 0.0044079 | 0.0011047
3 | 0.003437 | 0.0008614
4 | 0.0022789 | 0.00057114
5 | 0.0017512 | 0.0004389
6 | 0.00053809 | 0.00013486
7 | 0.0052506 | 0.0013159
8 | 0.0018376 | 0.00046055
9 | 0.001726 | 0.00043258
10 | 0.0028455 | 0.00071316
11 | 0.0014457 | 0.00036233
12 | 0.00057417 | 0.0001439
13 | 0.00084267 | 0.00021119
14 | 0.0014079 | 0.00035286
15 | 0.0010326 | 0.00025879
16 | 0.00089528 | 0.00022438
17 | 0.00061791 | 0.00015486
18 | 0.0022409 | 0.00056163
19 | 0.00069753 | 0.00017482
20 | 0.00090276 | 0.00022625
21 | 0.001027 | 0.00025739
22 | 0.00028721 | 7.198e-05
23 | 0.0018048 | 0.00045231
24 | 0.00069795 | 0.00017492
25 | 0.00092725 | 0.00023239
26 | 0.0014727 | 0.0003691
27 | 0.0013269 | 0.00033256
28 | 0.00084969 | 0.00021295
29 | 0.0010752 | 0.00026947
30 | 0.00093789 | 0.00023506
31 | 0.0049718 | 0.0012461
32 | 0.002492 | 0.00062455
33 | 0.0011239 | 0.00028169
34 | 0.0010359 | 0.00025963
35 | 0.0011262 | 0.00028226
36 | 0.00046617 | 0.00011683
37 | 0.0028531 | 0.00071507
38 | 0.0031076 | 0.00077884
39 | 0.0098975 | 0.0024806
40 | 0.0018315 | 0.00045901
41 | 0.00066441 | 0.00016652
42 | 0.00059787 | 0.00014984
43 | 0.00075953 | 0.00019036
44 | 0.001918 | 0.00048069
45 | 0.00095569 | 0.00023952
46 | 0.0010383 | 0.00026022
47 | 0.001306 | 0.00032733
48 | 0.0033604 | 0.00084218
49 | 0.00062165 | 0.0001558
50 | 0.0008364 | 0.00020962
51 | 0.001095 | 0.00027443
52 | 0.00062654 | 0.00015702
53 | 0.00060655 | 0.00015202
54 | 0.00079662 | 0.00019965
55 | 0.0012119 | 0.00030373
56 | 0.0021767 | 0.00054552
57 | 0.0018903 | 0.00047375
58 | 0.001016 | 0.00025463
59 | 0.00067818 | 0.00016997
60 | 0.0012655 | 0.00031716
61 | 0.0038762 | 0.00097146
62 | 0.0023781 | 0.000596
63 | 0.001246 | 0.00031227
64 | 0.00073871 | 0.00018514
65 | 0.0015405 | 0.00038607
66 | 0.0015876 | 0.00039788
67 | 0.0038928 | 0.00097564
68 | 0.001051 | 0.00026341
69 | 0.0012689 | 0.00031802
70 | 0.00081525 | 0.00020432
71 | 0.00094415 | 0.00023663
72 | 0.00069002 | 0.00017294
73 | 0.0014076 | 0.00035278
74 | 0.0020414 | 0.00051162
75 | 0.0017933 | 0.00044944
76 | 0.00088337 | 0.00022139
77 | 0.0011869 | 0.00029745
78 | 0.00063657 | 0.00015954
79 | 0.00069634 | 0.00017452
80 | 0.00093222 | 0.00023364
81 | 0.0015482 | 0.00038802
82 | 0.00037223 | 9.3289e-05
83 | 0.0022815 | 0.00057179
84 | 0.0014314 | 0.00035875
85 | 0.0012298 | 0.00030821
86 | 0.000885 | 0.0002218
87 | 0.0017033 | 0.00042688
88 | 0.0013666 | 0.0003425
89 | 0.001381 | 0.0003461
90 | 0.0011037 | 0.0002766
91 | 0.00060335 | 0.00015121
92 | 0.00058603 | 0.00014687
93 | 0.0010403 | 0.00026073
94 | 0.0011262 | 0.00028225
95 | 0.0022871 | 0.0005732
96 | 0.0012184 | 0.00030536
97 | 0.00084133 | 0.00021086
98 | 0.0002586 | 6.4812e-05
99 | 0.00021919 | 5.4935e-05
100 | 0.0014593 | 0.00036574
101 | 0.0016196 | 0.00040591
102 | 0.00080444 | 0.00020161
103 | 0.00072159 | 0.00018085
104 | 0.00077594 | 0.00019447
105 | 0.00046517 | 0.00011658
106 | 0.0017555 | 0.00043996
107 | 0.0031695 | 0.00079435
108 | 0.0022591 | 0.00056618
109 | 0.00021766 | 5.455e-05
110 | 0.00077635 | 0.00019457
111 | 0.00069095 | 0.00017317
112 | 0.0012381 | 0.00031031
113 | 0.001588 | 0.00039799
114 | 0.0010767 | 0.00026985
115 | 0.0017888 | 0.00044831
116 | 0.0022729 | 0.00056964
117 | 0.0011313 | 0.00028354
118 | 0.0009327 | 0.00023376
119 | 0.0011944 | 0.00029934
120 | 0.0010439 | 0.00026162
121 | 0.0014148 | 0.00035457
122 | 0.0003547 | 8.8896e-05
123 | 0.0084462 | 0.0021168

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1