## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2053-28_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2053-28_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2053-28_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2053-28_0_4_node_30 | 0.4 | n |  | TRUE
4 | bus_LV_2053-28_0_4_node_39 | 0.4 | n |  | TRUE
5 | bus_LV_2053-28_0_4_node_35 | 0.4 | n |  | TRUE
6 | bus_LV_2053-28_0_4_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_2053-28_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_2053-28_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2053-28_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2053-28_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2053-28_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2053-28_0_4_node_55 | 0.4 | n |  | TRUE
13 | bus_LV_2053-28_0_4_node_54 | 0.4 | n |  | TRUE
14 | bus_LV_2053-28_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2053-28_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2053-28_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2053-28_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2053-28_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2053-28_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_2053-28_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_2053-28_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2053-28_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_2053-28_0_4_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2053-28_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_2053-28_0_4_node_72 | 0.4 | n |  | TRUE
26 | bus_LV_2053-28_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_2053-28_0_4_node_73 | 0.4 | n |  | TRUE
28 | bus_LV_2053-28_0_4_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_2053-28_0_4_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_2053-28_0_4_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_2053-28_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_2053-28_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_2053-28_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2053-28_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_2053-28_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_2053-28_0_4_node_71 | 0.4 | n |  | TRUE
37 | bus_LV_2053-28_0_4_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_2053-28_0_4_node_70 | 0.4 | n |  | TRUE
39 | bus_LV_2053-28_0_4_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_2053-28_0_4_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_2053-28_0_4_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_2053-28_0_4_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_2053-28_0_4_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_2053-28_0_4_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_2053-28_0_4_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_2053-28_0_4_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_2053-28_0_4_node_85 | 0.4 | n |  | TRUE
48 | bus_LV_2053-28_0_4_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_2053-28_0_4_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_2053-28_0_4_node_86 | 0.4 | n |  | TRUE
51 | bus_LV_2053-28_0_4_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_2053-28_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_2053-28_0_4_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_2053-28_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_2053-28_0_4_node_80 | 0.4 | n |  | TRUE
56 | bus_LV_2053-28_0_4_node_78 | 0.4 | n |  | TRUE
57 | bus_LV_2053-28_0_4_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_2053-28_0_4_node_83 | 0.4 | n |  | TRUE
59 | bus_LV_2053-28_0_4_node_81 | 0.4 | n |  | TRUE
60 | bus_LV_2053-28_0_4_node_76 | 0.4 | n |  | TRUE
61 | bus_LV_2053-28_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_2053-28_0_4_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_2053-28_0_4_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_2053-28_0_4_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_2053-28_0_4_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_2053-28_0_4_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_2053-28_0_4_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_2053-28_0_4_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_2053-28_0_4_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_2053-28_0_4_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_2053-28_0_4_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_2053-28_0_4_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_2053-28_0_4_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_2053-28_0_4_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_2053-28_0_4_node_75 | 0.4 | n |  | TRUE
76 | bus_LV_2053-28_0_4_node_77 | 0.4 | n |  | TRUE
77 | bus_LV_2053-28_0_4_node_79 | 0.4 | n |  | TRUE
78 | bus_LV_2053-28_0_4_node_84 | 0.4 | n |  | TRUE
79 | bus_LV_2053-28_0_4_node_82 | 0.4 | n |  | TRUE
80 | bus_MV_377_1_node_249 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2053-28_0_4_load_0 | 0 | 0.00080258 | 0.00020114 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2053-28_0_4_load_3 | 2 | 0.01348 | 0.0033785 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2053-28_0_4_load_39 | 4 | 0.0046518 | 0.0011659 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2053-28_0_4_load_35 | 5 | 0.0021701 | 0.00054387 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2053-28_0_4_load_4 | 7 | 0.002997 | 0.00075113 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2053-28_0_4_load_5 | 8 | 0.0051624 | 0.0012938 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2053-28_0_4_load_7 | 10 | 0.0021547 | 0.00054001 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2053-28_0_4_load_55 | 12 | 0.0068793 | 0.0017241 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2053-28_0_4_load_54 | 13 | 0.0040688 | 0.0010197 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2053-28_0_4_load_9 | 14 | 0.001481 | 0.00037118 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2053-28_0_4_load_10 | 15 | 0.00045997 | 0.00011528 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2053-28_0_4_load_12 | 16 | 0.001389 | 0.00034812 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2053-28_0_4_load_13 | 17 | 0.00087567 | 0.00021946 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2053-28_0_4_load_14 | 18 | 0.0019062 | 0.00047773 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2053-28_0_4_load_19 | 20 | 0.00088177 | 0.00022099 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2053-28_0_4_load_15 | 21 | 0.0017215 | 0.00043145 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2053-28_0_4_load_16 | 22 | 0.0015222 | 0.00038149 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2053-28_0_4_load_18 | 23 | 0.0052245 | 0.0013094 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2053-28_0_4_load_20 | 24 | 0.00090624 | 0.00022713 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2053-28_0_4_load_72 | 25 | 0.0040471 | 0.0010143 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2053-28_0_4_load_21 | 26 | 0.0044813 | 0.0011231 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2053-28_0_4_load_73 | 27 | 0.0017732 | 0.00044442 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2053-28_0_4_load_31 | 28 | 0.0020932 | 0.00052461 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2053-28_0_4_load_29 | 29 | 0.0014674 | 0.00036777 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2053-28_0_4_load_22 | 30 | 0.0026227 | 0.0006573 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2053-28_0_4_load_23 | 31 | 0.0019869 | 0.00049796 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2053-28_0_4_load_24 | 32 | 0.00085381 | 0.00021399 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2053-28_0_4_load_25 | 33 | 0.007465 | 0.0018709 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2053-28_0_4_load_26 | 34 | 0.0031503 | 0.00078954 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2053-28_0_4_load_28 | 35 | 0.0076597 | 0.0019197 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2053-28_0_4_load_71 | 36 | 0.0054095 | 0.0013558 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2053-28_0_4_load_70 | 38 | 0.0030687 | 0.00076909 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2053-28_0_4_load_32 | 39 | 0.0043319 | 0.0010857 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2053-28_0_4_load_36 | 41 | 0.0069077 | 0.0017312 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2053-28_0_4_load_38 | 43 | 0.029383 | 0.007364 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2053-28_0_4_load_53 | 44 | 0.0069078 | 0.0017312 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2053-28_0_4_load_40 | 46 | 0.003775 | 0.0009461 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2053-28_0_4_load_85 | 47 | 0.0016691 | 0.00041832 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2053-28_0_4_load_41 | 48 | 0.0060972 | 0.0015281 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2053-28_0_4_load_42 | 49 | 0.0015863 | 0.00039757 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2053-28_0_4_load_86 | 50 | 0.0069087 | 0.0017315 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2053-28_0_4_load_44 | 51 | 0.0010009 | 0.00025085 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2053-28_0_4_load_48 | 54 | 0.00053798 | 0.00013483 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2053-28_0_4_load_78 | 56 | 0.0011205 | 0.00028083 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2053-28_0_4_load_51 | 57 | 0.00092077 | 0.00023077 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2053-28_0_4_load_83 | 58 | 0.0020802 | 0.00052134 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2053-28_0_4_load_81 | 59 | 0.0012191 | 0.00030553 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2053-28_0_4_load_76 | 60 | 0.0018637 | 0.0004671 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2053-28_0_4_load_49 | 61 | 0.0030581 | 0.00076644 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2053-28_0_4_load_50 | 62 | 0.00094557 | 0.00023698 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2053-28_0_4_load_56 | 64 | 0.00092155 | 0.00023096 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2053-28_0_4_load_57 | 65 | 0.00066975 | 0.00016786 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2053-28_0_4_load_58 | 66 | 0.0012093 | 0.00030309 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2053-28_0_4_load_59 | 67 | 0.00086778 | 0.00021749 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2053-28_0_4_load_61 | 68 | 0.0021199 | 0.00053129 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2053-28_0_4_load_62 | 69 | 0.0041852 | 0.0010489 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2053-28_0_4_load_66 | 71 | 0.0019237 | 0.00048212 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2053-28_0_4_load_67 | 72 | 0.0017402 | 0.00043613 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2053-28_0_4_load_68 | 73 | 0.0051183 | 0.0012828 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2053-28_0_4_load_69 | 74 | 0.00149 | 0.00037342 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2053-28_0_4_load_75 | 75 | 0.0019886 | 0.00049838 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2053-28_0_4_load_77 | 76 | 0.0013446 | 0.00033699 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2053-28_0_4_load_79 | 77 | 0.0013881 | 0.00034789 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2053-28_0_4_load_84 | 78 | 0.002003 | 0.000502 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2053-28_0_4_load_82 | 79 | 0.0016759 | 0.00042002 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2053-28_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.027369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2053-28_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.019408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2053-28_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.045865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2053-28_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.018362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2053-28_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.045841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_2053-28_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.047168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2053-28_0_4_line_6 | NAYY 4x150 SE | 4 | 10 | 0.0037639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2053-28_0_4_line_7 | NAYY 4x150 SE | 5 | 37 | 0.0052257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_2053-28_0_4_line_8 | NAYY 4x150 SE | 6 | 28 | 0.015683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2053-28_0_4_line_9 | NAYY 4x150 SE | 6 | 29 | 0.043298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2053-28_0_4_line_10 | NAYY 4x150 SE | 6 | 26 | 0.021358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2053-28_0_4_line_11 | NAYY 4x150 SE | 7 | 8 | 0.003115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2053-28_0_4_line_12 | NAYY 4x150 SE | 7 | 9 | 0.049423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2053-28_0_4_line_13 | NAYY 4x150 SE | 8 | 10 | 0.049655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2053-28_0_4_line_14 | NAYY 4x150 SE | 9 | 11 | 0.005706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2053-28_0_4_line_15 | NAYY 4x150 SE | 11 | 12 | 0.020842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2053-28_0_4_line_16 | NAYY 4x150 SE | 12 | 13 | 0.029497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2053-28_0_4_line_17 | NAYY 4x150 SE | 13 | 63 | 0.028037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2053-28_0_4_line_18 | NAYY 4x150 SE | 14 | 15 | 0.0087674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2053-28_0_4_line_19 | NAYY 4x150 SE | 15 | 16 | 0.014801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2053-28_0_4_line_20 | NAYY 4x150 SE | 16 | 17 | 0.0015941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2053-28_0_4_line_21 | NAYY 4x150 SE | 17 | 18 | 0.0029671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2053-28_0_4_line_22 | NAYY 4x150 SE | 18 | 19 | 0.0023364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2053-28_0_4_line_23 | NAYY 4x150 SE | 19 | 20 | 0.023154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2053-28_0_4_line_24 | NAYY 4x150 SE | 19 | 21 | 0.016664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2053-28_0_4_line_25 | NAYY 4x150 SE | 20 | 25 | 0.014629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2053-28_0_4_line_26 | NAYY 4x150 SE | 21 | 22 | 0.010457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2053-28_0_4_line_27 | NAYY 4x150 SE | 22 | 23 | 0.0092428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2053-28_0_4_line_28 | NAYY 4x150 SE | 23 | 24 | 0.018476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2053-28_0_4_line_29 | NAYY 4x150 SE | 24 | 26 | 0.033839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2053-28_0_4_line_30 | NAYY 4x150 SE | 25 | 27 | 0.027131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2053-28_0_4_line_31 | NAYY 4x150 SE | 28 | 36 | 0.020071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2053-28_0_4_line_32 | NAYY 4x150 SE | 29 | 34 | 0.0029204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2053-28_0_4_line_33 | NAYY 4x150 SE | 30 | 31 | 0.017949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2053-28_0_4_line_34 | NAYY 4x150 SE | 30 | 32 | 0.0019755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2053-28_0_4_line_35 | NAYY 4x150 SE | 31 | 33 | 0.037732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2053-28_0_4_line_36 | NAYY 4x150 SE | 32 | 34 | 0.0064508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2053-28_0_4_line_37 | NAYY 4x150 SE | 33 | 35 | 0.056521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2053-28_0_4_line_38 | NAYY 4x150 SE | 36 | 38 | 0.0025812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2053-28_0_4_line_39 | NAYY 4x150 SE | 37 | 41 | 0.024287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2053-28_0_4_line_40 | NAYY 4x150 SE | 37 | 39 | 0.011233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2053-28_0_4_line_41 | NAYY 4x150 SE | 38 | 74 | 0.016381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2053-28_0_4_line_42 | NAYY 4x150 SE | 39 | 40 | 0.017466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2053-28_0_4_line_43 | NAYY 4x150 SE | 40 | 42 | 0.018938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2053-28_0_4_line_44 | NAYY 4x150 SE | 40 | 43 | 0.034893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2053-28_0_4_line_45 | NAYY 4x150 SE | 41 | 44 | 0.042056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2053-28_0_4_line_46 | NAYY 4x150 SE | 42 | 45 | 0.049368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2053-28_0_4_line_47 | NAYY 4x150 SE | 42 | 46 | 0.019889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2053-28_0_4_line_48 | NAYY 4x150 SE | 45 | 47 | 0.012055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2053-28_0_4_line_49 | NAYY 4x150 SE | 46 | 48 | 0.00020427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2053-28_0_4_line_50 | NAYY 4x150 SE | 47 | 50 | 0.022187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2053-28_0_4_line_51 | NAYY 4x150 SE | 48 | 49 | 0.022718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2053-28_0_4_line_52 | NAYY 4x150 SE | 51 | 52 | 0.017236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2053-28_0_4_line_53 | NAYY 4x150 SE | 52 | 53 | 0.065655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2053-28_0_4_line_54 | NAYY 4x150 SE | 52 | 54 | 0.033892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2053-28_0_4_line_55 | NAYY 4x150 SE | 53 | 55 | 0.057395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2053-28_0_4_line_56 | NAYY 4x150 SE | 53 | 56 | 0.011487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2053-28_0_4_line_57 | NAYY 4x150 SE | 54 | 57 | 0.022932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2053-28_0_4_line_58 | NAYY 4x150 SE | 55 | 58 | 0.045326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2053-28_0_4_line_59 | NAYY 4x150 SE | 55 | 59 | 0.034465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2053-28_0_4_line_60 | NAYY 4x150 SE | 56 | 60 | 0.022939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2053-28_0_4_line_61 | NAYY 4x150 SE | 57 | 61 | 0.0020969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2053-28_0_4_line_62 | NAYY 4x150 SE | 59 | 79 | 0.0088218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2053-28_0_4_line_63 | NAYY 4x150 SE | 60 | 75 | 0.0020466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2053-28_0_4_line_64 | NAYY 4x150 SE | 61 | 62 | 0.02463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2053-28_0_4_line_65 | NAYY 4x150 SE | 62 | 63 | 0.009682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2053-28_0_4_line_66 | NAYY 4x150 SE | 63 | 64 | 0.0076875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2053-28_0_4_line_67 | NAYY 4x150 SE | 64 | 65 | 0.00077207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2053-28_0_4_line_68 | NAYY 4x150 SE | 65 | 66 | 0.0090193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2053-28_0_4_line_69 | NAYY 4x150 SE | 66 | 67 | 0.021931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2053-28_0_4_line_70 | NAYY 4x150 SE | 68 | 69 | 0.018472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2053-28_0_4_line_71 | NAYY 4x150 SE | 69 | 70 | 0.0035653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2053-28_0_4_line_72 | NAYY 4x150 SE | 70 | 71 | 0.014454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2053-28_0_4_line_73 | NAYY 4x150 SE | 70 | 72 | 0.016662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2053-28_0_4_line_74 | NAYY 4x150 SE | 71 | 73 | 0.01853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2053-28_0_4_line_75 | NAYY 4x150 SE | 73 | 74 | 0.0025078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2053-28_0_4_line_76 | NAYY 4x150 SE | 75 | 76 | 0.027869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2053-28_0_4_line_77 | NAYY 4x150 SE | 76 | 77 | 0.020766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2053-28_0_4_line_78 | NAYY 4x150 SE | 77 | 78 | 0.027816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2053-28_0_4_trafo_33 | 0.25 MVA 20/0.4 kV | 80 | 37 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2565840.5045 | 1189004.1397 | 2565854.713 | 1188980.7474
1 | 2565840.5045 | 1189004.1397 | 2565843.454 | 1189006.4352 | 2565844.1055 | 1189022.0917
2 | 2565872.3533 | 1189055.9632 | 2565844.409 | 1189029.3865 | 2565844.1055 | 1189022.0917
3 | 2565872.3533 | 1189055.9632 | 2565882.7914 | 1189040.8565
4 | 2565872.3533 | 1189055.9632 | 2565884.5529 | 1189056.7272 | 2565911.9713 | 1189076.1791
5 | 2565841.83 | 1189091.8014 | 2565849.8905 | 1189082.2946 | 2565866.9329 | 1189060.3632 | 2565872.3533 | 1189055.9632
6 | 2565882.7914 | 1189040.8565 | 2565884.9311 | 1189037.7599
7 | 2565916.2334 | 1189079.2027 | 2565911.9713 | 1189076.1791
8 | 2565841.83 | 1189091.8014 | 2565830.8955 | 1189080.5583
9 | 2565841.83 | 1189091.8014 | 2565866.1101 | 1189115.1751 | 2565869.4716 | 1189118.8579 | 2565872.7301 | 1189121.8519 | 2565872.8562 | 1189121.9866
10 | 2565841.83 | 1189091.8014 | 2565834.6076 | 1189099.8137 | 2565827.3178 | 1189107.4692
11 | 2565914.9287 | 1188994.3458 | 2565913.1579 | 1188996.9086
12 | 2565953.5778 | 1188966.2512 | 2565945.4686 | 1188972.612 | 2565924.1005 | 1188981.0718 | 2565914.9287 | 1188994.3458
13 | 2565884.9311 | 1189037.7599 | 2565913.1579 | 1188996.9086
14 | 2565953.5778 | 1188966.2512 | 2565957.3746 | 1188961.9828
15 | 2565957.3746 | 1188961.9828 | 2565967.8944 | 1188963.7127 | 2565977.0381 | 1188968.1901
16 | 2566003.7311 | 1188980.7232 | 2565994.8698 | 1188976.9216 | 2565977.0381 | 1188968.1901
17 | 2566029.4966 | 1188991.7769 | 2566003.7311 | 1188980.7232
18 | 2565742.3763 | 1189190.722 | 2565749.2223 | 1189185.2447
19 | 2565760.7798 | 1189175.9979 | 2565749.2223 | 1189185.2447
20 | 2565760.7798 | 1189175.9979 | 2565762.0245 | 1189175.0021
21 | 2565764.3413 | 1189173.1484 | 2565762.0245 | 1189175.0021
22 | 2565766.1657 | 1189171.6888 | 2565764.3413 | 1189173.1484
23 | 2565766.1657 | 1189171.6888 | 2565746.2346 | 1189159.9051
24 | 2565766.1657 | 1189171.6888 | 2565777.657 | 1189159.6211
25 | 2565733.6417 | 1189152.4599 | 2565746.2346 | 1189159.9051
26 | 2565784.8678 | 1189152.0485 | 2565777.657 | 1189159.6211
27 | 2565784.8678 | 1189152.0485 | 2565791.2417 | 1189145.355
28 | 2565791.2417 | 1189145.355 | 2565803.9827 | 1189131.9748
29 | 2565827.3178 | 1189107.4692 | 2565803.9827 | 1189131.9748
30 | 2565733.6417 | 1189152.4599 | 2565710.2874 | 1189138.6522
31 | 2565816.9018 | 1189066.1696 | 2565830.8955 | 1189080.5583
32 | 2565872.8562 | 1189121.9866 | 2565874.853 | 1189124.1178
33 | 2565880.614 | 1189130.2669 | 2565892.8859 | 1189143.3654
34 | 2565879.2634 | 1189128.8253 | 2565880.614 | 1189130.2669
35 | 2565917.8076 | 1189171.6872 | 2565899.7179 | 1189150.6576 | 2565892.8859 | 1189143.3654
36 | 2565879.2634 | 1189128.8253 | 2565874.853 | 1189124.1178
37 | 2565954.6663 | 1189214.536 | 2565917.8076 | 1189171.6872
38 | 2565815.1022 | 1189064.3192 | 2565816.9018 | 1189066.1696
39 | 2565916.2334 | 1189079.2027 | 2565932.2349 | 1189060.9324
40 | 2565916.2334 | 1189079.2027 | 2565925.2422 | 1189085.9133
41 | 2565815.1022 | 1189064.3192 | 2565811.1652 | 1189060.2711 | 2565803.348 | 1189052.9145
42 | 2565939.2497 | 1189096.3472 | 2565925.2422 | 1189085.9133
43 | 2565954.9832 | 1189106.9521 | 2565939.2497 | 1189096.3472
44 | 2565913.5532 | 1189120.0289 | 2565939.2497 | 1189096.3472
45 | 2565959.9432 | 1189029.2942 | 2565948.2024 | 1189042.7007 | 2565932.2349 | 1189060.9324
46 | 2565954.9832 | 1189106.9521 | 2565975.8191 | 1189116.2605 | 2565994.9118 | 1189119.4646 | 2566002.2244 | 1189119.2117
47 | 2565954.9832 | 1189106.9521 | 2565967.7294 | 1189091.685
48 | 2566002.2244 | 1189119.2117 | 2565998.9399 | 1189107.613
49 | 2565967.8604 | 1189091.5282 | 2565967.7294 | 1189091.685
50 | 2565997.0089 | 1189091.3042 | 2565991.7623 | 1189104.7969 | 2565998.9399 | 1189107.613
51 | 2565982.4199 | 1189074.0892 | 2565967.8604 | 1189091.5282
52 | 2566064.3751 | 1189075.0566 | 2566053.8263 | 1189082.9208 | 2566051.3919 | 1189086.1932
53 | 2566128.3254 | 1189079.04 | 2566092.3793 | 1189069.4389 | 2566079.1791 | 1189071.0925 | 2566064.3751 | 1189075.0566
54 | 2566064.3751 | 1189075.0566 | 2566055.5337 | 1189069.3371 | 2566052.7828 | 1189052.3325 | 2566050.0863 | 1189046.8207
55 | 2566185.3358 | 1189076.3931 | 2566153.3175 | 1189081.5885 | 2566128.3254 | 1189079.04
56 | 2566128.3254 | 1189079.04 | 2566128.6423 | 1189090.5221
57 | 2566050.0863 | 1189046.8207 | 2566046.8874 | 1189040.2818 | 2566040.4371 | 1189029.924 | 2566039.0609 | 1189026.7603
58 | 2566185.3358 | 1189076.3931 | 2566223.472 | 1189051.8964
59 | 2566185.3358 | 1189076.3931 | 2566207.9502 | 1189102.4012
60 | 2566128.6423 | 1189090.5221 | 2566128.6423 | 1189090.5221 | 2566131.4031 | 1189098.5774 | 2566141.2909 | 1189109.078
61 | 2566038.2245 | 1189024.8374 | 2566039.0609 | 1189026.7603
62 | 2566207.9502 | 1189102.4012 | 2566213.7386 | 1189109.0583
63 | 2566142.6939 | 1189110.568 | 2566141.2909 | 1189109.078
64 | 2566038.2245 | 1189024.8374 | 2566035.0585 | 1189017.5591 | 2566031.5383 | 1189001.2412
65 | 2566029.4966 | 1188991.7769 | 2566031.5383 | 1189001.2412
66 | 2566029.4966 | 1188991.7769 | 2566028.757 | 1188984.125
67 | 2566028.6827 | 1188983.3565 | 2566028.757 | 1188984.125
68 | 2566028.6827 | 1188983.3565 | 2566028.3539 | 1188979.9548 | 2566028.0478 | 1188974.3615
69 | 2566028.0478 | 1188974.3615 | 2566026.8492 | 1188952.4635
70 | 2565761.7991 | 1189013.1302 | 2565763.2506 | 1189014.5434 | 2565774.9627 | 1189026.0885
71 | 2565777.5018 | 1189028.5914 | 2565774.9627 | 1189026.0885
72 | 2565777.5018 | 1189028.5914 | 2565788.0276 | 1189038.497
73 | 2565777.5018 | 1189028.5914 | 2565782.8468 | 1189012.8096
74 | 2565801.5217 | 1189051.1959 | 2565788.0276 | 1189038.497
75 | 2565801.5217 | 1189051.1959 | 2565803.348 | 1189052.9145
76 | 2566142.6939 | 1189110.568 | 2566161.7991 | 1189130.8573
77 | 2566161.7991 | 1189130.8573 | 2566176.0349 | 1189145.9754
78 | 2566176.0349 | 1189145.9754 | 2566151.2573 | 1189158.6171

## bus_geodata
| x | y | coords
0 | 2565854.713 | 1188980.7474
1 | 2565840.5045 | 1189004.1397
2 | 2565844.1055 | 1189022.0917
3 | 2565872.3533 | 1189055.9632
4 | 2565882.7914 | 1189040.8565
5 | 2565911.9713 | 1189076.1791
6 | 2565841.83 | 1189091.8014
7 | 2565914.9287 | 1188994.3458
8 | 2565913.1579 | 1188996.9086
9 | 2565953.5778 | 1188966.2512
10 | 2565884.9311 | 1189037.7599
11 | 2565957.3746 | 1188961.9828
12 | 2565977.0381 | 1188968.1901
13 | 2566003.7311 | 1188980.7232
14 | 2565742.3763 | 1189190.722
15 | 2565749.2223 | 1189185.2447
16 | 2565760.7798 | 1189175.9979
17 | 2565762.0245 | 1189175.0021
18 | 2565764.3413 | 1189173.1484
19 | 2565766.1657 | 1189171.6888
20 | 2565746.2346 | 1189159.9051
21 | 2565777.657 | 1189159.6211
22 | 2565784.8678 | 1189152.0485
23 | 2565791.2417 | 1189145.355
24 | 2565803.9827 | 1189131.9748
25 | 2565733.6417 | 1189152.4599
26 | 2565827.3178 | 1189107.4692
27 | 2565710.2874 | 1189138.6522
28 | 2565830.8955 | 1189080.5583
29 | 2565872.8562 | 1189121.9866
30 | 2565880.614 | 1189130.2669
31 | 2565892.8859 | 1189143.3654
32 | 2565879.2634 | 1189128.8253
33 | 2565917.8076 | 1189171.6872
34 | 2565874.853 | 1189124.1178
35 | 2565954.6663 | 1189214.536
36 | 2565816.9018 | 1189066.1696
37 | 2565916.2334 | 1189079.2027
38 | 2565815.1022 | 1189064.3192
39 | 2565925.2422 | 1189085.9133
40 | 2565939.2497 | 1189096.3472
41 | 2565932.2349 | 1189060.9324
42 | 2565954.9832 | 1189106.9521
43 | 2565913.5532 | 1189120.0289
44 | 2565959.9432 | 1189029.2942
45 | 2566002.2244 | 1189119.2117
46 | 2565967.7294 | 1189091.685
47 | 2565998.9399 | 1189107.613
48 | 2565967.8604 | 1189091.5282
49 | 2565982.4199 | 1189074.0892
50 | 2565997.0089 | 1189091.3042
51 | 2566051.3919 | 1189086.1932
52 | 2566064.3751 | 1189075.0566
53 | 2566128.3254 | 1189079.04
54 | 2566050.0863 | 1189046.8207
55 | 2566185.3358 | 1189076.3931
56 | 2566128.6423 | 1189090.5221
57 | 2566039.0609 | 1189026.7603
58 | 2566223.472 | 1189051.8964
59 | 2566207.9502 | 1189102.4012
60 | 2566141.2909 | 1189109.078
61 | 2566038.2245 | 1189024.8374
62 | 2566031.5383 | 1189001.2412
63 | 2566029.4966 | 1188991.7769
64 | 2566028.757 | 1188984.125
65 | 2566028.6827 | 1188983.3565
66 | 2566028.0478 | 1188974.3615
67 | 2566026.8492 | 1188952.4635
68 | 2565761.7991 | 1189013.1302
69 | 2565774.9627 | 1189026.0885
70 | 2565777.5018 | 1189028.5914
71 | 2565788.0276 | 1189038.497
72 | 2565782.8468 | 1189012.8096
73 | 2565801.5217 | 1189051.1959
74 | 2565803.348 | 1189052.9145
75 | 2566142.6939 | 1189110.568
76 | 2566161.7991 | 1189130.8573
77 | 2566176.0349 | 1189145.9754
78 | 2566151.2573 | 1189158.6171
79 | 2566213.7386 | 1189109.0583
80 | 2565939.2497 | 1189096.3472

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99369 | -0.04399 | 0.00080258 | 0.00020114
1 | 0.99372 | -0.043768 | 0 | 0
2 | 0.99374 | -0.043609 | 0.01348 | 0.0033785
3 | 0.99468 | -0.036992 | 0 | 0
4 | 0.99333 | -0.046413 | 0.0046518 | 0.0011659
5 | 0.99945 | -0.0038182 | 0.0021701 | 0.00054387
6 | 0.9893 | -0.07482 | 0 | 0
7 | 0.98974 | -0.071574 | 0.002997 | 0.00075113
8 | 0.98992 | -0.070342 | 0.0051624 | 0.0012938
9 | 0.98718 | -0.089656 | 0 | 0
10 | 0.99308 | -0.04817 | 0.0021547 | 0.00054001
11 | 0.98688 | -0.09175 | 0 | 0
12 | 0.9858 | -0.099407 | 0.0068793 | 0.0017241
13 | 0.98456 | -0.10818 | 0.0040688 | 0.0010197
14 | 0.98597 | -0.098384 | 0.001481 | 0.00037118
15 | 0.98599 | -0.098251 | 0.00045997 | 0.00011528
16 | 0.98603 | -0.097955 | 0.001389 | 0.00034812
17 | 0.98604 | -0.097901 | 0.00087567 | 0.00021946
18 | 0.98606 | -0.097773 | 0.0019062 | 0.00047773
19 | 0.98608 | -0.097626 | 0 | 0
20 | 0.98585 | -0.09922 | 0.00088177 | 0.00022099
21 | 0.98639 | -0.095433 | 0.0017215 | 0.00043145
22 | 0.9866 | -0.093873 | 0.0015222 | 0.00038149
23 | 0.98682 | -0.092351 | 0.0052245 | 0.0013094
24 | 0.98739 | -0.088321 | 0.00090624 | 0.00022713
25 | 0.98573 | -0.1001 | 0.0040471 | 0.0010143
26 | 0.98847 | -0.080638 | 0.0044813 | 0.0011231
27 | 0.98566 | -0.10059 | 0.0017732 | 0.00044442
28 | 0.98868 | -0.079167 | 0.0020932 | 0.00052461
29 | 0.98772 | -0.085973 | 0.0014674 | 0.00036777
30 | 0.98737 | -0.088442 | 0.0026227 | 0.0006573
31 | 0.98693 | -0.091589 | 0.0019869 | 0.00049796
32 | 0.98743 | -0.088043 | 0.00085381 | 0.00021399
33 | 0.9861 | -0.097445 | 0.007465 | 0.0018709
34 | 0.98762 | -0.086683 | 0.0031503 | 0.00078954
35 | 0.98548 | -0.10189 | 0.0076597 | 0.0019197
36 | 0.98796 | -0.084307 | 0.0054095 | 0.0013558
37 | 1 | 0 | -0.21662 | -0.054341
38 | 0.98788 | -0.084826 | 0.0030687 | 0.00076909
39 | 0.99914 | -0.0060337 | 0.0043319 | 0.0010857
40 | 0.9979 | -0.014677 | 0 | 0
41 | 0.99952 | -0.0033516 | 0.0069077 | 0.0017312
42 | 0.99736 | -0.018485 | 0 | 0
43 | 0.99644 | -0.024968 | 0.029383 | 0.007364
44 | 0.99911 | -0.0062559 | 0.0069078 | 0.0017312
45 | 0.99675 | -0.022739 | 0 | 0
46 | 0.99703 | -0.020773 | 0.003775 | 0.0009461
47 | 0.99661 | -0.023778 | 0.0016691 | 0.00041832
48 | 0.99703 | -0.020788 | 0.0060972 | 0.0015281
49 | 0.99698 | -0.021151 | 0.0015863 | 0.00039757
50 | 0.99639 | -0.025319 | 0.0069087 | 0.0017315
51 | 0.98114 | -0.13256 | 0.0010009 | 0.00025085
52 | 0.98116 | -0.13238 | 0 | 0
53 | 0.97976 | -0.14241 | 0 | 0
54 | 0.98194 | -0.12686 | 0.00053798 | 0.00013483
55 | 0.97934 | -0.14539 | 0 | 0
56 | 0.9796 | -0.14357 | 0.0011205 | 0.00028083
57 | 0.98248 | -0.12301 | 0.00092077 | 0.00023077
58 | 0.97921 | -0.14637 | 0.0020802 | 0.00052134
59 | 0.9792 | -0.14643 | 0.0012191 | 0.00030553
60 | 0.97931 | -0.14562 | 0.0018637 | 0.0004671
61 | 0.98253 | -0.12263 | 0.0030581 | 0.00076644
62 | 0.98325 | -0.11748 | 0.00094557 | 0.00023698
63 | 0.98355 | -0.11537 | 0 | 0
64 | 0.98351 | -0.11566 | 0.00092155 | 0.00023096
65 | 0.98351 | -0.11568 | 0.00066975 | 0.00016786
66 | 0.98348 | -0.11587 | 0.0012093 | 0.00030309
67 | 0.98345 | -0.11607 | 0.00086778 | 0.00021749
68 | 0.98691 | -0.091709 | 0.0021199 | 0.00053129
69 | 0.98697 | -0.091307 | 0.0041852 | 0.0010489
70 | 0.987 | -0.091077 | 0 | 0
71 | 0.98717 | -0.089885 | 0.0019237 | 0.00048212
72 | 0.98696 | -0.091374 | 0.0017402 | 0.00043613
73 | 0.98744 | -0.087993 | 0.0051183 | 0.0012828
74 | 0.98749 | -0.087605 | 0.00149 | 0.00037342
75 | 0.97929 | -0.14577 | 0.0019886 | 0.00049838
76 | 0.9791 | -0.14714 | 0.0013446 | 0.00033699
77 | 0.979 | -0.14787 | 0.0013881 | 0.00034789
78 | 0.97892 | -0.14846 | 0.002003 | 0.000502
79 | 0.97918 | -0.14658 | 0.0016759 | 0.00042002
80 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00080258 | -0.00020114 | 0.0008026 | 0.0002008 | 2.4666e-08 | -3.4507e-07 | 0.0012018 | 0.0012017 | 0.0012018 | 0.99369 | -0.04399 | 0.99372 | -0.043768 | 0.44512
1 | -0.0008026 | -0.0002008 | 0.00080262 | 0.00020056 | 1.7487e-08 | -2.447e-07 | 0.0012017 | 0.0012016 | 0.0012017 | 0.99372 | -0.043768 | 0.99374 | -0.043609 | 0.44508
2 | -0.014283 | -0.0035791 | 0.014296 | 0.0035835 | 1.3091e-05 | 4.4402e-06 | 0.021387 | 0.021387 | 0.021387 | 0.99374 | -0.043609 | 0.99468 | -0.036992 | 7.9212
3 | 0.051222 | 0.012895 | -0.051155 | -0.012869 | 6.7314e-05 | 2.5652e-05 | 0.076648 | 0.076648 | 0.076648 | 0.99468 | -0.036992 | 0.99333 | -0.046413 | 28.388
4 | -0.14515 | -0.03651 | 0.14582 | 0.036768 | 0.00067464 | 0.00025828 | 0.21719 | 0.21718 | 0.21719 | 0.99468 | -0.036992 | 0.99945 | -0.0038182 | 40.2195
5 | 0.07963 | 0.020031 | -0.079212 | -0.019871 | 0.00041786 | 0.00016011 | 0.11915 | 0.11915 | 0.11915 | 0.99468 | -0.036992 | 0.9893 | -0.07482 | 44.13
6 | 0.046503 | 0.011703 | -0.046492 | -0.011699 | 1.1403e-05 | 4.3372e-06 | 0.069679 | 0.069679 | 0.069679 | 0.99333 | -0.046413 | 0.99308 | -0.04817 | 25.8071
7 | -0.14799 | -0.037312 | 0.14807 | 0.037342 | 7.921e-05 | 3.0328e-05 | 0.22042 | 0.22042 | 0.22042 | 0.99945 | -0.0038182 | 1 | 0 | 40.8177
8 | 0.027196 | 0.0068206 | -0.027179 | -0.0068145 | 1.6377e-05 | 6.0976e-06 | 0.040907 | 0.040907 | 0.040907 | 0.9893 | -0.07482 | 0.98868 | -0.079167 | 15.1509
9 | 0.025277 | 0.0063423 | -0.025238 | -0.0063278 | 3.9059e-05 | 1.4467e-05 | 0.038022 | 0.038022 | 0.038022 | 0.9893 | -0.07482 | 0.98772 | -0.085973 | 14.0821
10 | 0.02674 | 0.0067084 | -0.026718 | -0.0067004 | 2.1561e-05 | 8.0189e-06 | 0.040222 | 0.040222 | 0.040222 | 0.9893 | -0.07482 | 0.98847 | -0.080638 | 14.8971
11 | -0.039031 | -0.0098107 | 0.039038 | 0.0098132 | 6.6956e-06 | 2.5352e-06 | 0.058691 | 0.058691 | 0.058691 | 0.98974 | -0.071574 | 0.98992 | -0.070342 | 21.7374
12 | 0.036034 | 0.0090596 | -0.035944 | -0.0090254 | 9.0547e-05 | 3.4192e-05 | 0.054185 | 0.054185 | 0.054185 | 0.98974 | -0.071574 | 0.98718 | -0.089656 | 20.0686
13 | -0.0442 | -0.011107 | 0.044337 | 0.011159 | 0.00013682 | 5.1982e-05 | 0.066451 | 0.066451 | 0.066451 | 0.98992 | -0.070342 | 0.99308 | -0.04817 | 24.6114
14 | 0.035944 | 0.0090254 | -0.035933 | -0.0090214 | 1.0454e-05 | 3.9478e-06 | 0.054185 | 0.054185 | 0.054185 | 0.98718 | -0.089656 | 0.98688 | -0.09175 | 20.0687
15 | 0.035933 | 0.0090214 | -0.035895 | -0.009007 | 3.8185e-05 | 1.442e-05 | 0.054185 | 0.054185 | 0.054185 | 0.98688 | -0.09175 | 0.9858 | -0.099407 | 20.0687
16 | 0.029016 | 0.0072829 | -0.02898 | -0.0072697 | 3.5314e-05 | 1.3207e-05 | 0.043802 | 0.043802 | 0.043802 | 0.9858 | -0.099407 | 0.98456 | -0.10818 | 16.2228
17 | 0.024912 | 0.0062499 | -0.024887 | -0.0062408 | 2.4802e-05 | 9.1832e-06 | 0.037652 | 0.037652 | 0.037652 | 0.98456 | -0.10818 | 0.98355 | -0.11537 | 13.9453
18 | -0.001481 | -0.00037118 | 0.001481 | 0.00037107 | 2.7331e-08 | -1.0131e-07 | 0.0022351 | 0.0022351 | 0.0022351 | 0.98597 | -0.098384 | 0.98599 | -0.098251 | 0.82782
19 | -0.001941 | -0.00048635 | 0.0019411 | 0.0004862 | 7.9248e-08 | -1.5831e-07 | 0.0029293 | 0.0029292 | 0.0029293 | 0.98599 | -0.098251 | 0.98603 | -0.097955 | 1.0849
20 | -0.0033301 | -0.00083432 | 0.0033301 | 0.00083431 | 2.512e-08 | -1.0671e-08 | 0.0050254 | 0.0050254 | 0.0050254 | 0.98603 | -0.097955 | 0.98604 | -0.097901 | 1.8612
21 | -0.0042058 | -0.0010538 | 0.0042059 | 0.0010538 | 7.4581e-08 | -9.1625e-09 | 0.0063468 | 0.0063468 | 0.0063468 | 0.98604 | -0.097901 | 0.98606 | -0.097773 | 2.3507
22 | -0.006112 | -0.0015315 | 0.0061122 | 0.0015315 | 1.2402e-07 | 1.7898e-08 | 0.0092233 | 0.0092233 | 0.0092233 | 0.98606 | -0.097773 | 0.98608 | -0.097626 | 3.416
23 | 0.0067045 | 0.0016798 | -0.006703 | -0.0016795 | 1.4788e-06 | 2.7349e-07 | 0.010117 | 0.010117 | 0.010117 | 0.98608 | -0.097626 | 0.98585 | -0.09922 | 3.7471
24 | -0.012817 | -0.0032113 | 0.012821 | 0.0032126 | 3.8894e-06 | 1.2833e-06 | 0.01934 | 0.01934 | 0.01934 | 0.98608 | -0.097626 | 0.98639 | -0.095433 | 7.1631
25 | 0.0058212 | 0.0014585 | -0.0058205 | -0.0014584 | 7.0471e-07 | 8.4534e-08 | 0.0087862 | 0.0087863 | 0.0087863 | 0.98585 | -0.09922 | 0.98573 | -0.1001 | 3.2542
26 | -0.014542 | -0.003644 | 0.014545 | 0.0036451 | 3.1401e-06 | 1.0742e-06 | 0.021937 | 0.021937 | 0.021937 | 0.98639 | -0.095433 | 0.9866 | -0.093873 | 8.1249
27 | -0.016067 | -0.0040266 | 0.016071 | 0.0040278 | 3.3869e-06 | 1.1846e-06 | 0.024233 | 0.024233 | 0.024233 | 0.9866 | -0.093873 | 0.98682 | -0.092351 | 8.9752
28 | -0.021295 | -0.0053371 | 0.021307 | 0.0053415 | 1.1888e-05 | 4.336e-06 | 0.032111 | 0.032111 | 0.032111 | 0.98682 | -0.092351 | 0.98739 | -0.088321 | 11.8929
29 | -0.022213 | -0.0055686 | 0.022237 | 0.0055773 | 2.3663e-05 | 8.668e-06 | 0.033476 | 0.033476 | 0.033476 | 0.98739 | -0.088321 | 0.98847 | -0.080638 | 12.3987
30 | 0.0017734 | 0.00044412 | -0.0017732 | -0.00044442 | 1.2132e-07 | -2.9916e-07 | 0.0026769 | 0.002677 | 0.002677 | 0.98573 | -0.1001 | 0.98566 | -0.10059 | 0.99148
31 | 0.025086 | 0.0062899 | -0.025068 | -0.0062833 | 1.7855e-05 | 6.6101e-06 | 0.037757 | 0.037757 | 0.037757 | 0.98868 | -0.079167 | 0.98796 | -0.084307 | 13.9841
32 | 0.02377 | 0.00596 | -0.023768 | -0.0059592 | 2.337e-06 | 8.6148e-07 | 0.035811 | 0.035811 | 0.035811 | 0.98772 | -0.085973 | 0.98762 | -0.086683 | 13.2633
33 | 0.017136 | 0.0042965 | -0.017129 | -0.0042939 | 7.47e-06 | 2.6436e-06 | 0.025825 | 0.025826 | 0.025826 | 0.98737 | -0.088442 | 0.98693 | -0.091589 | 9.565
34 | -0.019759 | -0.0049538 | 0.01976 | 0.0049542 | 1.093e-06 | 3.9514e-07 | 0.029778 | 0.029778 | 0.029778 | 0.98737 | -0.088442 | 0.98743 | -0.088043 | 11.0289
35 | 0.015142 | 0.0037959 | -0.015129 | -0.0037917 | 1.2272e-05 | 4.2381e-06 | 0.02283 | 0.02283 | 0.02283 | 0.98693 | -0.091589 | 0.9861 | -0.097445 | 8.4556
36 | -0.020614 | -0.0051682 | 0.020617 | 0.0051696 | 3.8844e-06 | 1.4115e-06 | 0.031065 | 0.031065 | 0.031065 | 0.98743 | -0.088043 | 0.98762 | -0.086683 | 11.5054
37 | 0.0076644 | 0.0019208 | -0.0076597 | -0.0019197 | 4.7177e-06 | 1.0939e-06 | 0.011565 | 0.011566 | 0.011566 | 0.9861 | -0.097445 | 0.98548 | -0.10189 | 4.2836
38 | 0.019659 | 0.0049275 | -0.019657 | -0.004927 | 1.4121e-06 | 5.1006e-07 | 0.02961 | 0.02961 | 0.02961 | 0.98796 | -0.084307 | 0.98788 | -0.084826 | 10.9665
39 | 0.013825 | 0.0034651 | -0.013818 | -0.003463 | 6.4134e-06 | 2.1482e-06 | 0.020571 | 0.020572 | 0.020572 | 1 | 0 | 0.99952 | -0.0033516 | 7.6191
40 | 0.05392 | 0.013533 | -0.053874 | -0.013516 | 4.5132e-05 | 1.7211e-05 | 0.08024 | 0.08024 | 0.08024 | 1 | 0 | 0.99914 | -0.0060337 | 29.7186
41 | 0.016589 | 0.0041579 | -0.016582 | -0.0041557 | 6.3822e-06 | 2.2451e-06 | 0.024987 | 0.024987 | 0.024987 | 0.98788 | -0.084826 | 0.98749 | -0.087605 | 9.2546
42 | 0.049543 | 0.01243 | -0.049483 | -0.012408 | 5.9343e-05 | 2.2596e-05 | 0.073789 | 0.073789 | 0.073789 | 0.99914 | -0.0060337 | 0.9979 | -0.014677 | 27.3292
43 | 0.020058 | 0.0050282 | -0.020048 | -0.0050244 | 1.0572e-05 | 3.819e-06 | 0.02991 | 0.029911 | 0.029911 | 0.9979 | -0.014677 | 0.99736 | -0.018485 | 11.078
44 | 0.029425 | 0.0073797 | -0.029383 | -0.007364 | 4.192e-05 | 1.5668e-05 | 0.043878 | 0.043878 | 0.043878 | 0.9979 | -0.014677 | 0.99644 | -0.024968 | 16.2513
45 | 0.0069105 | 0.0017318 | -0.0069078 | -0.0017312 | 2.7776e-06 | 5.1732e-07 | 0.010288 | 0.010288 | 0.010288 | 0.99952 | -0.0033516 | 0.99911 | -0.0062559 | 3.8104
46 | 0.0085856 | 0.0021517 | -0.0085806 | -0.0021504 | 5.0547e-06 | 1.3002e-06 | 0.012809 | 0.01281 | 0.01281 | 0.99736 | -0.018485 | 0.99675 | -0.022739 | 4.7443
47 | 0.011462 | 0.0028727 | -0.011459 | -0.0028715 | 3.6295e-06 | 1.1365e-06 | 0.017101 | 0.017101 | 0.017101 | 0.99736 | -0.018485 | 0.99703 | -0.020773 | 6.3338
48 | 0.0085806 | 0.0021504 | -0.0085794 | -0.0021501 | 1.2343e-06 | 3.1762e-07 | 0.01281 | 0.01281 | 0.01281 | 0.99675 | -0.022739 | 0.99661 | -0.023778 | 4.7443
49 | 0.0076836 | 0.0019254 | -0.0076836 | -0.0019254 | 1.6761e-08 | 3.7827e-09 | 0.011467 | 0.011467 | 0.011467 | 0.99703 | -0.020773 | 0.99703 | -0.020788 | 4.2471
50 | 0.0069102 | 0.0017318 | -0.0069087 | -0.0017315 | 1.4738e-06 | 2.778e-07 | 0.010318 | 0.010318 | 0.010318 | 0.99661 | -0.023778 | 0.99639 | -0.025319 | 3.8213
51 | 0.0015864 | 0.00039731 | -0.0015863 | -0.00039757 | 7.9463e-08 | -2.657e-07 | 0.0023675 | 0.0023677 | 0.0023677 | 0.99703 | -0.020788 | 0.99698 | -0.021151 | 0.87691
52 | -0.0010009 | -0.00025085 | 0.0010009 | 0.00025065 | 2.4783e-08 | -2.0815e-07 | 0.001518 | 0.0015179 | 0.001518 | 0.98114 | -0.13256 | 0.98116 | -0.13238 | 0.56223
53 | 0.014712 | 0.003687 | -0.014692 | -0.00368 | 2.0396e-05 | 7.0167e-06 | 0.022312 | 0.022313 | 0.022313 | 0.98116 | -0.13238 | 0.97976 | -0.14241 | 8.264
54 | -0.015713 | -0.0039377 | 0.015725 | 0.0039419 | 1.201e-05 | 4.1908e-06 | 0.02383 | 0.02383 | 0.02383 | 0.98116 | -0.13238 | 0.98194 | -0.12686 | 8.8261
55 | 0.0049779 | 0.0012461 | -0.0049759 | -0.001246 | 2.0468e-06 | 6.4738e-08 | 0.0075597 | 0.0075599 | 0.0075599 | 0.97976 | -0.14241 | 0.97934 | -0.14539 | 2.8
56 | 0.0097141 | 0.0024339 | -0.0097125 | -0.0024334 | 1.5601e-06 | 4.5539e-07 | 0.014753 | 0.014753 | 0.014753 | 0.97976 | -0.14241 | 0.9796 | -0.14357 | 5.4641
57 | -0.016263 | -0.0040767 | 0.016272 | 0.0040798 | 8.6915e-06 | 3.0526e-06 | 0.024646 | 0.024645 | 0.024646 | 0.98194 | -0.12686 | 0.98248 | -0.12301 | 9.128
58 | 0.0020804 | 0.00052088 | -0.0020802 | -0.00052134 | 2.8259e-07 | -4.6156e-07 | 0.0031608 | 0.003161 | 0.003161 | 0.97934 | -0.14539 | 0.97921 | -0.14637 | 1.1708
59 | 0.0028954 | 0.00072517 | -0.002895 | -0.00072545 | 4.162e-07 | -2.7353e-07 | 0.0043991 | 0.0043993 | 0.0043993 | 0.97934 | -0.14539 | 0.9792 | -0.14643 | 1.6294
60 | 0.008592 | 0.0021526 | -0.0085896 | -0.002152 | 2.4381e-06 | 6.4902e-07 | 0.013051 | 0.013051 | 0.013051 | 0.9796 | -0.14357 | 0.97931 | -0.14562 | 4.8338
61 | -0.017193 | -0.0043105 | 0.017194 | 0.0043108 | 8.8723e-07 | 3.1469e-07 | 0.02604 | 0.02604 | 0.02604 | 0.98248 | -0.12301 | 0.98253 | -0.12263 | 9.6444
62 | 0.0016759 | 0.00041992 | -0.0016759 | -0.00042002 | 3.5704e-08 | -9.7236e-08 | 0.0025467 | 0.0025468 | 0.0025468 | 0.9792 | -0.14643 | 0.97918 | -0.14658 | 0.94325
63 | 0.0067258 | 0.0016849 | -0.0067257 | -0.0016848 | 1.3337e-07 | 2.5546e-08 | 0.010219 | 0.010219 | 0.010219 | 0.97931 | -0.14562 | 0.97929 | -0.14577 | 3.7849
64 | -0.020252 | -0.0050773 | 0.020266 | 0.0050825 | 1.4458e-05 | 5.2488e-06 | 0.030671 | 0.030671 | 0.030671 | 0.98253 | -0.12263 | 0.98325 | -0.11748 | 11.3598
65 | -0.021212 | -0.0053195 | 0.021218 | 0.0053218 | 6.2262e-06 | 2.2719e-06 | 0.032102 | 0.032102 | 0.032102 | 0.98325 | -0.11748 | 0.98355 | -0.11537 | 11.8897
66 | 0.0036687 | 0.00091898 | -0.0036685 | -0.00091902 | 1.4777e-07 | -4.0726e-08 | 0.0055501 | 0.0055502 | 0.0055502 | 0.98355 | -0.11537 | 0.98351 | -0.11566 | 2.0556
67 | 0.002747 | 0.00068806 | -0.0027469 | -0.00068807 | 8.3211e-09 | -6.5974e-09 | 0.0041559 | 0.0041559 | 0.0041559 | 0.98351 | -0.11566 | 0.98351 | -0.11568 | 1.5392
68 | 0.0020772 | 0.00052021 | -0.0020771 | -0.00052031 | 5.5583e-08 | -9.3075e-08 | 0.0031426 | 0.0031426 | 0.0031426 | 0.98351 | -0.11568 | 0.98348 | -0.11587 | 1.1639
69 | 0.0008678 | 0.00021722 | -0.00086778 | -0.00021749 | 2.359e-08 | -2.6921e-07 | 0.0013129 | 0.001313 | 0.001313 | 0.98348 | -0.11587 | 0.98345 | -0.11607 | 0.4863
70 | -0.0021199 | -0.00053129 | 0.00212 | 0.0005311 | 1.1775e-07 | -1.9076e-07 | 0.0031962 | 0.0031961 | 0.0031962 | 0.98691 | -0.091709 | 0.98697 | -0.091307 | 1.1838
71 | -0.0063052 | -0.00158 | 0.0063054 | 0.00158 | 2.0104e-07 | 3.1757e-08 | 0.009506 | 0.009506 | 0.009506 | 0.98697 | -0.091307 | 0.987 | -0.091077 | 3.5207
72 | -0.0080456 | -0.002016 | 0.0080469 | 0.0020163 | 1.3269e-06 | 3.256e-07 | 0.01213 | 0.012129 | 0.01213 | 0.987 | -0.091077 | 0.98717 | -0.089885 | 4.4924
73 | 0.0017403 | 0.00043595 | -0.0017402 | -0.00043613 | 7.1568e-08 | -1.8542e-07 | 0.0026236 | 0.0026236 | 0.0026236 | 0.987 | -0.091077 | 0.98696 | -0.091374 | 0.97172
74 | -0.0099706 | -0.0024984 | 0.0099732 | 0.0024992 | 2.6117e-06 | 7.6753e-07 | 0.015029 | 0.015029 | 0.015029 | 0.98717 | -0.089885 | 0.98744 | -0.087993 | 5.5663
75 | -0.015092 | -0.003782 | 0.015092 | 0.0037823 | 8.0936e-07 | 2.7921e-07 | 0.022742 | 0.022742 | 0.022742 | 0.98744 | -0.087993 | 0.98749 | -0.087605 | 8.423
76 | 0.0047371 | 0.0011865 | -0.0047362 | -0.0011865 | 9.0093e-07 | -4.0487e-09 | 0.0071977 | 0.0071978 | 0.0071978 | 0.97929 | -0.14577 | 0.9791 | -0.14714 | 2.6659
77 | 0.0033916 | 0.00084947 | -0.0033913 | -0.0008496 | 3.4425e-07 | -1.2873e-07 | 0.0051543 | 0.0051544 | 0.0051544 | 0.9791 | -0.14714 | 0.979 | -0.14787 | 1.909
78 | 0.0020032 | 0.00050171 | -0.002003 | -0.000502 | 1.609e-07 | -2.8785e-07 | 0.0030446 | 0.0030447 | 0.0030447 | 0.979 | -0.14787 | 0.97892 | -0.14846 | 1.1277

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21662 | 0.054341

## res_load
| p_mw | q_mvar
0 | 0.00080258 | 0.00020114
1 | 0.01348 | 0.0033785
2 | 0.0046518 | 0.0011659
3 | 0.0021701 | 0.00054387
4 | 0.002997 | 0.00075113
5 | 0.0051624 | 0.0012938
6 | 0.0021547 | 0.00054001
7 | 0.0068793 | 0.0017241
8 | 0.0040688 | 0.0010197
9 | 0.001481 | 0.00037118
10 | 0.00045997 | 0.00011528
11 | 0.001389 | 0.00034812
12 | 0.00087567 | 0.00021946
13 | 0.0019062 | 0.00047773
14 | 0.00088177 | 0.00022099
15 | 0.0017215 | 0.00043145
16 | 0.0015222 | 0.00038149
17 | 0.0052245 | 0.0013094
18 | 0.00090624 | 0.00022713
19 | 0.0040471 | 0.0010143
20 | 0.0044813 | 0.0011231
21 | 0.0017732 | 0.00044442
22 | 0.0020932 | 0.00052461
23 | 0.0014674 | 0.00036777
24 | 0.0026227 | 0.0006573
25 | 0.0019869 | 0.00049796
26 | 0.00085381 | 0.00021399
27 | 0.007465 | 0.0018709
28 | 0.0031503 | 0.00078954
29 | 0.0076597 | 0.0019197
30 | 0.0054095 | 0.0013558
31 | 0.0030687 | 0.00076909
32 | 0.0043319 | 0.0010857
33 | 0.0069077 | 0.0017312
34 | 0.029383 | 0.007364
35 | 0.0069078 | 0.0017312
36 | 0.003775 | 0.0009461
37 | 0.0016691 | 0.00041832
38 | 0.0060972 | 0.0015281
39 | 0.0015863 | 0.00039757
40 | 0.0069087 | 0.0017315
41 | 0.0010009 | 0.00025085
42 | 0.00053798 | 0.00013483
43 | 0.0011205 | 0.00028083
44 | 0.00092077 | 0.00023077
45 | 0.0020802 | 0.00052134
46 | 0.0012191 | 0.00030553
47 | 0.0018637 | 0.0004671
48 | 0.0030581 | 0.00076644
49 | 0.00094557 | 0.00023698
50 | 0.00092155 | 0.00023096
51 | 0.00066975 | 0.00016786
52 | 0.0012093 | 0.00030309
53 | 0.00086778 | 0.00021749
54 | 0.0021199 | 0.00053129
55 | 0.0041852 | 0.0010489
56 | 0.0019237 | 0.00048212
57 | 0.0017402 | 0.00043613
58 | 0.0051183 | 0.0012828
59 | 0.00149 | 0.00037342
60 | 0.0019886 | 0.00049838
61 | 0.0013446 | 0.00033699
62 | 0.0013881 | 0.00034789
63 | 0.002003 | 0.000502
64 | 0.0016759 | 0.00042002

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1