## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2053-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2053-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2053-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2053-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2053-2_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2053-2_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2053-2_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2053-2_0_4_node_34 | 0.4 | n |  | TRUE
8 | bus_LV_2053-2_0_4_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_2053-2_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2053-2_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2053-2_0_4_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_2053-2_0_4_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_2053-2_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2053-2_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2053-2_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2053-2_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_2053-2_0_4_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2053-2_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2053-2_0_4_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_2053-2_0_4_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_2053-2_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2053-2_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2053-2_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2053-2_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2053-2_0_4_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_2053-2_0_4_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_2053-2_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_2053-2_0_4_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_2053-2_0_4_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2053-2_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_2053-2_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_MV_377_1_node_94 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2053-2_0_4_load_0 | 0 | 0.035281 | 0.0088423 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2053-2_0_4_load_1 | 1 | 0.0057904 | 0.0014512 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2053-2_0_4_load_5 | 5 | 0.0053633 | 0.0013442 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2053-2_0_4_load_34 | 7 | 0.0036171 | 0.00090654 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2053-2_0_4_load_28 | 8 | 0.051034 | 0.01279 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2053-2_0_4_load_8 | 9 | 0.035811 | 0.0089751 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2053-2_0_4_load_6 | 10 | 0.0041595 | 0.0010425 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2053-2_0_4_load_27 | 11 | 0.0023174 | 0.0005808 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2053-2_0_4_load_25 | 12 | 0.0053565 | 0.0013425 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2053-2_0_4_load_9 | 13 | 0.002648 | 0.00066366 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2053-2_0_4_load_10 | 14 | 0.001187 | 0.0002975 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2053-2_0_4_load_22 | 17 | 0.0036707 | 0.00091997 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2053-2_0_4_load_30 | 20 | 0.0040678 | 0.0010195 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2053-2_0_4_load_12 | 21 | 0.0075153 | 0.0018835 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2053-2_0_4_load_15 | 23 | 0.0013259 | 0.00033231 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2053-2_0_4_load_18 | 24 | 0.0021554 | 0.0005402 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2053-2_0_4_load_32 | 25 | 0.0052918 | 0.0013263 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2053-2_0_4_load_26 | 26 | 0.00099994 | 0.00025061 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2053-2_0_4_load_24 | 27 | 0.0015941 | 0.00039953 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2053-2_0_4_load_31 | 28 | 0.0051045 | 0.0012793 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2053-2_0_4_load_20 | 29 | 0.0030023 | 0.00075245 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2053-2_0_4_load_19 | 30 | 0.0041853 | 0.0010489 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2053-2_0_4_load_21 | 31 | 0.0031008 | 0.00077714 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2053-2_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.072501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2053-2_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.060658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2053-2_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0092438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2053-2_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.066393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_2053-2_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.043004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2053-2_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.068806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2053-2_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.044591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2053-2_0_4_line_7 | NAYY 4x150 SE | 4 | 8 | 0.24473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_2053-2_0_4_line_8 | NAYY 4x150 SE | 5 | 9 | 0.019869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2053-2_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.10948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2053-2_0_4_line_10 | NAYY 4x150 SE | 8 | 11 | 0.14186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_2053-2_0_4_line_11 | NAYY 4x150 SE | 11 | 12 | 0.45989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_2053-2_0_4_line_12 | NAYY 4x150 SE | 12 | 27 | 0.017714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2053-2_0_4_line_13 | NAYY 4x150 SE | 13 | 14 | 0.01903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2053-2_0_4_line_14 | NAYY 4x150 SE | 14 | 15 | 0.041814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2053-2_0_4_line_15 | NAYY 4x150 SE | 15 | 19 | 0.040656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2053-2_0_4_line_16 | NAYY 4x150 SE | 16 | 17 | 0.02286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2053-2_0_4_line_17 | NAYY 4x150 SE | 16 | 18 | 0.049951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2053-2_0_4_line_18 | NAYY 4x150 SE | 17 | 29 | 0.017084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2053-2_0_4_line_19 | NAYY 4x150 SE | 18 | 24 | 0.015257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2053-2_0_4_line_20 | NAYY 4x150 SE | 18 | 25 | 0.035407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2053-2_0_4_line_21 | NAYY 4x150 SE | 18 | 21 | 0.097507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2053-2_0_4_line_22 | NAYY 4x150 SE | 19 | 20 | 0.055716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2053-2_0_4_line_23 | NAYY 4x150 SE | 20 | 28 | 0.039091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2053-2_0_4_line_24 | NAYY 4x150 SE | 21 | 22 | 0.0055558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2053-2_0_4_line_25 | NAYY 4x150 SE | 22 | 23 | 0.039741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2053-2_0_4_line_26 | NAYY 4x150 SE | 23 | 26 | 0.012915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2053-2_0_4_line_27 | NAYY 4x150 SE | 24 | 27 | 0.013849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2053-2_0_4_line_28 | NAYY 4x150 SE | 25 | 28 | 0.066756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2053-2_0_4_line_29 | NAYY 4x150 SE | 29 | 30 | 0.022173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2053-2_0_4_line_30 | NAYY 4x150 SE | 30 | 31 | 0.0035434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2053-2_0_4_trafo_28 | 0.25 MVA 20/0.4 kV | 32 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2568050.8955 | 1191758.6189 | 2568106.5269 | 1191805.1108
1 | 2568004.5505 | 1191719.4842 | 2568043.5915 | 1191752.515 | 2568050.8955 | 1191758.6189
2 | 2568113.6199 | 1191811.0385 | 2568106.5269 | 1191805.1108
3 | 2568004.5505 | 1191719.4842 | 2567955.027 | 1191675.1149
4 | 2568004.5505 | 1191719.4842 | 2568032.2549 | 1191686.5933
5 | 2568113.6199 | 1191811.0385 | 2568132.3438 | 1191826.947 | 2568141.2389 | 1191833.8588 | 2568167.5839 | 1191853.6844
6 | 2567955.027 | 1191675.1149 | 2567971.1601 | 1191655.5956 | 2567986.0992 | 1191667.8553
7 | 2567955.027 | 1191675.1149 | 2567772.6359 | 1191511.9345
8 | 2568045.0551 | 1191671.3968 | 2568032.2549 | 1191686.5933
9 | 2568167.5839 | 1191853.6844 | 2568230.0114 | 1191763.7477
10 | 2567666.6192 | 1191417.6704 | 2567716.7841 | 1191461.9511 | 2567772.6359 | 1191511.9345
11 | 2567935.9651 | 1191044.9115 | 2567666.6192 | 1191417.6704
12 | 2567935.9651 | 1191044.9115 | 2567946.3531 | 1191030.5636
13 | 2568106.4609 | 1190984.8547 | 2568094.8324 | 1190999.9181
14 | 2568132.0125 | 1190951.7557 | 2568106.4609 | 1190984.8547
15 | 2568111.8632 | 1190916.4443 | 2568125.1474 | 1190939.7303 | 2568132.0125 | 1190951.7557
16 | 2568003.8442 | 1191036.4871 | 2567990.369 | 1191054.9528
17 | 2568003.8442 | 1191036.4871 | 2567963.4221 | 1191006.9881
18 | 2567990.369 | 1191054.9528 | 2567980.2984 | 1191068.753
19 | 2567963.4221 | 1191006.9881 | 2567954.475 | 1191019.3457
20 | 2567963.4221 | 1191006.9881 | 2567998.1632 | 1191000.1536
21 | 2567963.4221 | 1191006.9881 | 2567925.6879 | 1190981.1769 | 2567882.164 | 1190953.1083
22 | 2568111.8632 | 1190916.4443 | 2568073.4223 | 1190956.7757
23 | 2568073.4223 | 1190956.7757 | 2568046.4516 | 1190985.0728
24 | 2567877.4949 | 1190950.0972 | 2567882.164 | 1190953.1083
25 | 2567877.4949 | 1190950.0972 | 2567871.3757 | 1190959.1795 | 2567883.8608 | 1190966.9943 | 2567875.8356 | 1190978.54
26 | 2567875.8356 | 1190978.54 | 2567868.4646 | 1190989.1446
27 | 2567946.3531 | 1191030.5636 | 2567954.475 | 1191019.3457
28 | 2568046.4516 | 1190985.0728 | 2568017.3946 | 1191015.5587 | 2567998.1632 | 1191000.1536
29 | 2567980.2984 | 1191068.753 | 2567980.2984 | 1191068.753 | 2567998.5687 | 1191081.3161
30 | 2568001.4884 | 1191083.3238 | 2567998.5687 | 1191081.3161

## bus_geodata
| x | y | coords
0 | 2568050.8954 | 1191758.6189
1 | 2568106.5269 | 1191805.1108
2 | 2568004.5505 | 1191719.4842
3 | 2568113.6199 | 1191811.0385
4 | 2567955.027 | 1191675.1149
5 | 2568032.2549 | 1191686.5933
6 | 2568167.5839 | 1191853.6844
7 | 2567986.0992 | 1191667.8553
8 | 2567772.6359 | 1191511.9345
9 | 2568045.0551 | 1191671.3968
10 | 2568230.0114 | 1191763.7477
11 | 2567666.6192 | 1191417.6704
12 | 2567935.9651 | 1191044.9115
13 | 2568094.8324 | 1190999.9181
14 | 2568106.4609 | 1190984.8547
15 | 2568132.0125 | 1190951.7557
16 | 2568003.8442 | 1191036.4871
17 | 2567990.369 | 1191054.9528
18 | 2567963.4221 | 1191006.9881
19 | 2568111.8632 | 1190916.4443
20 | 2568073.4223 | 1190956.7757
21 | 2567882.164 | 1190953.1083
22 | 2567877.4949 | 1190950.0972
23 | 2567875.8356 | 1190978.54
24 | 2567954.475 | 1191019.3457
25 | 2567998.1632 | 1191000.1536
26 | 2567868.4646 | 1190989.1446
27 | 2567946.3531 | 1191030.5636
28 | 2568046.4516 | 1190985.0728
29 | 2567980.2984 | 1191068.753
30 | 2567998.5687 | 1191081.3161
31 | 2568001.4884 | 1191083.3238
32 | 2567810.333 | 1191545.6613

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97571 | -0.17021 | 0.035281 | 0.0088423
1 | 0.97466 | -0.17779 | 0.0057904 | 0.0014512
2 | 0.97972 | -0.14154 | 0 | 0
3 | 0.9746 | -0.1782 | 0 | 0
4 | 0.98391 | -0.11183 | 0 | 0
5 | 0.97714 | -0.16001 | 0.0053633 | 0.0013442
6 | 0.97418 | -0.18122 | 0 | 0
7 | 0.98368 | -0.1135 | 0.0036171 | 0.00090654
8 | 1 | 0 | -0.14787 | -0.037296
9 | 0.9761 | -0.16745 | 0.035811 | 0.0089751
10 | 0.97351 | -0.18601 | 0.0041595 | 0.0010425
11 | 0.99444 | -0.038215 | 0.0023174 | 0.0005808
12 | 0.97719 | -0.15938 | 0.0053565 | 0.0013425
13 | 0.97063 | -0.20651 | 0.002648 | 0.00066366
14 | 0.97071 | -0.20598 | 0.001187 | 0.0002975
15 | 0.97094 | -0.20428 | 0 | 0
16 | 0.97314 | -0.18842 | 0 | 0
17 | 0.97267 | -0.19179 | 0.0036707 | 0.00091997
18 | 0.97416 | -0.18108 | 0 | 0
19 | 0.97117 | -0.20263 | 0 | 0
20 | 0.97149 | -0.20036 | 0.0040678 | 0.0010195
21 | 0.97276 | -0.1912 | 0.0075153 | 0.0018835
22 | 0.97274 | -0.19133 | 0 | 0
23 | 0.9726 | -0.19231 | 0.0013259 | 0.00033231
24 | 0.9751 | -0.17432 | 0.0021554 | 0.0005402
25 | 0.97321 | -0.18791 | 0.0052918 | 0.0013263
26 | 0.97258 | -0.19245 | 0.00099994 | 0.00025061
27 | 0.976 | -0.16789 | 0.0015941 | 0.00039953
28 | 0.97194 | -0.19709 | 0.0051045 | 0.0012793
29 | 0.97242 | -0.19365 | 0.0030023 | 0.00075245
30 | 0.97218 | -0.19535 | 0.0041853 | 0.0010489
31 | 0.97216 | -0.19547 | 0.0031008 | 0.00077714
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.009965 | 0.0024963 | -0.0099546 | -0.0024932 | 1.0448e-05 | 3.114e-06 | 0.015197 | 0.015197 | 0.015197 | 0.97571 | -0.17021 | 0.97466 | -0.17779 | 5.6286
1 | -0.045246 | -0.011339 | 0.045426 | 0.011407 | 0.00018022 | 6.8554e-05 | 0.069002 | 0.069002 | 0.069002 | 0.97571 | -0.17021 | 0.97972 | -0.14154 | 25.5564
2 | 0.0041642 | 0.001042 | -0.004164 | -0.001042 | 2.331e-07 | -2.5544e-08 | 0.0063569 | 0.006357 | 0.006357 | 0.97466 | -0.17779 | 0.9746 | -0.1782 | 2.3544
3 | -0.086743 | -0.02178 | 0.087103 | 0.021917 | 0.00035963 | 0.00013664 | 0.13176 | 0.13176 | 0.13176 | 0.97972 | -0.14154 | 0.98391 | -0.11183 | 24.4003
4 | 0.041317 | 0.010373 | -0.041211 | -0.010333 | 0.00010569 | 4.0112e-05 | 0.06276 | 0.06276 | 0.06276 | 0.97972 | -0.14154 | 0.97714 | -0.16001 | 23.2444
5 | 0.004164 | 0.001042 | -0.0041623 | -0.0010422 | 1.7351e-06 | -1.8968e-07 | 0.006357 | 0.0063573 | 0.0063573 | 0.9746 | -0.1782 | 0.97418 | -0.18122 | 2.3546
6 | 0.003618 | 0.00090629 | -0.0036171 | -0.00090654 | 8.3301e-07 | -2.4581e-07 | 0.0054715 | 0.0054717 | 0.0054717 | 0.98391 | -0.11183 | 0.98368 | -0.1135 | 2.0265
7 | -0.090721 | -0.022823 | 0.092159 | 0.02337 | 0.001438 | 0.00054675 | 0.13723 | 0.13723 | 0.13723 | 0.98391 | -0.11183 | 1 | 0 | 25.4134
8 | 0.035848 | 0.0089891 | -0.035811 | -0.0089751 | 3.6951e-05 | 1.3963e-05 | 0.054592 | 0.054592 | 0.054592 | 0.97714 | -0.16001 | 0.9761 | -0.16745 | 20.2194
9 | 0.0041623 | 0.0010422 | -0.0041595 | -0.0010425 | 2.7612e-06 | -3.0016e-07 | 0.0063573 | 0.0063578 | 0.0063578 | 0.97418 | -0.18122 | 0.97351 | -0.18601 | 2.3547
10 | 0.054912 | 0.013925 | -0.054616 | -0.013815 | 0.00029594 | 0.00011012 | 0.081768 | 0.081769 | 0.081769 | 1 | 0 | 0.99444 | -0.038215 | 15.1424
11 | 0.052299 | 0.013234 | -0.051419 | -0.012908 | 0.00087977 | 0.00032665 | 0.078301 | 0.078306 | 0.078306 | 0.99444 | -0.038215 | 0.97719 | -0.15938 | 14.5011
12 | 0.046063 | 0.011565 | -0.046008 | -0.011545 | 5.4392e-05 | 2.0698e-05 | 0.070149 | 0.070149 | 0.070149 | 0.97719 | -0.15938 | 0.976 | -0.16789 | 25.9812
13 | -0.002648 | -0.00066366 | 0.0026482 | 0.0006635 | 1.9569e-07 | -1.5996e-07 | 0.0040596 | 0.0040595 | 0.0040596 | 0.97063 | -0.20651 | 0.97071 | -0.20598 | 1.5035
14 | -0.0038353 | -0.000961 | 0.0038362 | 0.00096083 | 9.0181e-07 | -1.7018e-07 | 0.0058791 | 0.0058789 | 0.0058791 | 0.97071 | -0.20598 | 0.97094 | -0.20428 | 2.1774
15 | -0.0038362 | -0.00096083 | 0.0038371 | 0.00096067 | 8.7677e-07 | -1.6573e-07 | 0.0058789 | 0.0058787 | 0.0058789 | 0.97094 | -0.20428 | 0.97117 | -0.20263 | 2.1774
16 | 0.01397 | 0.0035019 | -0.013964 | -0.0034997 | 6.5092e-06 | 2.2197e-06 | 0.021362 | 0.021362 | 0.021362 | 0.97314 | -0.18842 | 0.97267 | -0.19179 | 7.9118
17 | -0.01397 | -0.0035019 | 0.013984 | 0.0035067 | 1.4223e-05 | 4.8492e-06 | 0.021362 | 0.021361 | 0.021362 | 0.97314 | -0.18842 | 0.97416 | -0.18108 | 7.9117
18 | 0.010293 | 0.0025797 | -0.01029 | -0.0025789 | 2.6432e-06 | 8.0462e-07 | 0.015746 | 0.015746 | 0.015746 | 0.97267 | -0.19179 | 0.97242 | -0.19365 | 5.832
19 | -0.042179 | -0.010575 | 0.042219 | 0.01059 | 3.9519e-05 | 1.501e-05 | 0.06443 | 0.06443 | 0.06443 | 0.97416 | -0.18108 | 0.9751 | -0.17432 | 23.8628
20 | 0.01834 | 0.0045981 | -0.018322 | -0.0045919 | 1.7339e-05 | 6.2286e-06 | 0.028014 | 0.028014 | 0.028014 | 0.97416 | -0.18108 | 0.97321 | -0.18791 | 10.3757
21 | 0.0098554 | 0.00247 | -0.0098416 | -0.0024659 | 1.3789e-05 | 4.0912e-06 | 0.015054 | 0.015054 | 0.015054 | 0.97416 | -0.18108 | 0.97276 | -0.1912 | 5.5757
22 | -0.0038371 | -0.00096067 | 0.0038383 | 0.00096044 | 1.2015e-06 | -2.2754e-07 | 0.0058787 | 0.0058785 | 0.0058787 | 0.97117 | -0.20263 | 0.97149 | -0.20036 | 2.1773
23 | -0.007906 | -0.0019799 | 0.0079096 | 0.0019808 | 3.5767e-06 | 8.9141e-07 | 0.012109 | 0.012109 | 0.012109 | 0.97149 | -0.20036 | 0.97194 | -0.19709 | 4.4848
24 | 0.0023262 | 0.00058234 | -0.0023262 | -0.00058239 | 4.3893e-08 | -5.2088e-08 | 0.0035582 | 0.0035582 | 0.0035582 | 0.97276 | -0.1912 | 0.97274 | -0.19133 | 1.3179
25 | 0.0023262 | 0.00058239 | -0.0023259 | -0.00058276 | 3.1399e-07 | -3.7251e-07 | 0.0035582 | 0.0035584 | 0.0035584 | 0.97274 | -0.19133 | 0.9726 | -0.19231 | 1.3179
26 | 0.00099995 | 0.00025045 | -0.00099994 | -0.00025061 | 1.8861e-08 | -1.5302e-07 | 0.0015298 | 0.0015299 | 0.0015299 | 0.9726 | -0.19231 | 0.97258 | -0.19245 | 0.56662
27 | -0.044374 | -0.01113 | 0.044414 | 0.011145 | 3.9631e-05 | 1.507e-05 | 0.067719 | 0.067719 | 0.067719 | 0.9751 | -0.17432 | 0.976 | -0.16789 | 25.081
28 | 0.013031 | 0.0032656 | -0.013014 | -0.0032601 | 1.6535e-05 | 5.5313e-06 | 0.019923 | 0.019924 | 0.019924 | 0.97321 | -0.18791 | 0.97194 | -0.19709 | 7.3792
29 | 0.0072879 | 0.0018264 | -0.0072862 | -0.001826 | 1.7208e-06 | 3.8684e-07 | 0.011152 | 0.011152 | 0.011152 | 0.97242 | -0.19365 | 0.97218 | -0.19535 | 4.1304
30 | 0.0031009 | 0.00077712 | -0.0031008 | -0.00077714 | 4.9807e-08 | -2.4778e-08 | 0.0047462 | 0.0047462 | 0.0047462 | 0.97218 | -0.19535 | 0.97216 | -0.19547 | 1.7579

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.1989 | 0.050086

## res_load
| p_mw | q_mvar
0 | 0.035281 | 0.0088423
1 | 0.0057904 | 0.0014512
2 | 0.0053633 | 0.0013442
3 | 0.0036171 | 0.00090654
4 | 0.051034 | 0.01279
5 | 0.035811 | 0.0089751
6 | 0.0041595 | 0.0010425
7 | 0.0023174 | 0.0005808
8 | 0.0053565 | 0.0013425
9 | 0.002648 | 0.00066366
10 | 0.001187 | 0.0002975
11 | 0.0036707 | 0.00091997
12 | 0.0040678 | 0.0010195
13 | 0.0075153 | 0.0018835
14 | 0.0013259 | 0.00033231
15 | 0.0021554 | 0.0005402
16 | 0.0052918 | 0.0013263
17 | 0.00099994 | 0.00025061
18 | 0.0015941 | 0.00039953
19 | 0.0051045 | 0.0012793
20 | 0.0030023 | 0.00075245
21 | 0.0041853 | 0.0010489
22 | 0.0031008 | 0.00077714

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1