## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2054-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2054-11_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2054-11_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2054-11_0_4_node_102 | 0.4 | n |  | TRUE
4 | bus_LV_2054-11_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2054-11_0_4_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_2054-11_0_4_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_2054-11_0_4_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_2054-11_0_4_node_101 | 0.4 | n |  | TRUE
9 | bus_LV_2054-11_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_2054-11_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2054-11_0_4_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_2054-11_0_4_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_2054-11_0_4_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_2054-11_0_4_node_4 | 0.4 | n |  | TRUE
15 | bus_LV_2054-11_0_4_node_5 | 0.4 | n |  | TRUE
16 | bus_LV_2054-11_0_4_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_2054-11_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_2054-11_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2054-11_0_4_node_116 | 0.4 | n |  | TRUE
20 | bus_LV_2054-11_0_4_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_2054-11_0_4_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_2054-11_0_4_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_2054-11_0_4_node_80 | 0.4 | n |  | TRUE
24 | bus_LV_2054-11_0_4_node_117 | 0.4 | n |  | TRUE
25 | bus_LV_2054-11_0_4_node_76 | 0.4 | n |  | TRUE
26 | bus_LV_2054-11_0_4_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_2054-11_0_4_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_2054-11_0_4_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_2054-11_0_4_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_2054-11_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_2054-11_0_4_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_2054-11_0_4_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_2054-11_0_4_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_2054-11_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2054-11_0_4_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_2054-11_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_2054-11_0_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_2054-11_0_4_node_104 | 0.4 | n |  | TRUE
39 | bus_LV_2054-11_0_4_node_105 | 0.4 | n |  | TRUE
40 | bus_LV_2054-11_0_4_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_2054-11_0_4_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_2054-11_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_2054-11_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_2054-11_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_2054-11_0_4_node_97 | 0.4 | n |  | TRUE
46 | bus_LV_2054-11_0_4_node_98 | 0.4 | n |  | TRUE
47 | bus_LV_2054-11_0_4_node_96 | 0.4 | n |  | TRUE
48 | bus_LV_2054-11_0_4_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_2054-11_0_4_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_2054-11_0_4_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_2054-11_0_4_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_2054-11_0_4_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_2054-11_0_4_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_2054-11_0_4_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_2054-11_0_4_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_2054-11_0_4_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_2054-11_0_4_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_2054-11_0_4_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_2054-11_0_4_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_2054-11_0_4_node_103 | 0.4 | n |  | TRUE
61 | bus_LV_2054-11_0_4_node_91 | 0.4 | n |  | TRUE
62 | bus_LV_2054-11_0_4_node_90 | 0.4 | n |  | TRUE
63 | bus_LV_2054-11_0_4_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_2054-11_0_4_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_2054-11_0_4_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_2054-11_0_4_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_2054-11_0_4_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_2054-11_0_4_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_2054-11_0_4_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_2054-11_0_4_node_54 | 0.4 | n |  | TRUE
71 | bus_LV_2054-11_0_4_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_2054-11_0_4_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_2054-11_0_4_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_2054-11_0_4_node_82 | 0.4 | n |  | TRUE
75 | bus_LV_2054-11_0_4_node_84 | 0.4 | n |  | TRUE
76 | bus_LV_2054-11_0_4_node_83 | 0.4 | n |  | TRUE
77 | bus_LV_2054-11_0_4_node_59 | 0.4 | n |  | TRUE
78 | bus_LV_2054-11_0_4_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_2054-11_0_4_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_2054-11_0_4_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_2054-11_0_4_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_2054-11_0_4_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_2054-11_0_4_node_66 | 0.4 | n |  | TRUE
84 | bus_LV_2054-11_0_4_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_2054-11_0_4_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_2054-11_0_4_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_2054-11_0_4_node_70 | 0.4 | n |  | TRUE
88 | bus_LV_2054-11_0_4_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_2054-11_0_4_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_2054-11_0_4_node_73 | 0.4 | n |  | TRUE
91 | bus_LV_2054-11_0_4_node_75 | 0.4 | n |  | TRUE
92 | bus_LV_2054-11_0_4_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_2054-11_0_4_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_2054-11_0_4_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_2054-11_0_4_node_81 | 0.4 | n |  | TRUE
96 | bus_LV_2054-11_0_4_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_2054-11_0_4_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_2054-11_0_4_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_2054-11_0_4_node_106 | 0.4 | n |  | TRUE
100 | bus_LV_2054-11_0_4_node_107 | 0.4 | n |  | TRUE
101 | bus_LV_2054-11_0_4_node_108 | 0.4 | n |  | TRUE
102 | bus_LV_2054-11_0_4_node_109 | 0.4 | n |  | TRUE
103 | bus_LV_2054-11_0_4_node_110 | 0.4 | n |  | TRUE
104 | bus_LV_2054-11_0_4_node_111 | 0.4 | n |  | TRUE
105 | bus_LV_2054-11_0_4_node_112 | 0.4 | n |  | TRUE
106 | bus_LV_2054-11_0_4_node_113 | 0.4 | n |  | TRUE
107 | bus_LV_2054-11_0_4_node_119 | 0.4 | n |  | TRUE
108 | bus_LV_2054-11_0_4_node_114 | 0.4 | n |  | TRUE
109 | bus_LV_2054-11_0_4_node_115 | 0.4 | n |  | TRUE
110 | bus_LV_2054-11_0_4_node_88 | 0.4 | n |  | TRUE
111 | bus_LV_2054-11_0_4_node_89 | 0.4 | n |  | TRUE
112 | bus_LV_2054-11_0_4_node_94 | 0.4 | n |  | TRUE
113 | bus_LV_2054-11_0_4_node_99 | 0.4 | n |  | TRUE
114 | bus_LV_2054-11_0_4_node_92 | 0.4 | n |  | TRUE
115 | bus_LV_2054-11_0_4_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_2054-11_0_4_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_2054-11_0_4_node_95 | 0.4 | n |  | TRUE
118 | bus_MV_454_1_node_254 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2054-11_0_4_load_0 | 0 | 0.00080432 | 0.00020158 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2054-11_0_4_load_102 | 3 | 0.0021133 | 0.00052963 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2054-11_0_4_load_3 | 4 | 0.00071718 | 0.00017974 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2054-11_0_4_load_21 | 5 | 0.0002021 | 5.0652e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2054-11_0_4_load_22 | 6 | 0.00026713 | 6.6949e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2054-11_0_4_load_23 | 7 | 0.00013629 | 3.4159e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2054-11_0_4_load_101 | 8 | 0.00037877 | 9.4929e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2054-11_0_4_load_20 | 11 | 0.00078697 | 0.00019723 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2054-11_0_4_load_31 | 12 | 0.00024206 | 6.0665e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2054-11_0_4_load_18 | 13 | 0.00047597 | 0.00011929 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2054-11_0_4_load_4 | 14 | 0.00020637 | 5.1722e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2054-11_0_4_load_5 | 15 | 0.00016051 | 4.0227e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2054-11_0_4_load_6 | 16 | 0.00015818 | 3.9643e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2054-11_0_4_load_8 | 17 | 0.0001622 | 4.065e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2054-11_0_4_load_116 | 19 | 0.00013186 | 3.3047e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2054-11_0_4_load_30 | 21 | 0.00037009 | 9.2754e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2054-11_0_4_load_28 | 22 | 0.00012727 | 3.1896e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2054-11_0_4_load_117 | 24 | 0.012995 | 0.0032568 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2054-11_0_4_load_11 | 26 | 0.00014725 | 3.6904e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2054-11_0_4_load_12 | 27 | 0.00016318 | 4.0896e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2054-11_0_4_load_13 | 28 | 0.0001763 | 4.4185e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2054-11_0_4_load_14 | 29 | 0.00013257 | 3.3224e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2054-11_0_4_load_27 | 30 | 0.0001366 | 3.4235e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2054-11_0_4_load_15 | 31 | 0.0008442 | 0.00021158 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2054-11_0_4_load_16 | 32 | 0.00058807 | 0.00014738 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2054-11_0_4_load_17 | 33 | 0.00050197 | 0.00012581 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2054-11_0_4_load_19 | 34 | 0.00073191 | 0.00018343 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2054-11_0_4_load_24 | 35 | 0.00016627 | 4.1672e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2054-11_0_4_load_25 | 36 | 0.00025524 | 6.397e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2054-11_0_4_load_26 | 37 | 0.00019196 | 4.811e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2054-11_0_4_load_104 | 38 | 0.00040778 | 0.0001022 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2054-11_0_4_load_105 | 39 | 0.00037011 | 9.2758e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2054-11_0_4_load_32 | 40 | 0.0029336 | 0.00073522 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2054-11_0_4_load_33 | 41 | 0.0035397 | 0.00088714 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2054-11_0_4_load_35 | 43 | 0.00031631 | 7.9274e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2054-11_0_4_load_97 | 45 | 0.0044857 | 0.0011242 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2054-11_0_4_load_98 | 46 | 0.0052146 | 0.0013069 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2054-11_0_4_load_96 | 47 | 0.0041413 | 0.0010379 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2054-11_0_4_load_41 | 48 | 0.0016917 | 0.00042397 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2054-11_0_4_load_37 | 49 | 0.0013406 | 0.00033599 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2054-11_0_4_load_38 | 50 | 0.0023823 | 0.00059707 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2054-11_0_4_load_40 | 52 | 0.0011028 | 0.00027639 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2054-11_0_4_load_42 | 53 | 0.0027158 | 0.00068064 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2054-11_0_4_load_47 | 55 | 0.0036112 | 0.00090505 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2054-11_0_4_load_44 | 56 | 0.0067424 | 0.0016898 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2054-11_0_4_load_48 | 57 | 0.0084952 | 0.0021291 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2054-11_0_4_load_45 | 58 | 0.0011354 | 0.00028456 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2054-11_0_4_load_103 | 60 | 0.0037186 | 0.00093198 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2054-11_0_4_load_91 | 61 | 0.0018323 | 0.00045922 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2054-11_0_4_load_90 | 62 | 0.0034078 | 0.00085407 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2054-11_0_4_load_49 | 63 | 0.00073243 | 0.00018356 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2054-11_0_4_load_52 | 65 | 0.0013056 | 0.00032722 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2054-11_0_4_load_51 | 66 | 0.0038261 | 0.00095892 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2054-11_0_4_load_58 | 68 | 0.002019 | 0.000506 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2054-11_0_4_load_53 | 69 | 0.0015061 | 0.00037747 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2054-11_0_4_load_54 | 70 | 0.0012053 | 0.00030207 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2054-11_0_4_load_55 | 71 | 0.0027338 | 0.00068514 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2054-11_0_4_load_56 | 72 | 0.0012861 | 0.00032233 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2054-11_0_4_load_57 | 73 | 0.0018166 | 0.00045528 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2054-11_0_4_load_83 | 76 | 0.0020494 | 0.00051362 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2054-11_0_4_load_59 | 77 | 0.0017678 | 0.00044305 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2054-11_0_4_load_62 | 78 | 0.0013641 | 0.00034187 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2054-11_0_4_load_63 | 79 | 0.0012281 | 0.00030778 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2054-11_0_4_load_64 | 80 | 0.00050646 | 0.00012693 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2054-11_0_4_load_65 | 81 | 0.0020727 | 0.00051948 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2054-11_0_4_load_66 | 83 | 0.0015806 | 0.00039613 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2054-11_0_4_load_67 | 84 | 0.0026987 | 0.00067637 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2054-11_0_4_load_69 | 86 | 0.0019229 | 0.00048193 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2054-11_0_4_load_70 | 87 | 0.0019636 | 0.00049214 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2054-11_0_4_load_71 | 88 | 0.0057947 | 0.0014523 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2054-11_0_4_load_72 | 89 | 0.0043349 | 0.0010864 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2054-11_0_4_load_85 | 92 | 0.0037664 | 0.00094394 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2054-11_0_4_load_87 | 93 | 0.0032425 | 0.00081264 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2054-11_0_4_load_86 | 94 | 0.0028319 | 0.00070974 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2054-11_0_4_load_81 | 95 | 0.0027841 | 0.00069775 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2054-11_0_4_load_78 | 96 | 0.002285 | 0.00057266 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2054-11_0_4_load_77 | 97 | 0.0017021 | 0.00042659 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2054-11_0_4_load_79 | 98 | 0.0034064 | 0.00085372 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2054-11_0_4_load_106 | 99 | 0.00062505 | 0.00015665 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2054-11_0_4_load_107 | 100 | 0.00042168 | 0.00010568 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2054-11_0_4_load_108 | 101 | 0.00062517 | 0.00015668 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2054-11_0_4_load_109 | 102 | 0.0001276 | 3.1979e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2054-11_0_4_load_110 | 103 | 0.00089153 | 0.00022344 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2054-11_0_4_load_111 | 104 | 0.00018856 | 4.7258e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2054-11_0_4_load_112 | 105 | 0.00036193 | 9.0708e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2054-11_0_4_load_113 | 106 | 0.00036195 | 9.0713e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2054-11_0_4_load_119 | 107 | 0.00029852 | 7.4816e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2054-11_0_4_load_114 | 108 | 0.00014538 | 3.6436e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2054-11_0_4_load_115 | 109 | 0.0019712 | 0.00049403 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2054-11_0_4_load_94 | 112 | 0.0038735 | 0.0009708 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2054-11_0_4_load_99 | 113 | 0.00086489 | 0.00021676 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2054-11_0_4_load_92 | 114 | 0.0068476 | 0.0017162 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2054-11_0_4_load_100 | 115 | 0.0060283 | 0.0015108 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2054-11_0_4_load_93 | 116 | 0.0009921 | 0.00024864 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2054-11_0_4_load_95 | 117 | 0.0015944 | 0.0003996 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 74 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2054-11_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.077785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2054-11_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.040409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2054-11_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.2933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2054-11_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.020518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2054-11_0_4_line_4 | NAYY 4x150 SE | 3 | 8 | 0.08665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2054-11_0_4_line_5 | NAYY 4x150 SE | 4 | 11 | 0.020508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2054-11_0_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.0051599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2054-11_0_4_line_7 | NAYY 4x150 SE | 5 | 7 | 0.014325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2054-11_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.045901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2054-11_0_4_line_9 | NAYY 4x150 SE | 7 | 12 | 0.048395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2054-11_0_4_line_10 | NAYY 4x150 SE | 8 | 43 | 0.0084836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2054-11_0_4_line_11 | NAYY 4x150 SE | 9 | 10 | 0.051581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2054-11_0_4_line_12 | NAYY 4x150 SE | 10 | 18 | 0.043741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2054-11_0_4_line_13 | NAYY 4x150 SE | 10 | 15 | 0.029084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2054-11_0_4_line_14 | NAYY 4x150 SE | 11 | 13 | 0.0047723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2054-11_0_4_line_15 | NAYY 4x150 SE | 12 | 37 | 0.0044508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2054-11_0_4_line_16 | NAYY 4x150 SE | 13 | 32 | 0.017447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2054-11_0_4_line_17 | NAYY 4x150 SE | 14 | 15 | 0.010657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2054-11_0_4_line_18 | NAYY 4x150 SE | 14 | 16 | 0.013267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2054-11_0_4_line_19 | NAYY 4x150 SE | 16 | 17 | 0.0039643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2054-11_0_4_line_20 | NAYY 4x150 SE | 18 | 19 | 0.010562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2054-11_0_4_line_21 | NAYY 4x150 SE | 18 | 20 | 0.070728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2054-11_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 0.0016702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2054-11_0_4_line_23 | NAYY 4x150 SE | 20 | 22 | 0.049574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2054-11_0_4_line_24 | NAYY 4x150 SE | 21 | 38 | 0.0024219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2054-11_0_4_line_25 | NAYY 4x150 SE | 22 | 30 | 0.0077411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2054-11_0_4_line_26 | NAYY 4x150 SE | 23 | 24 | 0.017883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2054-11_0_4_line_27 | NAYY 4x150 SE | 23 | 25 | 0.050807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2054-11_0_4_line_28 | NAYY 4x150 SE | 25 | 82 | 0.050789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2054-11_0_4_line_29 | NAYY 4x150 SE | 25 | 81 | 0.017379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2054-11_0_4_line_30 | NAYY 4x150 SE | 26 | 27 | 0.01059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2054-11_0_4_line_31 | NAYY 4x150 SE | 26 | 28 | 0.023958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2054-11_0_4_line_32 | NAYY 4x150 SE | 27 | 29 | 0.0095747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2054-11_0_4_line_33 | NAYY 4x150 SE | 29 | 30 | 0.0045713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2054-11_0_4_line_34 | NAYY 4x150 SE | 31 | 32 | 0.0017549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2054-11_0_4_line_35 | NAYY 4x150 SE | 31 | 33 | 0.0089934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2054-11_0_4_line_36 | NAYY 4x150 SE | 33 | 34 | 0.02264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2054-11_0_4_line_37 | NAYY 4x150 SE | 34 | 35 | 0.0032115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2054-11_0_4_line_38 | NAYY 4x150 SE | 35 | 36 | 0.027821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2054-11_0_4_line_39 | NAYY 4x150 SE | 36 | 37 | 0.0056559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2054-11_0_4_line_40 | NAYY 4x150 SE | 38 | 39 | 0.0037495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2054-11_0_4_line_41 | NAYY 4x150 SE | 39 | 99 | 0.023962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2054-11_0_4_line_42 | NAYY 4x150 SE | 40 | 41 | 0.0048129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2054-11_0_4_line_43 | NAYY 4x150 SE | 40 | 42 | 0.017961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_2054-11_0_4_line_44 | NAYY 4x150 SE | 41 | 43 | 0.019394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2054-11_0_4_line_45 | NAYY 4x150 SE | 42 | 44 | 0.065193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
46 | LV_2054-11_0_4_line_46 | NAYY 4x150 SE | 44 | 45 | 0.011294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
47 | LV_2054-11_0_4_line_47 | NAYY 4x150 SE | 44 | 46 | 0.048429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2054-11_0_4_line_48 | NAYY 4x150 SE | 45 | 47 | 0.0093988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_2054-11_0_4_line_49 | NAYY 4x150 SE | 46 | 48 | 0.041118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2054-11_0_4_line_50 | NAYY 4x150 SE | 47 | 117 | 0.019168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_2054-11_0_4_line_51 | NAYY 4x150 SE | 49 | 50 | 0.014712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2054-11_0_4_line_52 | NAYY 4x150 SE | 49 | 51 | 0.022361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2054-11_0_4_line_53 | NAYY 4x150 SE | 50 | 52 | 0.011506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2054-11_0_4_line_54 | NAYY 4x150 SE | 51 | 53 | 0.059895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2054-11_0_4_line_55 | NAYY 4x150 SE | 52 | 54 | 0.02564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2054-11_0_4_line_56 | NAYY 4x150 SE | 54 | 55 | 0.014915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2054-11_0_4_line_57 | NAYY 4x150 SE | 54 | 56 | 0.015692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2054-11_0_4_line_58 | NAYY 4x150 SE | 55 | 57 | 0.0027503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2054-11_0_4_line_59 | NAYY 4x150 SE | 56 | 58 | 0.026552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2054-11_0_4_line_60 | NAYY 4x150 SE | 57 | 63 | 0.016336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2054-11_0_4_line_61 | NAYY 4x150 SE | 58 | 59 | 0.0071502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2054-11_0_4_line_62 | NAYY 4x150 SE | 59 | 60 | 0.024033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2054-11_0_4_line_63 | NAYY 4x150 SE | 59 | 61 | 0.0043664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2054-11_0_4_line_64 | NAYY 4x150 SE | 61 | 62 | 0.051208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2054-11_0_4_line_65 | NAYY 4x150 SE | 62 | 110 | 0.021918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2054-11_0_4_line_66 | NAYY 4x150 SE | 63 | 64 | 0.0054173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2054-11_0_4_line_67 | NAYY 4x150 SE | 64 | 65 | 0.02653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2054-11_0_4_line_68 | NAYY 4x150 SE | 64 | 66 | 0.035929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2054-11_0_4_line_69 | NAYY 4x150 SE | 65 | 67 | 0.011859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2054-11_0_4_line_70 | NAYY 4x150 SE | 67 | 68 | 0.0022065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2054-11_0_4_line_71 | NAYY 4x150 SE | 68 | 77 | 0.021872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2054-11_0_4_line_72 | NAYY 4x150 SE | 69 | 70 | 0.0028383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2054-11_0_4_line_73 | NAYY 4x150 SE | 69 | 71 | 0.050594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2054-11_0_4_line_74 | NAYY 4x150 SE | 70 | 72 | 0.0052585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2054-11_0_4_line_75 | NAYY 4x150 SE | 71 | 73 | 0.0051466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2054-11_0_4_line_76 | NAYY 4x150 SE | 73 | 74 | 0.016617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2054-11_0_4_line_77 | NAYY 4x150 SE | 74 | 75 | 0.023705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
78 | LV_2054-11_0_4_line_78 | NAYY 4x150 SE | 74 | 76 | 0.00061475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2054-11_0_4_line_79 | NAYY 4x150 SE | 75 | 93 | 0.039835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
80 | LV_2054-11_0_4_line_80 | NAYY 4x150 SE | 76 | 95 | 0.030294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2054-11_0_4_line_81 | NAYY 4x150 SE | 78 | 79 | 0.019347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2054-11_0_4_line_82 | NAYY 4x150 SE | 78 | 80 | 0.0056676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2054-11_0_4_line_83 | NAYY 4x150 SE | 79 | 81 | 0.0058238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2054-11_0_4_line_84 | NAYY 4x150 SE | 82 | 91 | 0.009346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2054-11_0_4_line_85 | NAYY 4x150 SE | 82 | 87 | 0.020187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2054-11_0_4_line_86 | NAYY 4x150 SE | 83 | 84 | 0.01806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2054-11_0_4_line_87 | NAYY 4x150 SE | 83 | 85 | 0.0031436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2054-11_0_4_line_88 | NAYY 4x150 SE | 84 | 86 | 0.025681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2054-11_0_4_line_89 | NAYY 4x150 SE | 85 | 87 | 0.01692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2054-11_0_4_line_90 | NAYY 4x150 SE | 85 | 88 | 0.018239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2054-11_0_4_line_91 | NAYY 4x150 SE | 86 | 89 | 0.025878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2054-11_0_4_line_92 | NAYY 4x150 SE | 89 | 90 | 0.016802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2054-11_0_4_line_93 | NAYY 4x150 SE | 90 | 92 | 0.0090814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2054-11_0_4_line_94 | NAYY 4x150 SE | 91 | 95 | 0.032265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2054-11_0_4_line_95 | NAYY 4x150 SE | 91 | 96 | 0.018719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2054-11_0_4_line_96 | NAYY 4x150 SE | 92 | 94 | 0.0068095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2054-11_0_4_line_97 | NAYY 4x150 SE | 93 | 110 | 0.0023347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
98 | LV_2054-11_0_4_line_98 | NAYY 4x150 SE | 96 | 97 | 0.0027946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2054-11_0_4_line_99 | NAYY 4x150 SE | 97 | 98 | 0.010566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2054-11_0_4_line_100 | NAYY 4x150 SE | 99 | 100 | 0.0017812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2054-11_0_4_line_101 | NAYY 4x150 SE | 100 | 101 | 0.0012695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2054-11_0_4_line_102 | NAYY 4x150 SE | 101 | 102 | 0.018884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2054-11_0_4_line_103 | NAYY 4x150 SE | 102 | 103 | 0.0049746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2054-11_0_4_line_104 | NAYY 4x150 SE | 103 | 104 | 0.0085327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2054-11_0_4_line_105 | NAYY 4x150 SE | 104 | 105 | 0.040853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2054-11_0_4_line_106 | NAYY 4x150 SE | 105 | 106 | 0.00049942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2054-11_0_4_line_107 | NAYY 4x150 SE | 105 | 107 | 0.13846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2054-11_0_4_line_108 | NAYY 4x150 SE | 106 | 108 | 0.012632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2054-11_0_4_line_109 | NAYY 4x150 SE | 108 | 109 | 0.078643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2054-11_0_4_line_110 | NAYY 4x150 SE | 110 | 111 | 0.018085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
111 | LV_2054-11_0_4_line_111 | NAYY 4x150 SE | 111 | 112 | 0.027327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
112 | LV_2054-11_0_4_line_112 | NAYY 4x150 SE | 111 | 113 | 0.02566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2054-11_0_4_line_113 | NAYY 4x150 SE | 112 | 114 | 4.1343e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
114 | LV_2054-11_0_4_line_114 | NAYY 4x150 SE | 113 | 115 | 0.0058484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2054-11_0_4_line_115 | NAYY 4x150 SE | 114 | 116 | 0.0080972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
116 | LV_2054-11_0_4_line_116 | NAYY 4x150 SE | 116 | 117 | 0.0082711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2054-11_0_4_trafo_82 | 0.25 MVA 20/0.4 kV | 118 | 74 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2552808.7237 | 1187775.2088 | 2552771.5159 | 1187843.5178
1 | 2552755.1407 | 1187879.4452 | 2552754.2679 | 1187875.1831 | 2552771.5159 | 1187843.5178
2 | 2552939.6845 | 1187512.7685 | 2552808.7237 | 1187775.2088
3 | 2552755.1407 | 1187879.4452 | 2552774.7568 | 1187885.4603
4 | 2552871.6917 | 1187459.0548 | 2552939.6845 | 1187512.7685
5 | 2552774.7568 | 1187885.4603 | 2552775.6043 | 1187885.7202 | 2552793.8518 | 1187892.9322
6 | 2552926.1081 | 1187909.431 | 2552928.2986 | 1187904.7591
7 | 2552920.0269 | 1187922.4006 | 2552926.1081 | 1187909.431
8 | 2552949.1566 | 1187863.8834 | 2552933.9963 | 1187892.6075 | 2552928.2986 | 1187904.7591
9 | 2552920.0269 | 1187922.4006 | 2552873.4912 | 1187935.6859
10 | 2552871.6917 | 1187459.0548 | 2552865.0347 | 1187453.7958
11 | 2552949.1566 | 1187863.8834 | 2552975.5127 | 1187880.2738 | 2552993.8351 | 1187889.8015
12 | 2553033.7303 | 1187907.9867 | 2552993.8351 | 1187889.8015
13 | 2552993.8351 | 1187889.8015 | 2552979.0549 | 1187914.8494
14 | 2552798.29 | 1187894.6864 | 2552793.8518 | 1187892.9322
15 | 2552873.4912 | 1187935.6859 | 2552869.3112 | 1187934.1569
16 | 2552798.29 | 1187894.6864 | 2552810.5989 | 1187899.5513 | 2552814.3768 | 1187901.412
17 | 2552973.6392 | 1187924.0273 | 2552979.0549 | 1187914.8494
18 | 2552973.6392 | 1187924.0273 | 2552966.897 | 1187935.4533
19 | 2552964.8823 | 1187938.8675 | 2552966.897 | 1187935.4533
20 | 2553033.7303 | 1187907.9867 | 2553028.2325 | 1187917.0126
21 | 2553033.7303 | 1187907.9867 | 2553065.384 | 1187923.9022 | 2553096.6321 | 1187940.6549
22 | 2553096.6321 | 1187940.6549 | 2553098.1093 | 1187941.4344
23 | 2553096.6321 | 1187940.6549 | 2553091.5174 | 1187950.8674 | 2553087.0048 | 1187957.1396 | 2553082.0907 | 1187960.8358 | 2553074.1721 | 1187962.7435 | 2553065.9562 | 1187963.7085 | 2553060.563 | 1187963.7176 | 2553058.179 | 1187963.0876
24 | 2553100.2513 | 1187942.5647 | 2553098.1093 | 1187941.4344
25 | 2553058.179 | 1187963.0876 | 2553052.1466 | 1187961.4936 | 2553050.997 | 1187960.5275
26 | 2553159.4507 | 1187526.1232 | 2553143.5255 | 1187517.8991
27 | 2553134.2317 | 1187493.3807 | 2553162.0929 | 1187507.9703 | 2553162.6362 | 1187511.1011 | 2553163.8883 | 1187517.0501 | 2553159.4507 | 1187526.1232
28 | 2553088.9107 | 1187470.4571 | 2553122.1987 | 1187487.294 | 2553134.2317 | 1187493.3807
29 | 2553134.2317 | 1187493.3807 | 2553143.0182 | 1187478.3865
30 | 2553030.6257 | 1187946.8316 | 2553040.1671 | 1187951.4266 | 2553040.1671 | 1187951.4266
31 | 2553007.5424 | 1187941.033 | 2553025.3806 | 1187944.3056 | 2553030.6257 | 1187946.8316
32 | 2553047.4973 | 1187957.5865 | 2553040.1671 | 1187951.4266
33 | 2553047.4973 | 1187957.5865 | 2553050.997 | 1187960.5275
34 | 2552815.9512 | 1187902.1874 | 2552814.3768 | 1187901.412
35 | 2552823.6449 | 1187906.5656 | 2552823.1508 | 1187905.7333 | 2552815.9512 | 1187902.1874
36 | 2552823.6449 | 1187906.5656 | 2552827.349 | 1187912.8041 | 2552830.7845 | 1187920.8703 | 2552834.8778 | 1187926.0699
37 | 2552836.8643 | 1187928.5932 | 2552836.8643 | 1187928.5932 | 2552834.8778 | 1187926.0699
38 | 2552836.8643 | 1187928.5932 | 2552853.4391 | 1187928.3512 | 2552863.9995 | 1187932.214
39 | 2552863.9995 | 1187932.214 | 2552869.3112 | 1187934.1569
40 | 2553100.2513 | 1187942.5647 | 2553103.5674 | 1187944.3146
41 | 2553124.7597 | 1187955.4973 | 2553103.5674 | 1187944.3146
42 | 2552846.0401 | 1187438.7903 | 2552849.8167 | 1187441.7737
43 | 2552831.9466 | 1187427.6566 | 2552846.0401 | 1187438.7903
44 | 2552849.8167 | 1187441.7737 | 2552865.0347 | 1187453.7958
45 | 2552831.9466 | 1187427.6566 | 2552834.0931 | 1187425.1049 | 2552857.184 | 1187397.7298 | 2552874.0019 | 1187377.8418
46 | 2552874.0019 | 1187377.8418 | 2552884.7199 | 1187381.4037
47 | 2552874.0019 | 1187377.8418 | 2552895.8245 | 1187349.2318 | 2552904.4082 | 1187340.219
48 | 2552893.2034 | 1187385.3423 | 2552888.5431 | 1187382.6742 | 2552884.7199 | 1187381.4037
49 | 2552904.4082 | 1187340.219 | 2552917.4271 | 1187326.5491 | 2552928.8633 | 1187307.4737
50 | 2552893.2034 | 1187385.3423 | 2552903.2728 | 1187391.1072 | 2552909.8712 | 1187394.807
51 | 2552995.2306 | 1187273.8954 | 2553003.0254 | 1187277.8596 | 2553008.0832 | 1187281.0266
52 | 2552974.4081 | 1187266.2561 | 2552982.8972 | 1187267.9013 | 2552990.5397 | 1187271.5099 | 2552995.2306 | 1187273.8954
53 | 2553008.0832 | 1187281.0266 | 2553017.8352 | 1187287.1329
54 | 2552974.4081 | 1187266.2561 | 2552969.4841 | 1187261.9925 | 2552959.1901 | 1187262.6962 | 2552940.283 | 1187268.2926 | 2552925.4338 | 1187270.8776 | 2552917.3223 | 1187269.2513
55 | 2553039.5666 | 1187300.7404 | 2553017.8352 | 1187287.1329
56 | 2553039.5666 | 1187300.7404 | 2553053.516 | 1187306.0192
57 | 2553039.5666 | 1187300.7404 | 2553038.4846 | 1187306.7411 | 2553034.3186 | 1187315.3837
58 | 2553056.0883 | 1187306.9926 | 2553053.516 | 1187306.0192
59 | 2553034.3186 | 1187315.3837 | 2553028.5006 | 1187327.4532 | 2553021.5856 | 1187332.8994 | 2553018.6089 | 1187336.073
60 | 2553056.0883 | 1187306.9926 | 2553071.3673 | 1187312.7744
61 | 2553013.7172 | 1187341.2881 | 2553018.6089 | 1187336.073
62 | 2553013.7172 | 1187341.2881 | 2553034.5409 | 1187353.3866
63 | 2553013.7172 | 1187341.2881 | 2553010.9889 | 1187344.6971
64 | 2552979.9261 | 1187385.3645 | 2552987.751 | 1187373.7324 | 2553010.9889 | 1187344.6971
65 | 2552967.6922 | 1187403.5511 | 2552979.9261 | 1187385.3645
66 | 2553076.434 | 1187314.6918 | 2553071.3673 | 1187312.7744
67 | 2553076.434 | 1187314.6918 | 2553095.2856 | 1187323.4041 | 2553100.1179 | 1187326.5436
68 | 2553076.434 | 1187314.6918 | 2553077.3259 | 1187311.6831 | 2553078.8291 | 1187305.8904 | 2553092.845 | 1187283.0404
69 | 2553110.0626 | 1187333.0045 | 2553100.1179 | 1187326.5436
70 | 2553110.0626 | 1187333.0045 | 2553111.4736 | 1187333.9273 | 2553111.9086 | 1187334.213
71 | 2553111.9086 | 1187334.213 | 2553130.1909 | 1187346.2197
72 | 2553069.8718 | 1187389.3534 | 2553072.6906 | 1187389.6851
73 | 2553069.8718 | 1187389.3534 | 2553053.9964 | 1187387.4858 | 2553036.2725 | 1187417.2126
74 | 2553077.913 | 1187390.2995 | 2553072.6906 | 1187389.6851
75 | 2553036.2725 | 1187417.2126 | 2553033.6369 | 1187421.6331
76 | 2553025.1271 | 1187435.9059 | 2553033.6369 | 1187421.6331
77 | 2553025.1271 | 1187435.9059 | 2553004.2411 | 1187424.5862
78 | 2553025.6676 | 1187436.1987 | 2553025.1271 | 1187435.9059
79 | 2553004.2411 | 1187424.5862 | 2552969.7157 | 1187404.7156
80 | 2553052.3043 | 1187450.6284 | 2553025.6676 | 1187436.1987
81 | 2553155.7443 | 1187456.6693 | 2553145.9626 | 1187473.3618
82 | 2553155.7443 | 1187456.6693 | 2553158.6097 | 1187451.7794
83 | 2553143.0182 | 1187478.3865 | 2553145.9626 | 1187473.3618
84 | 2553080.6745 | 1187465.9971 | 2553082.2451 | 1187466.8519 | 2553088.9107 | 1187470.4571
85 | 2553088.9107 | 1187470.4571 | 2553078.4956 | 1187487.75
86 | 2553063.1235 | 1187497.7548 | 2553059.3083 | 1187496.4483 | 2553047.035 | 1187489.6571
87 | 2553066.2233 | 1187497.8059 | 2553063.7834 | 1187497.9807 | 2553063.1235 | 1187497.7548
88 | 2553024.5645 | 1187477.2235 | 2553047.035 | 1187489.6571
89 | 2553066.2233 | 1187497.8059 | 2553068.2438 | 1187497.6566 | 2553072.4442 | 1187496.2784 | 2553076.6129 | 1187490.876 | 2553078.4956 | 1187487.75
90 | 2553081.7855 | 1187507.3889 | 2553066.2233 | 1187497.8059
91 | 2553024.5645 | 1187477.2235 | 2553001.922 | 1187464.6947
92 | 2552987.2205 | 1187456.5598 | 2553001.922 | 1187464.6947
93 | 2552987.2205 | 1187456.5598 | 2552979.4766 | 1187451.8161
94 | 2553080.6745 | 1187465.9971 | 2553052.3043 | 1187450.6284
95 | 2553080.6745 | 1187465.9971 | 2553089.8505 | 1187449.6812
96 | 2552979.4766 | 1187451.8161 | 2552973.67 | 1187448.259
97 | 2552967.6922 | 1187403.5511 | 2552969.7157 | 1187404.7156
98 | 2553091.2203 | 1187447.2454 | 2553089.8505 | 1187449.6812
99 | 2553096.3996 | 1187438.0361 | 2553091.2203 | 1187447.2454
100 | 2553124.7597 | 1187955.4973 | 2553126.335 | 1187956.3286
101 | 2553127.4578 | 1187956.9211 | 2553126.335 | 1187956.3286
102 | 2553127.4578 | 1187956.9211 | 2553132.7115 | 1187959.6934 | 2553143.7679 | 1187966.4232
103 | 2553148.0172 | 1187969.0097 | 2553143.7679 | 1187966.4232
104 | 2553148.0172 | 1187969.0097 | 2553155.3059 | 1187973.4462
105 | 2553155.3059 | 1187973.4462 | 2553169.082 | 1187981.8315 | 2553189.9517 | 1187995.0913
106 | 2553190.3732 | 1187995.3591 | 2553189.9517 | 1187995.0913
107 | 2553189.9517 | 1187995.0913 | 2553253.4318 | 1187872.0439
108 | 2553190.3732 | 1187995.3591 | 2553201.035 | 1188002.1333
109 | 2553201.035 | 1188002.1333 | 2553242.0215 | 1188028.1746 | 2553259.8307 | 1188039.497 | 2553267.4215 | 1188044.295
110 | 2552967.6922 | 1187403.5511 | 2552950.7131 | 1187397.1924
111 | 2552950.7131 | 1187397.1924 | 2552946.9228 | 1187395.4323 | 2552937.8949 | 1187392.2017 | 2552932.6101 | 1187392.4768 | 2552925.0431 | 1187395.806
112 | 2552950.7131 | 1187397.1924 | 2552960.1148 | 1187373.3163
113 | 2552925.0052 | 1187395.8227 | 2552925.0431 | 1187395.806
114 | 2552965.5294 | 1187371.1058 | 2552960.1148 | 1187373.3163
115 | 2552925.0052 | 1187395.8227 | 2552919.6169 | 1187398.1934 | 2552917.4178 | 1187397.9709
116 | 2552909.8712 | 1187394.807 | 2552911.8171 | 1187395.898 | 2552915.8451 | 1187397.8118 | 2552917.4178 | 1187397.9709

## bus_geodata
| x | y | coords
0 | 2552771.5159 | 1187843.5178
1 | 2552808.7237 | 1187775.2088
2 | 2552755.1407 | 1187879.4452
3 | 2552939.6845 | 1187512.7685
4 | 2552774.7568 | 1187885.4603
5 | 2552926.1081 | 1187909.431
6 | 2552928.2986 | 1187904.7591
7 | 2552920.0269 | 1187922.4006
8 | 2552871.6917 | 1187459.0548
9 | 2552949.1566 | 1187863.8834
10 | 2552993.8351 | 1187889.8015
11 | 2552793.8518 | 1187892.9322
12 | 2552873.4912 | 1187935.6859
13 | 2552798.29 | 1187894.6864
14 | 2552973.6392 | 1187924.0273
15 | 2552979.0549 | 1187914.8494
16 | 2552966.897 | 1187935.4533
17 | 2552964.8823 | 1187938.8675
18 | 2553033.7303 | 1187907.9867
19 | 2553028.2325 | 1187917.0126
20 | 2553096.6321 | 1187940.6549
21 | 2553098.1093 | 1187941.4344
22 | 2553058.179 | 1187963.0876
23 | 2553159.4507 | 1187526.1232
24 | 2553143.5255 | 1187517.8991
25 | 2553134.2317 | 1187493.3807
26 | 2553030.6257 | 1187946.8316
27 | 2553040.1671 | 1187951.4266
28 | 2553007.5424 | 1187941.033
29 | 2553047.4973 | 1187957.5865
30 | 2553050.997 | 1187960.5275
31 | 2552815.9512 | 1187902.1874
32 | 2552814.3768 | 1187901.412
33 | 2552823.6449 | 1187906.5656
34 | 2552834.8778 | 1187926.0698
35 | 2552836.8643 | 1187928.5932
36 | 2552863.9995 | 1187932.214
37 | 2552869.3112 | 1187934.1569
38 | 2553100.2513 | 1187942.5647
39 | 2553103.5674 | 1187944.3146
40 | 2552846.0401 | 1187438.7903
41 | 2552849.8167 | 1187441.7737
42 | 2552831.9466 | 1187427.6566
43 | 2552865.0347 | 1187453.7958
44 | 2552874.0019 | 1187377.8418
45 | 2552884.7199 | 1187381.4037
46 | 2552904.4082 | 1187340.219
47 | 2552893.2034 | 1187385.3423
48 | 2552928.8633 | 1187307.4737
49 | 2552995.2306 | 1187273.8954
50 | 2553008.0832 | 1187281.0266
51 | 2552974.4081 | 1187266.2561
52 | 2553017.8352 | 1187287.1329
53 | 2552917.3223 | 1187269.2513
54 | 2553039.5666 | 1187300.7404
55 | 2553053.516 | 1187306.0192
56 | 2553034.3186 | 1187315.3837
57 | 2553056.0883 | 1187306.9925
58 | 2553018.6089 | 1187336.073
59 | 2553013.7172 | 1187341.2881
60 | 2553034.5409 | 1187353.3866
61 | 2553010.9889 | 1187344.6971
62 | 2552979.9261 | 1187385.3645
63 | 2553071.3673 | 1187312.7744
64 | 2553076.434 | 1187314.6918
65 | 2553100.1179 | 1187326.5436
66 | 2553092.845 | 1187283.0404
67 | 2553110.0626 | 1187333.0045
68 | 2553111.9086 | 1187334.213
69 | 2553069.8718 | 1187389.3534
70 | 2553072.6906 | 1187389.6851
71 | 2553036.2725 | 1187417.2126
72 | 2553077.913 | 1187390.2995
73 | 2553033.6369 | 1187421.6331
74 | 2553025.1271 | 1187435.9059
75 | 2553004.2411 | 1187424.5862
76 | 2553025.6676 | 1187436.1987
77 | 2553130.1909 | 1187346.2197
78 | 2553155.7443 | 1187456.6693
79 | 2553145.9626 | 1187473.3618
80 | 2553158.6097 | 1187451.7794
81 | 2553143.0182 | 1187478.3865
82 | 2553088.9107 | 1187470.4571
83 | 2553063.1235 | 1187497.7548
84 | 2553047.035 | 1187489.6571
85 | 2553066.2233 | 1187497.8059
86 | 2553024.5645 | 1187477.2235
87 | 2553078.4956 | 1187487.75
88 | 2553081.7855 | 1187507.3889
89 | 2553001.922 | 1187464.6947
90 | 2552987.2205 | 1187456.5598
91 | 2553080.6745 | 1187465.9971
92 | 2552979.4766 | 1187451.8161
93 | 2552969.7157 | 1187404.7156
94 | 2552973.67 | 1187448.259
95 | 2553052.3043 | 1187450.6284
96 | 2553089.8505 | 1187449.6812
97 | 2553091.2203 | 1187447.2454
98 | 2553096.3996 | 1187438.0361
99 | 2553124.7597 | 1187955.4973
100 | 2553126.335 | 1187956.3286
101 | 2553127.4577 | 1187956.9211
102 | 2553143.7679 | 1187966.4232
103 | 2553148.0172 | 1187969.0097
104 | 2553155.3059 | 1187973.4462
105 | 2553189.9517 | 1187995.0913
106 | 2553190.3732 | 1187995.3591
107 | 2553253.4318 | 1187872.0439
108 | 2553201.035 | 1188002.1333
109 | 2553267.4215 | 1188044.295
110 | 2552967.6922 | 1187403.5511
111 | 2552950.7131 | 1187397.1924
112 | 2552925.0431 | 1187395.806
113 | 2552960.1148 | 1187373.3163
114 | 2552925.0052 | 1187395.8227
115 | 2552965.5294 | 1187371.1058
116 | 2552917.4178 | 1187397.9709
117 | 2552909.8712 | 1187394.807
118 | 2553004.2411 | 1187424.5862

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97806 | -0.15459 | 0.00080432 | 0.00020158
1 | 0.97986 | -0.14173 | 0 | 0
2 | 0.97717 | -0.16095 | 0 | 0
3 | 0.98663 | -0.093616 | 0.0021133 | 0.00052963
4 | 0.97672 | -0.16418 | 0.00071718 | 0.00017974
5 | 0.97384 | -0.18496 | 0.0002021 | 5.0652e-05
6 | 0.97377 | -0.18546 | 0.00026713 | 6.6949e-05
7 | 0.97403 | -0.18355 | 0.00013629 | 3.4159e-05
8 | 0.9889 | -0.077642 | 0.00037877 | 9.4929e-05
9 | 0.97317 | -0.18978 | 0 | 0
10 | 0.9725 | -0.19464 | 0 | 0
11 | 0.97629 | -0.16726 | 0.00078697 | 0.00019723
12 | 0.9747 | -0.17869 | 0.00024206 | 6.0665e-05
13 | 0.9762 | -0.16794 | 0.00047597 | 0.00011929
14 | 0.97246 | -0.19491 | 0.00020637 | 5.1722e-05
15 | 0.97247 | -0.19485 | 0.00016051 | 4.0227e-05
16 | 0.97245 | -0.19496 | 0.00015818 | 3.9643e-05
17 | 0.97245 | -0.19496 | 0.0001622 | 4.065e-05
18 | 0.97197 | -0.19844 | 0 | 0
19 | 0.97197 | -0.19846 | 0.00013186 | 3.3047e-05
20 | 0.97114 | -0.20449 | 0 | 0
21 | 0.97112 | -0.20462 | 0.00037009 | 9.2754e-05
22 | 0.97107 | -0.20496 | 0.00012727 | 3.1896e-05
23 | 0.99245 | -0.052932 | 0 | 0
24 | 0.99211 | -0.055288 | 0.012995 | 0.0032568
25 | 0.9934 | -0.046246 | 0 | 0
26 | 0.97105 | -0.20514 | 0.00014725 | 3.6904e-05
27 | 0.97105 | -0.2051 | 0.00016318 | 4.0896e-05
28 | 0.97104 | -0.20519 | 0.0001763 | 4.4185e-05
29 | 0.97106 | -0.20505 | 0.00013257 | 3.3224e-05
30 | 0.97106 | -0.20502 | 0.0001366 | 3.4235e-05
31 | 0.97583 | -0.17056 | 0.0008442 | 0.00021158
32 | 0.97587 | -0.17033 | 0.00058807 | 0.00014738
33 | 0.97568 | -0.17165 | 0.00050197 | 0.00012581
34 | 0.97531 | -0.1743 | 0.00073191 | 0.00018343
35 | 0.97527 | -0.17465 | 0.00016627 | 4.1672e-05
36 | 0.97485 | -0.17764 | 0.00025524 | 6.397e-05
37 | 0.97477 | -0.17823 | 0.00019196 | 4.811e-05
38 | 0.97109 | -0.2048 | 0.00040778 | 0.0001022
39 | 0.97106 | -0.20505 | 0.00037011 | 9.2758e-05
40 | 0.98981 | -0.071255 | 0.0029336 | 0.00073522
41 | 0.98965 | -0.072347 | 0.0035397 | 0.00088714
42 | 0.99014 | -0.06895 | 0 | 0
43 | 0.98913 | -0.076049 | 0.00031631 | 7.9274e-05
44 | 0.99133 | -0.060595 | 0 | 0
45 | 0.99159 | -0.058753 | 0.0044857 | 0.0011242
46 | 0.99085 | -0.063997 | 0.0052146 | 0.0013069
47 | 0.99184 | -0.057007 | 0.0041413 | 0.0010379
48 | 0.99075 | -0.064705 | 0.0016917 | 0.00042397
49 | 0.98699 | -0.091258 | 0.0013406 | 0.00033599
50 | 0.98708 | -0.090645 | 0.0023823 | 0.00059707
51 | 0.9869 | -0.091882 | 0 | 0
52 | 0.98718 | -0.089885 | 0.0011028 | 0.00027639
53 | 0.98667 | -0.093551 | 0.0027158 | 0.00068064
54 | 0.98746 | -0.087903 | 0 | 0
55 | 0.98699 | -0.091228 | 0.0036112 | 0.00090505
56 | 0.98813 | -0.083196 | 0.0067424 | 0.0016898
57 | 0.98692 | -0.091739 | 0.0084952 | 0.0021291
58 | 0.98951 | -0.07342 | 0.0011354 | 0.00028456
59 | 0.98989 | -0.070709 | 0 | 0
60 | 0.98976 | -0.07162 | 0.0037186 | 0.00093198
61 | 0.99015 | -0.06889 | 0.0018323 | 0.00045922
62 | 0.99331 | -0.046668 | 0.0034078 | 0.00085407
63 | 0.98669 | -0.093357 | 0.00073243 | 0.00018356
64 | 0.98662 | -0.093853 | 0 | 0
65 | 0.98643 | -0.095239 | 0.0013056 | 0.00032722
66 | 0.98643 | -0.095263 | 0.0038261 | 0.00095892
67 | 0.98636 | -0.0957 | 0 | 0
68 | 0.98635 | -0.095786 | 0.002019 | 0.000506
69 | 0.99946 | -0.0037871 | 0.0015061 | 0.00037747
70 | 0.99945 | -0.0038577 | 0.0012053 | 0.00030207
71 | 0.99975 | -0.0017653 | 0.0027338 | 0.00068514
72 | 0.99944 | -0.0039253 | 0.0012861 | 0.00032233
73 | 0.9998 | -0.0014191 | 0.0018166 | 0.00045528
74 | 1 | 0 | -0.17652 | -0.044232
75 | 0.99812 | -0.013085 | 0 | 0
76 | 0.99995 | -0.00033948 | 0.0020494 | 0.00051362
77 | 0.9863 | -0.096183 | 0.0017678 | 0.00044305
78 | 0.99319 | -0.047705 | 0.0013641 | 0.00034187
79 | 0.99324 | -0.047339 | 0.0012281 | 0.00030778
80 | 0.99319 | -0.047734 | 0.00050646 | 0.00012693
81 | 0.99327 | -0.047156 | 0.0020727 | 0.00051948
82 | 0.99472 | -0.036921 | 0 | 0
83 | 0.99337 | -0.046465 | 0.0015806 | 0.00039613
84 | 0.99296 | -0.049309 | 0.0026987 | 0.00067637
85 | 0.99344 | -0.04592 | 0 | 0
86 | 0.99249 | -0.052654 | 0.0019229 | 0.00048193
87 | 0.994 | -0.041996 | 0.0019636 | 0.00049214
88 | 0.99329 | -0.046989 | 0.0057947 | 0.0014523
89 | 0.99208 | -0.055523 | 0.0043349 | 0.0010864
90 | 0.99192 | -0.056648 | 0 | 0
91 | 0.9953 | -0.032861 | 0 | 0
92 | 0.99184 | -0.057256 | 0.0037664 | 0.00094394
93 | 0.99495 | -0.035184 | 0.0032425 | 0.00081264
94 | 0.99181 | -0.057451 | 0.0028319 | 0.00070974
95 | 0.99764 | -0.016487 | 0.0027841 | 0.00069775
96 | 0.9951 | -0.034256 | 0.002285 | 0.00057266
97 | 0.99508 | -0.0344 | 0.0017021 | 0.00042659
98 | 0.99503 | -0.034763 | 0.0034064 | 0.00085372
99 | 0.97085 | -0.20659 | 0.00062505 | 0.00015665
100 | 0.97083 | -0.20669 | 0.00042168 | 0.00010568
101 | 0.97082 | -0.20675 | 0.00062517 | 0.00015668
102 | 0.9707 | -0.20763 | 0.0001276 | 3.1979e-05
103 | 0.97067 | -0.20785 | 0.00089153 | 0.00022344
104 | 0.97063 | -0.20816 | 0.00018856 | 4.7258e-05
105 | 0.97044 | -0.20953 | 0.00036193 | 9.0708e-05
106 | 0.97044 | -0.20954 | 0.00036195 | 9.0713e-05
107 | 0.97038 | -0.20997 | 0.00029852 | 7.4816e-05
108 | 0.9704 | -0.20982 | 0.00014538 | 3.6436e-05
109 | 0.97017 | -0.21147 | 0.0019712 | 0.00049403
110 | 0.99477 | -0.036446 | 0 | 0
111 | 0.99397 | -0.042011 | 0 | 0
112 | 0.99291 | -0.049483 | 0.0038735 | 0.0009708
113 | 0.99372 | -0.043799 | 0.00086489 | 0.00021676
114 | 0.99291 | -0.049494 | 0.0068476 | 0.0017162
115 | 0.99367 | -0.044155 | 0.0060283 | 0.0015108
116 | 0.99265 | -0.051271 | 0.0009921 | 0.00024864
117 | 0.9924 | -0.053046 | 0.0015944 | 0.0003996
118 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.015859 | -0.0039733 | 0.015888 | 0.0039832 | 2.8257e-05 | 9.8899e-06 | 0.024128 | 0.024128 | 0.024128 | 0.97806 | -0.15459 | 0.97986 | -0.14173 | 8.9363
1 | 0.015055 | 0.0037717 | -0.015042 | -0.0037671 | 1.3228e-05 | 4.5811e-06 | 0.022904 | 0.022905 | 0.022905 | 0.97806 | -0.15459 | 0.97717 | -0.16095 | 8.4832
2 | -0.015888 | -0.0039832 | 0.015994 | 0.0040204 | 0.00010654 | 3.7256e-05 | 0.024128 | 0.024126 | 0.024128 | 0.97986 | -0.14173 | 0.98663 | -0.093616 | 8.9362
3 | 0.015042 | 0.0037671 | -0.015035 | -0.0037648 | 6.7167e-06 | 2.3264e-06 | 0.022905 | 0.022905 | 0.022905 | 0.97717 | -0.16095 | 0.97672 | -0.16418 | 8.4832
4 | -0.018107 | -0.0045501 | 0.018148 | 0.0045645 | 4.0337e-05 | 1.4405e-05 | 0.027314 | 0.027313 | 0.027314 | 0.98663 | -0.093616 | 0.9889 | -0.077642 | 10.1161
5 | 0.014318 | 0.0035851 | -0.014312 | -0.003583 | 6.0882e-06 | 2.0851e-06 | 0.021812 | 0.021812 | 0.021812 | 0.97672 | -0.16418 | 0.97629 | -0.16726 | 8.0786
6 | 0.0091628 | 0.002291 | -0.0091621 | -0.0022908 | 6.3096e-07 | 1.7848e-07 | 0.013999 | 0.013999 | 0.013999 | 0.97384 | -0.18496 | 0.97377 | -0.18546 | 5.1847
7 | -0.0093649 | -0.0023416 | 0.0093667 | 0.0023422 | 1.8298e-06 | 5.2549e-07 | 0.014308 | 0.014307 | 0.014308 | 0.97384 | -0.18496 | 0.97403 | -0.18355 | 5.2991
8 | 0.008895 | 0.0022239 | -0.0088897 | -0.0022224 | 5.2903e-06 | 1.4641e-06 | 0.013591 | 0.013591 | 0.013591 | 0.97377 | -0.18546 | 0.97317 | -0.18978 | 5.0336
9 | -0.009503 | -0.0023763 | 0.0095094 | 0.0023782 | 6.3629e-06 | 1.8445e-06 | 0.014516 | 0.014515 | 0.014516 | 0.97403 | -0.18355 | 0.9747 | -0.17869 | 5.3762
10 | -0.018527 | -0.0046594 | 0.018531 | 0.0046609 | 4.1157e-06 | 1.4741e-06 | 0.027883 | 0.027883 | 0.027883 | 0.9889 | -0.077642 | 0.98913 | -0.076049 | 10.3271
11 | 0.0088897 | 0.0022224 | -0.0088838 | -0.0022207 | 5.9452e-06 | 1.6462e-06 | 0.013591 | 0.013591 | 0.013591 | 0.97317 | -0.18978 | 0.9725 | -0.19464 | 5.0337
12 | 0.0081965 | 0.0020492 | -0.0081922 | -0.0020481 | 4.2919e-06 | 1.1083e-06 | 0.01254 | 0.01254 | 0.01254 | 0.9725 | -0.19464 | 0.97197 | -0.19844 | 4.6444
13 | 0.00068728 | 0.00017155 | -0.00068726 | -0.0001719 | 2.0062e-08 | -3.5313e-07 | 0.0010514 | 0.0010515 | 0.0010515 | 0.9725 | -0.19464 | 0.97247 | -0.19485 | 0.38944
14 | 0.013525 | 0.0033857 | -0.013524 | -0.0033853 | 1.2653e-06 | 4.2697e-07 | 0.020613 | 0.020613 | 0.020613 | 0.97629 | -0.16726 | 0.9762 | -0.16794 | 7.6343
15 | -0.0097514 | -0.0024388 | 0.009752 | 0.002439 | 6.1535e-07 | 1.8119e-07 | 0.014885 | 0.014885 | 0.014885 | 0.9747 | -0.17869 | 0.97477 | -0.17823 | 5.513
16 | 0.013048 | 0.003266 | -0.013043 | -0.0032646 | 4.3057e-06 | 1.438e-06 | 0.019887 | 0.019887 | 0.019887 | 0.9762 | -0.16794 | 0.97587 | -0.17033 | 7.3656
17 | -0.00052675 | -0.0001318 | 0.00052675 | 0.00013167 | 4.3189e-09 | -1.3055e-07 | 0.00080593 | 0.00080588 | 0.00080593 | 0.97246 | -0.19491 | 0.97247 | -0.19485 | 0.29849
18 | 0.00032037 | 8.008e-05 | -0.00032037 | -8.0244e-05 | 1.9891e-09 | -1.6383e-07 | 0.00049015 | 0.0004902 | 0.0004902 | 0.97246 | -0.19491 | 0.97245 | -0.19496 | 0.18156
19 | 0.0001622 | 4.0601e-05 | -0.0001622 | -4.065e-05 | 1.5236e-10 | -4.9124e-08 | 0.00024817 | 0.00024819 | 0.00024819 | 0.97245 | -0.19496 | 0.97245 | -0.19496 | 0.091921
20 | 0.00013186 | 3.2916e-05 | -0.00013186 | -3.3047e-05 | 2.6851e-10 | -1.308e-07 | 0.00020182 | 0.00020187 | 0.00020187 | 0.97197 | -0.19844 | 0.97197 | -0.19846 | 0.074765
21 | 0.0080604 | 0.0020152 | -0.0080536 | -0.0020135 | 6.7186e-06 | 1.7082e-06 | 0.012338 | 0.012338 | 0.012338 | 0.97197 | -0.19844 | 0.97114 | -0.20449 | 4.5697
22 | 0.0071704 | 0.0017934 | -0.0071703 | -0.0017934 | 1.2578e-07 | 2.771e-08 | 0.010985 | 0.010985 | 0.010985 | 0.97114 | -0.20449 | 0.97112 | -0.20462 | 4.0687
23 | 0.00088323 | 0.00022006 | -0.00088317 | -0.00022065 | 5.6625e-08 | -5.9155e-07 | 0.0013529 | 0.0013531 | 0.0013531 | 0.97114 | -0.20449 | 0.97107 | -0.20496 | 0.50114
24 | 0.0068002 | 0.0017006 | -0.0068 | -0.0017006 | 1.6404e-07 | 3.3127e-08 | 0.010418 | 0.010418 | 0.010418 | 0.97112 | -0.20462 | 0.97109 | -0.2048 | 3.8587
25 | 0.0007559 | 0.00018875 | -0.0007559 | -0.00018884 | 6.4783e-09 | -9.3274e-08 | 0.0011581 | 0.0011581 | 0.0011581 | 0.97107 | -0.20496 | 0.97106 | -0.20502 | 0.42892
26 | 0.012999 | 0.0032582 | -0.012995 | -0.0032568 | 4.2388e-06 | 1.3993e-06 | 0.01949 | 0.01949 | 0.01949 | 0.99245 | -0.052932 | 0.99211 | -0.055288 | 7.2185
27 | -0.012999 | -0.0032582 | 0.013011 | 0.0032621 | 1.2043e-05 | 3.9746e-06 | 0.01949 | 0.01949 | 0.01949 | 0.99245 | -0.052932 | 0.9934 | -0.046246 | 7.2184
28 | -0.018183 | -0.0045579 | 0.018207 | 0.0045663 | 2.351e-05 | 8.3841e-06 | 0.027237 | 0.027237 | 0.027237 | 0.9934 | -0.046246 | 0.99472 | -0.036921 | 10.0877
29 | 0.0051722 | 0.0012958 | -0.0051715 | -0.0012957 | 6.509e-07 | 2.5375e-08 | 0.0077473 | 0.0077474 | 0.0077474 | 0.9934 | -0.046246 | 0.99327 | -0.047156 | 2.8694
30 | -0.00032355 | -8.0793e-05 | 0.00032355 | 8.0662e-05 | 1.6236e-09 | -1.3038e-07 | 0.00049569 | 0.00049565 | 0.00049569 | 0.97105 | -0.20514 | 0.97105 | -0.2051 | 0.18359
31 | 0.0001763 | 4.3889e-05 | -0.0001763 | -4.4185e-05 | 1.0907e-09 | -2.9595e-07 | 0.00027005 | 0.00027016 | 0.00027016 | 0.97105 | -0.20514 | 0.97104 | -0.20519 | 0.10006
32 | -0.00048673 | -0.00012156 | 0.00048673 | 0.00012144 | 3.3221e-09 | -1.1717e-07 | 0.0007457 | 0.00074565 | 0.0007457 | 0.97105 | -0.2051 | 0.97106 | -0.20505 | 0.27618
33 | -0.0006193 | -0.00015467 | 0.0006193 | 0.00015461 | 2.5678e-09 | -5.5564e-08 | 0.00094879 | 0.00094877 | 0.00094879 | 0.97106 | -0.20505 | 0.97106 | -0.20502 | 0.3514
34 | -0.012455 | -0.0031171 | 0.012455 | 0.0031172 | 3.9493e-07 | 1.2997e-07 | 0.018991 | 0.018991 | 0.018991 | 0.97583 | -0.17056 | 0.97587 | -0.17033 | 7.0335
35 | 0.011611 | 0.0029055 | -0.011609 | -0.0029049 | 1.7588e-06 | 5.6412e-07 | 0.017703 | 0.017703 | 0.017703 | 0.97583 | -0.17056 | 0.97568 | -0.17165 | 6.5568
36 | 0.011107 | 0.0027791 | -0.011103 | -0.0027779 | 4.053e-06 | 1.2762e-06 | 0.016938 | 0.016938 | 0.016938 | 0.97568 | -0.17165 | 0.97531 | -0.1743 | 6.2733
37 | 0.010371 | 0.0025944 | -0.010371 | -0.0025943 | 5.0161e-07 | 1.5285e-07 | 0.015821 | 0.015821 | 0.015821 | 0.97531 | -0.1743 | 0.97527 | -0.17465 | 5.8597
38 | 0.010204 | 0.0025526 | -0.0102 | -0.0025513 | 4.2073e-06 | 1.2712e-06 | 0.015567 | 0.015568 | 0.015568 | 0.97527 | -0.17465 | 0.97485 | -0.17764 | 5.7658
39 | 0.0099448 | 0.0024874 | -0.009944 | -0.0024871 | 8.1305e-07 | 2.422e-07 | 0.015178 | 0.015178 | 0.015178 | 0.97485 | -0.17764 | 0.97477 | -0.17823 | 5.6215
40 | 0.0063922 | 0.0015984 | -0.006392 | -0.0015984 | 2.2441e-07 | 3.9925e-08 | 0.0097936 | 0.0097936 | 0.0097936 | 0.97109 | -0.2048 | 0.97106 | -0.20505 | 3.6273
41 | 0.0060219 | 0.0015056 | -0.0060206 | -0.0015054 | 1.2728e-06 | 1.9319e-07 | 0.0092264 | 0.0092266 | 0.0092266 | 0.97106 | -0.20505 | 0.97085 | -0.20659 | 3.4172
42 | 0.0224 | 0.005632 | -0.022396 | -0.0056308 | 3.4069e-06 | 1.2485e-06 | 0.033681 | 0.033681 | 0.033681 | 0.98981 | -0.071255 | 0.98965 | -0.072347 | 12.4745
43 | -0.025333 | -0.0063673 | 0.025342 | 0.0063699 | 8.1306e-06 | 2.6653e-06 | 0.038091 | 0.038091 | 0.038091 | 0.98981 | -0.071255 | 0.99014 | -0.06895 | 7.0539
44 | 0.018857 | 0.0047437 | -0.018847 | -0.0047402 | 9.7325e-06 | 3.4942e-06 | 0.028359 | 0.028359 | 0.028359 | 0.98965 | -0.072347 | 0.98913 | -0.076049 | 10.5033
45 | -0.025342 | -0.0063699 | 0.025371 | 0.0063796 | 2.9512e-05 | 9.6716e-06 | 0.038091 | 0.03809 | 0.038091 | 0.99014 | -0.06895 | 0.99133 | -0.060595 | 7.0539
46 | -0.032281 | -0.0081106 | 0.032289 | 0.0081135 | 8.2759e-06 | 2.8917e-06 | 0.048462 | 0.048462 | 0.048462 | 0.99133 | -0.060595 | 0.99159 | -0.058753 | 8.9744
47 | 0.0069096 | 0.001731 | -0.0069064 | -0.0017304 | 3.2507e-06 | 6.2617e-07 | 0.010371 | 0.010372 | 0.010372 | 0.99133 | -0.060595 | 0.99085 | -0.063997 | 3.8413
48 | -0.036775 | -0.0092377 | 0.036784 | 0.0092409 | 8.9329e-06 | 3.1932e-06 | 0.055193 | 0.055193 | 0.055193 | 0.99159 | -0.058753 | 0.99184 | -0.057007 | 10.2209
49 | 0.0016918 | 0.0004235 | -0.0016917 | -0.00042397 | 1.6562e-07 | -4.6586e-07 | 0.0025405 | 0.0025407 | 0.0025407 | 0.99085 | -0.063997 | 0.99075 | -0.064705 | 0.94101
50 | -0.040925 | -0.010279 | 0.040947 | 0.010287 | 2.255e-05 | 8.178e-06 | 0.061406 | 0.061406 | 0.061406 | 0.99184 | -0.057007 | 0.9924 | -0.053046 | 11.3715
51 | -0.0040573 | -0.0010159 | 0.0040576 | 0.0010159 | 3.4346e-07 | -5.5942e-08 | 0.0061166 | 0.0061165 | 0.0061166 | 0.98699 | -0.091258 | 0.98708 | -0.090645 | 2.2654
52 | 0.0027167 | 0.00067992 | -0.0027164 | -0.00068012 | 2.3404e-07 | -1.9574e-07 | 0.0040954 | 0.0040955 | 0.0040955 | 0.98699 | -0.091258 | 0.9869 | -0.091882 | 1.5168
53 | -0.00644 | -0.0016129 | 0.0064407 | 0.001613 | 6.7664e-07 | 1.1316e-07 | 0.0097079 | 0.0097078 | 0.0097079 | 0.98708 | -0.090645 | 0.98718 | -0.089885 | 3.5955
54 | 0.0027164 | 0.00068012 | -0.0027158 | -0.00068064 | 6.2692e-07 | -5.2402e-07 | 0.0040955 | 0.0040958 | 0.0040958 | 0.9869 | -0.091882 | 0.98667 | -0.093551 | 1.517
55 | -0.0075435 | -0.0018894 | 0.0075455 | 0.0018899 | 2.0684e-06 | 4.6763e-07 | 0.01137 | 0.01137 | 0.01137 | 0.98718 | -0.089885 | 0.98746 | -0.087903 | 4.2112
56 | 0.021774 | 0.0054574 | -0.021764 | -0.0054537 | 1.0019e-05 | 3.6629e-06 | 0.032811 | 0.032811 | 0.032811 | 0.98746 | -0.087903 | 0.98699 | -0.091228 | 12.1522
57 | -0.029319 | -0.0073473 | 0.029338 | 0.0073544 | 1.9113e-05 | 7.1502e-06 | 0.044181 | 0.044181 | 0.044181 | 0.98746 | -0.087903 | 0.98813 | -0.083196 | 16.3633
58 | 0.018152 | 0.0045487 | -0.018151 | -0.0045482 | 1.2853e-06 | 4.592e-07 | 0.027367 | 0.027367 | 0.027367 | 0.98699 | -0.091228 | 0.98692 | -0.091739 | 10.1358
59 | -0.036081 | -0.0090442 | 0.036129 | 0.0090627 | 4.8913e-05 | 1.8472e-05 | 0.054334 | 0.054334 | 0.054334 | 0.98813 | -0.083196 | 0.98951 | -0.07342 | 20.1238
60 | 0.0096558 | 0.0024191 | -0.0096536 | -0.0024185 | 2.1605e-06 | 6.2225e-07 | 0.014558 | 0.014558 | 0.014558 | 0.98692 | -0.091739 | 0.98669 | -0.093357 | 5.3919
61 | -0.037265 | -0.0093472 | 0.037279 | 0.0093525 | 1.4013e-05 | 5.2976e-06 | 0.056041 | 0.056041 | 0.056041 | 0.98951 | -0.07342 | 0.98989 | -0.070709 | 20.7561
62 | 0.0037191 | 0.00093185 | -0.0037186 | -0.00093198 | 4.6871e-07 | -1.2864e-07 | 0.0055905 | 0.0055906 | 0.0055906 | 0.98989 | -0.070709 | 0.98976 | -0.07162 | 2.0706
63 | -0.040998 | -0.010284 | 0.041008 | 0.010288 | 1.0349e-05 | 3.9244e-06 | 0.061632 | 0.061632 | 0.061632 | 0.98989 | -0.070709 | 0.99015 | -0.06889 | 22.8266
64 | -0.042841 | -0.010748 | 0.042973 | 0.010798 | 0.00013246 | 5.0287e-05 | 0.064386 | 0.064385 | 0.064386 | 0.99015 | -0.06889 | 0.99331 | -0.046668 | 23.8465
65 | -0.046381 | -0.011652 | 0.046447 | 0.011677 | 6.6045e-05 | 2.5118e-05 | 0.06949 | 0.06949 | 0.06949 | 0.99331 | -0.046668 | 0.99477 | -0.036446 | 25.7371
66 | 0.0089212 | 0.0022349 | -0.0089206 | -0.0022347 | 6.1185e-07 | 1.6614e-07 | 0.013454 | 0.013454 | 0.013454 | 0.98669 | -0.093357 | 0.98662 | -0.093853 | 4.9828
67 | 0.0050937 | 0.001276 | -0.0050927 | -0.001276 | 9.7699e-07 | 3.7024e-08 | 0.0076821 | 0.0076822 | 0.0076822 | 0.98662 | -0.093853 | 0.98643 | -0.095239 | 2.8453
68 | 0.0038269 | 0.00095875 | -0.0038261 | -0.00095892 | 7.4683e-07 | -1.715e-07 | 0.0057715 | 0.0057717 | 0.0057717 | 0.98662 | -0.093853 | 0.98643 | -0.095263 | 2.1377
69 | 0.0037871 | 0.00094874 | -0.0037869 | -0.0009488 | 2.4151e-07 | -5.8492e-08 | 0.0057127 | 0.0057128 | 0.0057128 | 0.98643 | -0.095239 | 0.98636 | -0.0957 | 2.1158
70 | 0.0037869 | 0.0009488 | -0.0037869 | -0.00094881 | 4.4934e-08 | -1.088e-08 | 0.0057128 | 0.0057128 | 0.0057128 | 0.98636 | -0.0957 | 0.98635 | -0.095786 | 2.1158
71 | 0.0017679 | 0.00044281 | -0.0017678 | -0.00044305 | 9.7078e-08 | -2.4182e-07 | 0.0026669 | 0.002667 | 0.002667 | 0.98635 | -0.095786 | 0.9863 | -0.096183 | 0.98779
72 | 0.0024914 | 0.00062431 | -0.0024914 | -0.00062434 | 2.4368e-08 | -2.7823e-08 | 0.0037093 | 0.0037093 | 0.0037093 | 0.99946 | -0.0037871 | 0.99945 | -0.0038577 | 1.3738
73 | -0.0039975 | -0.0010018 | 0.0039987 | 0.0010015 | 1.1182e-06 | -2.3314e-07 | 0.0059516 | 0.0059514 | 0.0059516 | 0.99946 | -0.0037871 | 0.99975 | -0.0017653 | 2.2043
74 | 0.0012861 | 0.00032227 | -0.0012861 | -0.00032233 | 1.2031e-08 | -6.4283e-08 | 0.0019148 | 0.0019148 | 0.0019148 | 0.99945 | -0.0038577 | 0.99944 | -0.0039253 | 0.7092
75 | -0.0067324 | -0.0016867 | 0.0067327 | 0.0016867 | 3.2245e-07 | 5.653e-08 | 0.01002 | 0.01002 | 0.01002 | 0.99975 | -0.0017653 | 0.9998 | -0.0014191 | 3.7112
76 | -0.0085493 | -0.002142 | 0.008551 | 0.0021425 | 1.6787e-06 | 4.277e-07 | 0.012724 | 0.012724 | 0.012724 | 0.9998 | -0.0014191 | 1 | 0 | 4.7126
77 | 0.11153 | 0.028102 | -0.11133 | -0.028024 | 0.00020383 | 7.7776e-05 | 0.16601 | 0.16601 | 0.16601 | 1 | 0 | 0.99812 | -0.013085 | 30.7429
78 | 0.055642 | 0.013987 | -0.055639 | -0.013986 | 2.6306e-06 | 1.0037e-06 | 0.08281 | 0.08281 | 0.08281 | 1 | 0 | 0.99995 | -0.00033948 | 30.6705
79 | 0.11133 | 0.028024 | -0.11098 | -0.027894 | 0.00034253 | 0.0001307 | 0.16601 | 0.16601 | 0.16601 | 0.99812 | -0.013085 | 0.99495 | -0.035184 | 30.743
80 | 0.05359 | 0.013472 | -0.053469 | -0.013427 | 0.00012026 | 4.5857e-05 | 0.079761 | 0.079761 | 0.079761 | 0.99995 | -0.00033948 | 0.99764 | -0.016487 | 29.541
81 | -0.0018706 | -0.00046873 | 0.0018706 | 0.00046852 | 9.4814e-08 | -2.1392e-07 | 0.0028025 | 0.0028024 | 0.0028025 | 0.99319 | -0.047705 | 0.99324 | -0.047339 | 1.038
82 | 0.00050646 | 0.00012686 | -0.00050646 | -0.00012693 | 2.0361e-09 | -7.2562e-08 | 0.00075876 | 0.00075878 | 0.00075878 | 0.99319 | -0.047705 | 0.99319 | -0.047734 | 0.28103
83 | -0.0030987 | -0.0007763 | 0.0030988 | 0.00077626 | 7.8314e-08 | -4.5257e-08 | 0.0046422 | 0.0046422 | 0.0046422 | 0.99324 | -0.047339 | 0.99327 | -0.047156 | 1.7193
84 | -0.043151 | -0.010822 | 0.043175 | 0.010832 | 2.4302e-05 | 9.2254e-06 | 0.064552 | 0.064552 | 0.064552 | 0.99472 | -0.036921 | 0.9953 | -0.032861 | 23.9083
85 | 0.024944 | 0.0062562 | -0.024927 | -0.0062497 | 1.7541e-05 | 6.4845e-06 | 0.037316 | 0.037316 | 0.037316 | 0.99472 | -0.036921 | 0.994 | -0.041996 | 13.8207
86 | 0.015573 | 0.0039041 | -0.015567 | -0.0039019 | 6.1327e-06 | 2.125e-06 | 0.023328 | 0.023328 | 0.023328 | 0.99337 | -0.046465 | 0.99296 | -0.049309 | 8.64
87 | -0.017154 | -0.0043002 | 0.017155 | 0.0043006 | 1.2952e-06 | 4.5745e-07 | 0.025696 | 0.025696 | 0.025696 | 0.99337 | -0.046465 | 0.99344 | -0.04592 | 9.5169
88 | 0.012868 | 0.0032256 | -0.012862 | -0.0032236 | 5.9592e-06 | 1.96e-06 | 0.019284 | 0.019284 | 0.019284 | 0.99296 | -0.049309 | 0.99249 | -0.052654 | 7.1422
89 | -0.02295 | -0.005753 | 0.022963 | 0.0057576 | 1.2477e-05 | 4.5795e-06 | 0.034376 | 0.034376 | 0.034376 | 0.99344 | -0.04592 | 0.994 | -0.041996 | 12.732
90 | 0.0057955 | 0.0014524 | -0.0057947 | -0.0014523 | 8.5763e-07 | 9.3739e-08 | 0.0086807 | 0.0086808 | 0.0086808 | 0.99344 | -0.04592 | 0.99329 | -0.046989 | 3.2151
91 | 0.010939 | 0.0027417 | -0.010935 | -0.0027403 | 4.3436e-06 | 1.3363e-06 | 0.016401 | 0.016401 | 0.016401 | 0.99249 | -0.052654 | 0.99208 | -0.055523 | 6.0745
92 | 0.0065999 | 0.0016539 | -0.0065989 | -0.0016537 | 1.0274e-06 | 1.7824e-07 | 0.0098991 | 0.0098992 | 0.0098992 | 0.99208 | -0.055523 | 0.99192 | -0.056648 | 3.6664
93 | 0.0065989 | 0.0016537 | -0.0065983 | -0.0016536 | 5.5531e-07 | 9.6368e-08 | 0.0098992 | 0.0098992 | 0.0098992 | 0.99192 | -0.056648 | 0.99184 | -0.057256 | 3.6664
94 | -0.05057 | -0.012685 | 0.050685 | 0.012729 | 0.0001151 | 4.3847e-05 | 0.075608 | 0.075608 | 0.075608 | 0.9953 | -0.032861 | 0.99764 | -0.016487 | 28.0031
95 | 0.0073952 | 0.0018532 | -0.0073937 | -0.0018529 | 1.4278e-06 | 3.0593e-07 | 0.011056 | 0.011056 | 0.011056 | 0.9953 | -0.032861 | 0.9951 | -0.034256 | 4.0949
96 | 0.002832 | 0.00070968 | -0.0028319 | -0.00070974 | 7.6703e-08 | -5.838e-08 | 0.0042487 | 0.0042487 | 0.0042487 | 0.99184 | -0.057256 | 0.99181 | -0.057451 | 1.5736
97 | 0.10774 | 0.027081 | -0.10772 | -0.027074 | 1.892e-05 | 7.2161e-06 | 0.16116 | 0.16116 | 0.16116 | 0.99495 | -0.035184 | 0.99477 | -0.036446 | 29.8449
98 | 0.0051088 | 0.0012802 | -0.0051087 | -0.0012802 | 1.0177e-07 | 2.8378e-09 | 0.0076393 | 0.0076393 | 0.0076393 | 0.9951 | -0.034256 | 0.99508 | -0.0344 | 2.8294
99 | 0.0034066 | 0.00085365 | -0.0034064 | -0.00085372 | 1.7109e-07 | -7.1445e-08 | 0.0050941 | 0.0050941 | 0.0050941 | 0.99508 | -0.0344 | 0.99503 | -0.034763 | 1.8867
100 | 0.0053956 | 0.0013487 | -0.0053955 | -0.0013487 | 7.5991e-08 | 7.2018e-09 | 0.0082685 | 0.0082685 | 0.0082685 | 0.97085 | -0.20659 | 0.97083 | -0.20669 | 3.0624
101 | 0.0049738 | 0.0012431 | -0.0049738 | -0.0012431 | 4.6022e-08 | 2.0039e-09 | 0.0076222 | 0.0076222 | 0.0076222 | 0.97083 | -0.20669 | 0.97082 | -0.20675 | 2.823
102 | 0.0043486 | 0.0010864 | -0.0043481 | -0.0010864 | 5.233e-07 | -3.2199e-08 | 0.006664 | 0.0066641 | 0.0066641 | 0.97082 | -0.20675 | 0.9707 | -0.20763 | 2.4682
103 | 0.0042205 | 0.0010544 | -0.0042204 | -0.0010544 | 1.2988e-07 | -1.1539e-08 | 0.0064685 | 0.0064685 | 0.0064685 | 0.9707 | -0.20763 | 0.97067 | -0.20785 | 2.3957
104 | 0.0033288 | 0.000831 | -0.0033287 | -0.00083105 | 1.3859e-07 | -5.2166e-08 | 0.0051018 | 0.0051019 | 0.0051019 | 0.97067 | -0.20785 | 0.97063 | -0.20816 | 1.8896
105 | 0.0031401 | 0.00078379 | -0.0031395 | -0.00078407 | 5.905e-07 | -2.7773e-07 | 0.0048128 | 0.004813 | 0.004813 | 0.97063 | -0.20816 | 0.97044 | -0.20953 | 1.7826
106 | 0.0024791 | 0.00062025 | -0.0024791 | -0.00062026 | 4.502e-09 | -4.4388e-09 | 0.0038009 | 0.0038009 | 0.0038009 | 0.97044 | -0.20953 | 0.97044 | -0.20954 | 1.4077
107 | 0.00029854 | 7.3112e-05 | -0.00029852 | -7.4816e-05 | 1.808e-08 | -1.7036e-06 | 0.00045715 | 0.00045776 | 0.00045776 | 0.97044 | -0.20953 | 0.97038 | -0.20997 | 0.16954
108 | 0.0021171 | 0.00052954 | -0.002117 | -0.00052967 | 8.3047e-08 | -1.2412e-07 | 0.0032459 | 0.0032459 | 0.0032459 | 0.97044 | -0.20954 | 0.9704 | -0.20982 | 1.2022
109 | 0.0019717 | 0.00049323 | -0.0019712 | -0.00049403 | 4.4851e-07 | -7.9884e-07 | 0.003023 | 0.0030234 | 0.0030234 | 0.9704 | -0.20982 | 0.97017 | -0.21147 | 1.1198
110 | 0.061275 | 0.015397 | -0.061228 | -0.015379 | 4.7419e-05 | 1.7769e-05 | 0.091673 | 0.091673 | 0.091673 | 0.99477 | -0.036446 | 0.99397 | -0.042011 | 16.9764
111 | 0.054333 | 0.013651 | -0.054276 | -0.01363 | 5.6423e-05 | 2.0994e-05 | 0.08135 | 0.081351 | 0.081351 | 0.99397 | -0.042011 | 0.99291 | -0.049483 | 15.0649
112 | 0.0068952 | 0.001728 | -0.0068935 | -0.0017276 | 1.7061e-06 | 3.2368e-07 | 0.010322 | 0.010322 | 0.010322 | 0.99397 | -0.042011 | 0.99372 | -0.043799 | 3.8231
113 | 0.050403 | 0.012659 | -0.050403 | -0.012659 | 7.3615e-08 | 2.7245e-08 | 0.075546 | 0.075546 | 0.075546 | 0.99291 | -0.049483 | 0.99291 | -0.049494 | 13.9899
114 | 0.0060286 | 0.0015109 | -0.0060283 | -0.0015108 | 2.974e-07 | 3.8622e-08 | 0.0090273 | 0.0090274 | 0.0090274 | 0.99372 | -0.043799 | 0.99367 | -0.044155 | 3.3435
115 | 0.043555 | 0.010943 | -0.043544 | -0.010939 | 1.0767e-05 | 3.9318e-06 | 0.065283 | 0.065284 | 0.065284 | 0.99291 | -0.049494 | 0.99265 | -0.051271 | 12.0895
116 | 0.042552 | 0.01069 | -0.042542 | -0.010687 | 1.0503e-05 | 3.8258e-06 | 0.063796 | 0.063796 | 0.063796 | 0.99265 | -0.051271 | 0.9924 | -0.053046 | 11.8142

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17652 | 0.044232

## res_load
| p_mw | q_mvar
0 | 0.00080432 | 0.00020158
1 | 0.0021133 | 0.00052963
2 | 0.00071718 | 0.00017974
3 | 0.0002021 | 5.0652e-05
4 | 0.00026713 | 6.6949e-05
5 | 0.00013629 | 3.4159e-05
6 | 0.00037877 | 9.4929e-05
7 | 0.00078697 | 0.00019723
8 | 0.00024206 | 6.0665e-05
9 | 0.00047597 | 0.00011929
10 | 0.00020637 | 5.1722e-05
11 | 0.00016051 | 4.0227e-05
12 | 0.00015818 | 3.9643e-05
13 | 0.0001622 | 4.065e-05
14 | 0.00013186 | 3.3047e-05
15 | 0.00037009 | 9.2754e-05
16 | 0.00012727 | 3.1896e-05
17 | 0.012995 | 0.0032568
18 | 0.00014725 | 3.6904e-05
19 | 0.00016318 | 4.0896e-05
20 | 0.0001763 | 4.4185e-05
21 | 0.00013257 | 3.3224e-05
22 | 0.0001366 | 3.4235e-05
23 | 0.0008442 | 0.00021158
24 | 0.00058807 | 0.00014738
25 | 0.00050197 | 0.00012581
26 | 0.00073191 | 0.00018343
27 | 0.00016627 | 4.1672e-05
28 | 0.00025524 | 6.397e-05
29 | 0.00019196 | 4.811e-05
30 | 0.00040778 | 0.0001022
31 | 0.00037011 | 9.2758e-05
32 | 0.0029336 | 0.00073522
33 | 0.0035397 | 0.00088714
34 | 0.00031631 | 7.9274e-05
35 | 0.0044857 | 0.0011242
36 | 0.0052146 | 0.0013069
37 | 0.0041413 | 0.0010379
38 | 0.0016917 | 0.00042397
39 | 0.0013406 | 0.00033599
40 | 0.0023823 | 0.00059707
41 | 0.0011028 | 0.00027639
42 | 0.0027158 | 0.00068064
43 | 0.0036112 | 0.00090505
44 | 0.0067424 | 0.0016898
45 | 0.0084952 | 0.0021291
46 | 0.0011354 | 0.00028456
47 | 0.0037186 | 0.00093198
48 | 0.0018323 | 0.00045922
49 | 0.0034078 | 0.00085407
50 | 0.00073243 | 0.00018356
51 | 0.0013056 | 0.00032722
52 | 0.0038261 | 0.00095892
53 | 0.002019 | 0.000506
54 | 0.0015061 | 0.00037747
55 | 0.0012053 | 0.00030207
56 | 0.0027338 | 0.00068514
57 | 0.0012861 | 0.00032233
58 | 0.0018166 | 0.00045528
59 | 0.0020494 | 0.00051362
60 | 0.0017678 | 0.00044305
61 | 0.0013641 | 0.00034187
62 | 0.0012281 | 0.00030778
63 | 0.00050646 | 0.00012693
64 | 0.0020727 | 0.00051948
65 | 0.0015806 | 0.00039613
66 | 0.0026987 | 0.00067637
67 | 0.0019229 | 0.00048193
68 | 0.0019636 | 0.00049214
69 | 0.0057947 | 0.0014523
70 | 0.0043349 | 0.0010864
71 | 0.0037664 | 0.00094394
72 | 0.0032425 | 0.00081264
73 | 0.0028319 | 0.00070974
74 | 0.0027841 | 0.00069775
75 | 0.002285 | 0.00057266
76 | 0.0017021 | 0.00042659
77 | 0.0034064 | 0.00085372
78 | 0.00062505 | 0.00015665
79 | 0.00042168 | 0.00010568
80 | 0.00062517 | 0.00015668
81 | 0.0001276 | 3.1979e-05
82 | 0.00089153 | 0.00022344
83 | 0.00018856 | 4.7258e-05
84 | 0.00036193 | 9.0708e-05
85 | 0.00036195 | 9.0713e-05
86 | 0.00029852 | 7.4816e-05
87 | 0.00014538 | 3.6436e-05
88 | 0.0019712 | 0.00049403
89 | 0.0038735 | 0.0009708
90 | 0.00086489 | 0.00021676
91 | 0.0068476 | 0.0017162
92 | 0.0060283 | 0.0015108
93 | 0.0009921 | 0.00024864
94 | 0.0015944 | 0.0003996

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1