## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2054-17_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2054-17_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2054-17_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2054-17_0_3_node_29 | 0.4 | n |  | TRUE
4 | bus_LV_2054-17_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2054-17_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2054-17_0_3_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_2054-17_0_3_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_2054-17_0_3_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_2054-17_0_3_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_2054-17_0_3_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_2054-17_0_3_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_2054-17_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2054-17_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2054-17_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2054-17_0_3_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_2054-17_0_3_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_2054-17_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2054-17_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2054-17_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2054-17_0_3_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_2054-17_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2054-17_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_2054-17_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_2054-17_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2054-17_0_3_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_2054-17_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_2054-17_0_3_node_24 | 0.4 | n |  | TRUE
28 | bus_MV_454_1_node_95 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2054-17_0_3_load_0 | 0 | 0.0035891 | 0.00089952 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2054-17_0_3_load_29 | 3 | 0.0087503 | 0.002193 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2054-17_0_3_load_30 | 6 | 0.0087473 | 0.0021923 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2054-17_0_3_load_12 | 11 | 0.0039465 | 0.00098908 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2054-17_0_3_load_7 | 12 | 0.002297 | 0.00057568 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2054-17_0_3_load_8 | 13 | 0.0024914 | 0.0006244 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2054-17_0_3_load_9 | 14 | 0.0061136 | 0.0015322 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2054-17_0_3_load_23 | 15 | 0.0017411 | 0.00043637 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2054-17_0_3_load_22 | 16 | 0.0022405 | 0.00056153 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2054-17_0_3_load_15 | 17 | 0.02643 | 0.0066241 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2054-17_0_3_load_13 | 18 | 0.018161 | 0.0045516 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2054-17_0_3_load_11 | 19 | 0.0089548 | 0.0022443 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2054-17_0_3_load_28 | 20 | 0.0076956 | 0.0019287 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2054-17_0_3_load_18 | 21 | 0.005091 | 0.0012759 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2054-17_0_3_load_16 | 22 | 0.0022582 | 0.00056596 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2054-17_0_3_load_17 | 23 | 0.0080842 | 0.0020261 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2054-17_0_3_load_19 | 24 | 0.0027182 | 0.00068125 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2054-17_0_3_load_21 | 25 | 0.0014904 | 0.00037354 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2054-17_0_3_load_27 | 26 | 0.0057182 | 0.0014331 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2054-17_0_3_load_24 | 27 | 0.037716 | 0.0094526 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2054-17_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2054-17_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.1991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2054-17_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.052182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2054-17_0_3_line_3 | NAYY 4x150 SE | 3 | 5 | 0.0078353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2054-17_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.02786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_2054-17_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.083808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_2054-17_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.010371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_2054-17_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.05252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_2054-17_0_3_line_8 | NAYY 4x150 SE | 7 | 10 | 0.029875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2054-17_0_3_line_9 | NAYY 4x150 SE | 7 | 11 | 0.024633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_2054-17_0_3_line_10 | NAYY 4x150 SE | 8 | 9 | 0.1994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_2054-17_0_3_line_11 | NAYY 4x150 SE | 9 | 27 | 0.27004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2054-17_0_3_line_12 | NAYY 4x150 SE | 10 | 20 | 0.014724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2054-17_0_3_line_13 | NAYY 4x150 SE | 10 | 21 | 0.0046643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2054-17_0_3_line_14 | NAYY 4x150 SE | 11 | 19 | 0.014239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_2054-17_0_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.0093362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2054-17_0_3_line_16 | NAYY 4x150 SE | 13 | 14 | 0.0051817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2054-17_0_3_line_17 | NAYY 4x150 SE | 14 | 15 | 0.0026991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2054-17_0_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.0022543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2054-17_0_3_line_19 | NAYY 4x150 SE | 16 | 25 | 0.00020918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2054-17_0_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.038725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2054-17_0_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.018762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2054-17_0_3_line_22 | NAYY 4x150 SE | 20 | 26 | 0.0018977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2054-17_0_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.021769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2054-17_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.0066275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2054-17_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.0021032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2054-17_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.008998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2054-17_0_3_trafo_11 | 0.25 MVA 20/0.4 kV | 28 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2554751.512 | 1188800.9641 | 2554746.5664 | 1188795.5208 | 2554736.7693 | 1188805.4369
1 | 2554779.5713 | 1188844.0531 | 2554795.6612 | 1188826.4438 | 2554810.9857 | 1188813.5208 | 2554827.7505 | 1188803.4329 | 2554835.1141 | 1188796.8069 | 2554830.2798 | 1188787.9275 | 2554795.0109 | 1188752.6527 | 2554764.5106 | 1188786.0797 | 2554757.6391 | 1188792.2129 | 2554757.3657 | 1188795.3945 | 2554751.512 | 1188800.9641
2 | 2554779.5713 | 1188844.0531 | 2554755.4663 | 1188874.8747 | 2554745.2345 | 1188882.9817
3 | 2554739.0436 | 1188887.784 | 2554744.2605 | 1188883.7534 | 2554745.2345 | 1188882.9817
4 | 2554739.0436 | 1188887.784 | 2554746.4593 | 1188900.1346 | 2554742.1486 | 1188909.0166 | 2554742.0537 | 1188912.5971
5 | 2554742.0537 | 1188912.5971 | 2554736.7677 | 1188914.5493 | 2554731.8899 | 1188917.0432 | 2554720.3593 | 1188927.314 | 2554718.2254 | 1188930.5653 | 2554714.0962 | 1188938.223 | 2554710.0897 | 1188941.9443 | 2554677.3748 | 1188963.5324
6 | 2554739.0436 | 1188887.784 | 2554731.0933 | 1188894.4702
7 | 2554634.3253 | 1188993.6143 | 2554674.0945 | 1188965.6971 | 2554677.3748 | 1188963.5324
8 | 2554731.0933 | 1188894.4702 | 2554726.2393 | 1188887.014 | 2554715.2349 | 1188869.132
9 | 2554731.0933 | 1188894.4702 | 2554726.068 | 1188897.6211 | 2554719.0737 | 1188901.6207 | 2554709.9867 | 1188907.1638
10 | 2554634.3253 | 1188993.6143 | 2554604.0788 | 1189013.9997 | 2554576.2831 | 1189033.6885 | 2554546.3856 | 1189066.8119 | 2554540.9647 | 1189073.0677 | 2554491.4311 | 1189041.5165 | 2554485.8601 | 1189038.0904 | 2554483.6925 | 1189033.8935 | 2554482.5013 | 1189027.7102
11 | 2554482.5013 | 1189027.7102 | 2554486.5583 | 1189024.6332 | 2554617.5096 | 1188958.7562 | 2554682.9336 | 1188926.4195 | 2554707.2296 | 1188913.8061 | 2554722.2275 | 1188905.1321 | 2554722.7957 | 1188904.7564
12 | 2554715.2349 | 1188869.132 | 2554709.4976 | 1188871.9437 | 2554701.8958 | 1188875.3604
13 | 2554715.2349 | 1188869.132 | 2554712.8975 | 1188865.0955
14 | 2554697.4063 | 1188913.8044 | 2554705.8787 | 1188909.6696 | 2554709.9867 | 1188907.1638
15 | 2554683.243 | 1188813.8834 | 2554687.9214 | 1188821.9628
16 | 2554690.518 | 1188826.4469 | 2554687.9214 | 1188821.9628
17 | 2554691.8705 | 1188828.7827 | 2554690.518 | 1188826.4469
18 | 2554691.8705 | 1188828.7827 | 2554693.0001 | 1188830.7335
19 | 2554693.0001 | 1188830.7335 | 2554693.1049 | 1188830.9146
20 | 2554680.5448 | 1188922.0333 | 2554652.5184 | 1188935.711 | 2554645.8266 | 1188939.1836
21 | 2554680.5448 | 1188922.0333 | 2554697.4063 | 1188913.8044
22 | 2554701.8958 | 1188875.3604 | 2554700.165 | 1188876.1383
23 | 2554712.8975 | 1188865.0955 | 2554701.9889 | 1188846.2567
24 | 2554701.9889 | 1188846.2567 | 2554698.6678 | 1188840.5213
25 | 2554697.6139 | 1188838.7013 | 2554698.6678 | 1188840.5213
26 | 2554697.6139 | 1188838.7013 | 2554693.1049 | 1188830.9146

## bus_geodata
| x | y | coords
0 | 2554736.7693 | 1188805.4369
1 | 2554751.512 | 1188800.9641
2 | 2554779.5713 | 1188844.0531
3 | 2554745.2345 | 1188882.9817
4 | 2554742.0538 | 1188912.5971
5 | 2554739.0436 | 1188887.784
6 | 2554677.3748 | 1188963.5324
7 | 2554731.0933 | 1188894.4702
8 | 2554634.3253 | 1188993.6143
9 | 2554482.5013 | 1189027.7102
10 | 2554715.2349 | 1188869.132
11 | 2554709.9867 | 1188907.1638
12 | 2554683.243 | 1188813.8834
13 | 2554687.9214 | 1188821.9628
14 | 2554690.518 | 1188826.4469
15 | 2554691.8705 | 1188828.7827
16 | 2554693.0001 | 1188830.7335
17 | 2554645.8266 | 1188939.1836
18 | 2554680.5448 | 1188922.0333
19 | 2554697.4063 | 1188913.8044
20 | 2554701.8958 | 1188875.3604
21 | 2554712.8975 | 1188865.0955
22 | 2554701.9889 | 1188846.2567
23 | 2554698.6678 | 1188840.5213
24 | 2554697.6139 | 1188838.7013
25 | 2554693.1049 | 1188830.9146
26 | 2554700.165 | 1188876.1383
27 | 2554722.7957 | 1188904.7564
28 | 2554697.4063 | 1188913.8044

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99498 | -0.035006 | 0.0035891 | 0.00089952
1 | 0.99509 | -0.034235 | 0 | 0
2 | 0.99611 | -0.027017 | 0 | 0
3 | 0.99638 | -0.025121 | 0.0087503 | 0.002193
4 | 0.99557 | -0.030671 | 0 | 0
5 | 0.99652 | -0.024147 | 0 | 0
6 | 0.99272 | -0.050367 | 0.0087473 | 0.0021923
7 | 0.99696 | -0.021077 | 0 | 0
8 | 0.99127 | -0.06043 | 0 | 0
9 | 0.98575 | -0.098881 | 0 | 0
10 | 0.99491 | -0.035491 | 0 | 0
11 | 0.99886 | -0.0078842 | 0.0039465 | 0.00098908
12 | 0.99307 | -0.048389 | 0.002297 | 0.00057568
13 | 0.9931 | -0.048172 | 0.0024914 | 0.0006244
14 | 0.99314 | -0.047921 | 0.0061136 | 0.0015322
15 | 0.99318 | -0.047623 | 0.0017411 | 0.00043637
16 | 0.99322 | -0.047335 | 0.0022405 | 0.00056153
17 | 0.99734 | -0.018616 | 0.02643 | 0.0066241
18 | 0.99881 | -0.0083608 | 0.018161 | 0.0045516
19 | 1 | 0 | -0.15767 | -0.03951
20 | 0.99462 | -0.037483 | 0.0076956 | 0.0019287
21 | 0.99467 | -0.037115 | 0.005091 | 0.0012759
22 | 0.99376 | -0.043586 | 0.0022582 | 0.00056596
23 | 0.9935 | -0.045407 | 0.0080842 | 0.0020261
24 | 0.99344 | -0.045813 | 0.0027182 | 0.00068125
25 | 0.99323 | -0.047303 | 0.0014904 | 0.00037354
26 | 0.99461 | -0.037592 | 0.0057182 | 0.0014331
27 | 0.97079 | -0.20514 | 0.037716 | 0.0094526
28 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0035891 | -0.00089952 | 0.0035895 | 0.00089939 | 3.8283e-07 | -1.2935e-07 | 0.0053677 | 0.0053676 | 0.0053677 | 0.99498 | -0.035006 | 0.99509 | -0.034235 | 1.988
1 | -0.0035895 | -0.00089939 | 0.0035931 | 0.00089818 | 3.5788e-06 | -1.2126e-06 | 0.0053676 | 0.0053667 | 0.0053676 | 0.99509 | -0.034235 | 0.99611 | -0.027017 | 1.988
2 | -0.0035931 | -0.00089818 | 0.003594 | 0.00089786 | 9.3777e-07 | -3.1878e-07 | 0.0053667 | 0.0053664 | 0.0053667 | 0.99611 | -0.027017 | 0.99638 | -0.025121 | 1.9876
3 | -0.012344 | -0.0030909 | 0.012346 | 0.0030914 | 1.6615e-06 | 5.3696e-07 | 0.018434 | 0.018434 | 0.018434 | 0.99638 | -0.025121 | 0.99652 | -0.024147 | 6.8275
4 | -0.047421 | -0.012001 | 0.047464 | 0.012017 | 4.3717e-05 | 1.6089e-05 | 0.070918 | 0.070918 | 0.070918 | 0.99557 | -0.030671 | 0.99652 | -0.024147 | 13.133
5 | 0.047421 | 0.012001 | -0.047289 | -0.011953 | 0.00013151 | 4.8407e-05 | 0.070918 | 0.070919 | 0.070919 | 0.99557 | -0.030671 | 0.99272 | -0.050367 | 13.1331
6 | -0.05981 | -0.015109 | 0.059836 | 0.015118 | 2.5833e-05 | 9.6656e-06 | 0.089352 | 0.089352 | 0.089352 | 0.99652 | -0.024147 | 0.99696 | -0.021077 | 16.5467
7 | 0.038542 | 0.0097603 | -0.038487 | -0.0097406 | 5.4758e-05 | 1.9705e-05 | 0.057807 | 0.057808 | 0.057808 | 0.99272 | -0.050367 | 0.99127 | -0.06043 | 10.7051
8 | 0.048086 | 0.01207 | -0.04799 | -0.012033 | 9.6044e-05 | 3.6551e-05 | 0.071778 | 0.071778 | 0.071778 | 0.99696 | -0.021077 | 0.99491 | -0.035491 | 26.5843
9 | -0.10792 | -0.027188 | 0.10812 | 0.027264 | 0.00019953 | 7.61e-05 | 0.16113 | 0.16113 | 0.16113 | 0.99696 | -0.021077 | 0.99886 | -0.0078842 | 29.8388
10 | 0.038487 | 0.0097406 | -0.038279 | -0.0096658 | 0.0002079 | 7.485e-05 | 0.057808 | 0.05781 | 0.05781 | 0.99127 | -0.06043 | 0.98575 | -0.098881 | 10.7055
11 | 0.038279 | 0.0096658 | -0.037716 | -0.0094526 | 0.00056315 | 0.00021321 | 0.05781 | 0.057811 | 0.057811 | 0.98575 | -0.098881 | 0.97079 | -0.20514 | 21.4114
12 | 0.013418 | 0.0033631 | -0.013414 | -0.0033618 | 3.7e-06 | 1.2319e-06 | 0.020068 | 0.020068 | 0.020068 | 0.99491 | -0.035491 | 0.99462 | -0.037483 | 7.4326
13 | 0.034572 | 0.0086701 | -0.034565 | -0.0086672 | 7.7825e-06 | 2.9327e-06 | 0.05171 | 0.05171 | 0.05171 | 0.99491 | -0.035491 | 0.99467 | -0.037115 | 19.1517
14 | -0.11207 | -0.028253 | 0.11219 | 0.0283 | 0.00012391 | 4.7286e-05 | 0.16701 | 0.16701 | 0.16701 | 0.99886 | -0.0078842 | 1 | 0 | 30.9274
15 | -0.002297 | -0.00057568 | 0.002297 | 0.00057558 | 6.901e-08 | -9.4255e-08 | 0.0034418 | 0.0034417 | 0.0034418 | 0.99307 | -0.048389 | 0.9931 | -0.048172 | 1.2747
16 | -0.0047884 | -0.0012 | 0.0047886 | 0.0012 | 1.6644e-07 | -3.0326e-09 | 0.0071747 | 0.0071747 | 0.0071747 | 0.9931 | -0.048172 | 0.99314 | -0.047921 | 2.6573
17 | -0.010902 | -0.0027322 | 0.010903 | 0.0027323 | 4.4939e-07 | 1.3791e-07 | 0.016335 | 0.016335 | 0.016335 | 0.99314 | -0.047921 | 0.99318 | -0.047623 | 6.0498
18 | -0.012644 | -0.0031687 | 0.012644 | 0.0031689 | 5.0477e-07 | 1.6497e-07 | 0.018943 | 0.018943 | 0.018943 | 0.99318 | -0.047623 | 0.99322 | -0.047335 | 7.016
19 | -0.014885 | -0.0037304 | 0.014885 | 0.0037304 | 6.4911e-08 | 2.2258e-08 | 0.0223 | 0.0223 | 0.0223 | 0.99322 | -0.047335 | 0.99323 | -0.047303 | 8.2592
20 | -0.02643 | -0.0066241 | 0.026468 | 0.006638 | 3.7576e-05 | 1.3946e-05 | 0.039434 | 0.039434 | 0.039434 | 0.99734 | -0.018616 | 0.99881 | -0.0083608 | 14.6051
21 | -0.044629 | -0.01119 | 0.044681 | 0.011209 | 5.1758e-05 | 1.9661e-05 | 0.06649 | 0.06649 | 0.06649 | 0.99881 | -0.0083608 | 1 | 0 | 24.6258
22 | 0.0057183 | 0.0014331 | -0.0057182 | -0.0014331 | 8.6664e-08 | 8.7038e-09 | 0.008555 | 0.008555 | 0.008555 | 0.99462 | -0.037483 | 0.99461 | -0.037592 | 3.1685
23 | 0.029474 | 0.0073912 | -0.029447 | -0.0073814 | 2.6411e-05 | 9.8757e-06 | 0.044094 | 0.044094 | 0.044094 | 0.99467 | -0.037115 | 0.99376 | -0.043586 | 16.331
24 | 0.027189 | 0.0068154 | -0.027182 | -0.0068129 | 6.8547e-06 | 2.5506e-06 | 0.040712 | 0.040712 | 0.040712 | 0.99376 | -0.043586 | 0.9935 | -0.045407 | 15.0787
25 | 0.019098 | 0.0047868 | -0.019097 | -0.0047864 | 1.0738e-06 | 3.8576e-07 | 0.028604 | 0.028604 | 0.028604 | 0.9935 | -0.045407 | 0.99344 | -0.045813 | 10.5941
26 | 0.016379 | 0.0041051 | -0.016375 | -0.0041039 | 3.3793e-06 | 1.1832e-06 | 0.024533 | 0.024533 | 0.024533 | 0.99344 | -0.045813 | 0.99323 | -0.047303 | 9.0862

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16663 | 0.041754

## res_load
| p_mw | q_mvar
0 | 0.0035891 | 0.00089952
1 | 0.0087503 | 0.002193
2 | 0.0087473 | 0.0021923
3 | 0.0039465 | 0.00098908
4 | 0.002297 | 0.00057568
5 | 0.0024914 | 0.0006244
6 | 0.0061136 | 0.0015322
7 | 0.0017411 | 0.00043637
8 | 0.0022405 | 0.00056153
9 | 0.02643 | 0.0066241
10 | 0.018161 | 0.0045516
11 | 0.0089548 | 0.0022443
12 | 0.0076956 | 0.0019287
13 | 0.005091 | 0.0012759
14 | 0.0022582 | 0.00056596
15 | 0.0080842 | 0.0020261
16 | 0.0027182 | 0.00068125
17 | 0.0014904 | 0.00037354
18 | 0.0057182 | 0.0014331
19 | 0.037716 | 0.0094526

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1