## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2054-26_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2054-26_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2054-26_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2054-26_0_3_node_17 | 0.4 | n |  | TRUE
4 | bus_LV_2054-26_0_3_node_15 | 0.4 | n |  | TRUE
5 | bus_LV_2054-26_0_3_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_2054-26_0_3_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_2054-26_0_3_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_2054-26_0_3_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_2054-26_0_3_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_2054-26_0_3_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_2054-26_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2054-26_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2054-26_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2054-26_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2054-26_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2054-26_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2054-26_0_3_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_2054-26_0_3_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_2054-26_0_3_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_2054-26_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_2054-26_0_3_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_2054-26_0_3_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_2054-26_0_3_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2054-26_0_3_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_2054-26_0_3_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_2054-26_0_3_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_2054-26_0_3_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2054-26_0_3_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_2054-26_0_3_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_2054-26_0_3_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_2054-26_0_3_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_2054-26_0_3_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_2054-26_0_3_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_2054-26_0_3_node_34 | 0.4 | n |  | TRUE
35 | bus_MV_454_1_node_115 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2054-26_0_3_load_0 | 0 | 0.0088782 | 0.0022251 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2054-26_0_3_load_1 | 1 | 0.0019808 | 0.00049645 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2054-26_0_3_load_17 | 3 | 0.0115 | 0.0028822 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2054-26_0_3_load_18 | 5 | 0.0046617 | 0.0011683 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2054-26_0_3_load_16 | 7 | 0.0045337 | 0.0011362 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2054-26_0_3_load_14 | 8 | 0.0072984 | 0.0018292 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2054-26_0_3_load_3 | 9 | 0.0082108 | 0.0020578 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2054-26_0_3_load_4 | 10 | 0.0040211 | 0.0010078 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2054-26_0_3_load_6 | 11 | 0.010086 | 0.0025277 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2054-26_0_3_load_7 | 12 | 0.0039226 | 0.0009831 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2054-26_0_3_load_8 | 13 | 0.004276 | 0.0010717 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2054-26_0_3_load_27 | 17 | 0.0052696 | 0.0013207 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2054-26_0_3_load_26 | 18 | 0.0072523 | 0.0018176 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2054-26_0_3_load_19 | 20 | 0.012171 | 0.0030502 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2054-26_0_3_load_24 | 22 | 0.0095021 | 0.0023815 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2054-26_0_3_load_28 | 23 | 0.0049936 | 0.0012515 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2054-26_0_3_load_13 | 24 | 0.0046536 | 0.0011663 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2054-26_0_3_load_20 | 25 | 0.003305 | 0.00082831 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2054-26_0_3_load_23 | 27 | 0.012357 | 0.0030971 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2054-26_0_3_load_25 | 28 | 0.0028793 | 0.00072163 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2054-26_0_3_load_32 | 29 | 0.022233 | 0.0055721 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2054-26_0_3_load_33 | 32 | 0.02757 | 0.0069097 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2054-26_0_3_load_36 | 33 | 0.010191 | 0.002554 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2054-26_0_3_load_34 | 34 | 0.016828 | 0.0042176 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2054-26_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.00064306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2054-26_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.010576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2054-26_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.003109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2054-26_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.008732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2054-26_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.022121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2054-26_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.014454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2054-26_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0058431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2054-26_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.01192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2054-26_0_3_line_8 | NAYY 4x150 SE | 5 | 20 | 0.01386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2054-26_0_3_line_9 | NAYY 4x150 SE | 6 | 11 | 0.024561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2054-26_0_3_line_10 | NAYY 4x150 SE | 7 | 25 | 0.0086703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2054-26_0_3_line_11 | NAYY 4x150 SE | 8 | 24 | 0.034509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2054-26_0_3_line_12 | NAYY 4x150 SE | 9 | 10 | 0.012344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2054-26_0_3_line_13 | NAYY 4x150 SE | 10 | 11 | 0.0087819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2054-26_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.022351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2054-26_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.016962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_2054-26_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.012064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2054-26_0_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.023777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_2054-26_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.0078435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2054-26_0_3_line_19 | NAYY 4x150 SE | 15 | 18 | 0.01932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2054-26_0_3_line_20 | NAYY 4x150 SE | 16 | 19 | 0.049005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2054-26_0_3_line_21 | NAYY 4x150 SE | 16 | 20 | 0.010331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2054-26_0_3_line_22 | NAYY 4x150 SE | 17 | 21 | 0.053333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2054-26_0_3_line_23 | NAYY 4x150 SE | 18 | 22 | 0.0070065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2054-26_0_3_line_24 | NAYY 4x150 SE | 19 | 23 | 0.016777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2054-26_0_3_line_25 | NAYY 4x150 SE | 21 | 29 | 0.040996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2054-26_0_3_line_26 | NAYY 4x150 SE | 22 | 27 | 0.0068258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2054-26_0_3_line_27 | NAYY 4x150 SE | 23 | 26 | 0.077946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2054-26_0_3_line_28 | NAYY 4x150 SE | 26 | 30 | 0.050423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2054-26_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.038491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2054-26_0_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.037989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2054-26_0_3_line_31 | NAYY 4x150 SE | 30 | 32 | 0.1018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2054-26_0_3_line_32 | NAYY 4x150 SE | 31 | 33 | 0.06815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2054-26_0_3_line_33 | NAYY 4x150 SE | 32 | 34 | 0.0089604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2054-26_0_3_trafo_7 | 0.25 MVA 20/0.4 kV | 35 | 12 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2554798.3997 | 1188740.7034 | 2554798.9745 | 1188740.4152
1 | 2554789.324 | 1188746.0143 | 2554791.4763 | 1188744.1748 | 2554798.3997 | 1188740.7034
2 | 2554787.3001 | 1188743.6506 | 2554789.324 | 1188746.0143
3 | 2554795.0109 | 1188752.6527 | 2554789.324 | 1188746.0143
4 | 2554787.3001 | 1188743.6506 | 2554783.4882 | 1188721.8602
5 | 2554778.0098 | 1188732.5592 | 2554784.4214 | 1188740.2149 | 2554787.3001 | 1188743.6506
6 | 2554795.0109 | 1188752.6527 | 2554799.1423 | 1188756.7847
7 | 2554795.0109 | 1188752.6527 | 2554786.9765 | 1188761.458
8 | 2554781.0998 | 1188708.2071 | 2554783.4882 | 1188721.8602
9 | 2554778.0098 | 1188732.5592 | 2554770.5522 | 1188736.8514 | 2554757.4205 | 1188745.9157
10 | 2554799.1423 | 1188756.7847 | 2554805.2726 | 1188762.9161
11 | 2554763.6316 | 1188786.8643 | 2554764.5106 | 1188786.0797 | 2554786.9765 | 1188761.458
12 | 2554740.0346 | 1188757.9165 | 2554750.1932 | 1188750.9045
13 | 2554750.1932 | 1188750.9045 | 2554757.4205 | 1188745.9157
14 | 2554734.5326 | 1188685.9195 | 2554743.6448 | 1188694.8655 | 2554750.212 | 1188701.8425
15 | 2554761.8379 | 1188714.1938 | 2554750.212 | 1188701.8425
16 | 2554725.924 | 1188677.468 | 2554734.5326 | 1188685.9195
17 | 2554779.3195 | 1188698.0304 | 2554766.8007 | 1188709.8205 | 2554761.8379 | 1188714.1938
18 | 2554725.924 | 1188677.468 | 2554720.3257 | 1188671.9745
19 | 2554725.924 | 1188677.468 | 2554711.2775 | 1188690.0667
20 | 2554779.3195 | 1188698.0304 | 2554773.464 | 1188677.1966 | 2554767.4731 | 1188660.644 | 2554766.3546 | 1188650.9472
21 | 2554779.3195 | 1188698.0304 | 2554781.0998 | 1188708.2071
22 | 2554683.7813 | 1188633.141 | 2554713.9282 | 1188665.6969 | 2554720.3257 | 1188671.9745
23 | 2554711.2775 | 1188690.0667 | 2554705.9658 | 1188694.6358
24 | 2554766.3546 | 1188650.9472 | 2554766.6742 | 1188648.8325 | 2554768.9185 | 1188634.3676
25 | 2554683.7813 | 1188633.141 | 2554651.7611 | 1188658.7412
26 | 2554700.791 | 1188699.0871 | 2554705.9658 | 1188694.6358
27 | 2554781.9929 | 1188557.5331 | 2554774.2812 | 1188599.8035 | 2554768.9185 | 1188634.3676
28 | 2554781.9929 | 1188557.5331 | 2554783.2029 | 1188554.1443 | 2554827.4896 | 1188569.3509
29 | 2554672.897 | 1188725.5965 | 2554695.8166 | 1188703.366 | 2554700.791 | 1188699.0871
30 | 2554827.4896 | 1188569.3509 | 2554861.4483 | 1188586.5703
31 | 2554827.4896 | 1188569.3509 | 2554811.9311 | 1188618.9736 | 2554807.8089 | 1188631.6339 | 2554808.1186 | 1188640.303 | 2554815.695 | 1188667.0534
32 | 2554861.4483 | 1188586.5703 | 2554834.2711 | 1188637.9817 | 2554834.8132 | 1188647.9644
33 | 2554815.695 | 1188667.0534 | 2554818.1368 | 1188675.6746

## bus_geodata
| x | y | coords
0 | 2554798.9745 | 1188740.4152
1 | 2554798.3997 | 1188740.7034
2 | 2554789.324 | 1188746.0143
3 | 2554787.3001 | 1188743.6506
4 | 2554795.0109 | 1188752.6527
5 | 2554783.4882 | 1188721.8602
6 | 2554778.0098 | 1188732.5592
7 | 2554799.1423 | 1188756.7847
8 | 2554786.9765 | 1188761.458
9 | 2554740.0346 | 1188757.9165
10 | 2554750.1932 | 1188750.9045
11 | 2554757.4205 | 1188745.9157
12 | 2554750.212 | 1188701.8425
13 | 2554734.5326 | 1188685.9195
14 | 2554761.8379 | 1188714.1938
15 | 2554725.924 | 1188677.468
16 | 2554779.3195 | 1188698.0304
17 | 2554720.3257 | 1188671.9745
18 | 2554711.2775 | 1188690.0667
19 | 2554766.3546 | 1188650.9472
20 | 2554781.0998 | 1188708.2071
21 | 2554683.7813 | 1188633.141
22 | 2554705.9658 | 1188694.6358
23 | 2554768.9185 | 1188634.3676
24 | 2554763.6316 | 1188786.8643
25 | 2554805.2726 | 1188762.9161
26 | 2554781.9929 | 1188557.5331
27 | 2554700.791 | 1188699.0871
28 | 2554672.897 | 1188725.5965
29 | 2554651.7611 | 1188658.7412
30 | 2554827.4896 | 1188569.3509
31 | 2554861.4483 | 1188586.5703
32 | 2554815.695 | 1188667.0534
33 | 2554834.8132 | 1188647.9644
34 | 2554818.1368 | 1188675.6746
35 | 2554761.8379 | 1188714.1938

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9909 | -0.063573 | 0.0088782 | 0.0022251
1 | 0.9909 | -0.063515 | 0.0019808 | 0.00049645
2 | 0.99107 | -0.062348 | 0 | 0
3 | 0.99121 | -0.061379 | 0.0115 | 0.0028822
4 | 0.99082 | -0.064105 | 0 | 0
5 | 0.99326 | -0.046919 | 0.0046617 | 0.0011683
6 | 0.99074 | -0.064658 | 0 | 0
7 | 0.99075 | -0.06457 | 0.0045337 | 0.0011362
8 | 0.99062 | -0.065554 | 0.0072984 | 0.0018292
9 | 0.98965 | -0.072364 | 0.0082108 | 0.0020578
10 | 0.9898 | -0.071331 | 0.0040211 | 0.0010078
11 | 0.98995 | -0.070237 | 0.010086 | 0.0025277
12 | 1 | 0 | -0.2079 | -0.05222
13 | 0.99796 | -0.014259 | 0.004276 | 0.0010717
14 | 0.99827 | -0.011951 | 0 | 0
15 | 0.99693 | -0.021461 | 0 | 0
16 | 0.99584 | -0.028773 | 0 | 0
17 | 0.99662 | -0.023628 | 0.0052696 | 0.0013207
18 | 0.99605 | -0.027674 | 0.0072523 | 0.0018176
19 | 0.99158 | -0.058302 | 0 | 0
20 | 0.99464 | -0.037238 | 0.012171 | 0.0030502
21 | 0.99492 | -0.035567 | 0 | 0
22 | 0.9958 | -0.029418 | 0.0095021 | 0.0023815
23 | 0.99012 | -0.068469 | 0.0049936 | 0.0012515
24 | 0.99038 | -0.067188 | 0.0046536 | 0.0011663
25 | 0.99071 | -0.064862 | 0.003305 | 0.00082831
26 | 0.98389 | -0.11208 | 0 | 0
27 | 0.99565 | -0.030465 | 0.012357 | 0.0030971
28 | 0.99549 | -0.031582 | 0.0028793 | 0.00072163
29 | 0.99361 | -0.04477 | 0.022233 | 0.0055721
30 | 0.97986 | -0.14059 | 0 | 0
31 | 0.9793 | -0.14462 | 0 | 0
32 | 0.97324 | -0.1879 | 0.02757 | 0.0069097
33 | 0.97829 | -0.15186 | 0.010191 | 0.002554
34 | 0.97302 | -0.18949 | 0.016828 | 0.0042176
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0088782 | -0.0022251 | 0.0088783 | 0.0022251 | 7.1326e-08 | 1.9149e-08 | 0.013332 | 0.013332 | 0.013332 | 0.9909 | -0.063573 | 0.9909 | -0.063515 | 4.9379
1 | -0.010859 | -0.0027216 | 0.010861 | 0.0027221 | 1.7549e-06 | 5.3871e-07 | 0.016307 | 0.016307 | 0.016307 | 0.9909 | -0.063515 | 0.99107 | -0.062348 | 6.0396
2 | -0.030661 | -0.0076846 | 0.030665 | 0.0076862 | 4.1113e-06 | 1.5412e-06 | 0.046035 | 0.046035 | 0.046035 | 0.99107 | -0.062348 | 0.99121 | -0.061379 | 17.0499
3 | 0.0198 | 0.0049625 | -0.019795 | -0.0049608 | 4.8153e-06 | 1.7395e-06 | 0.029728 | 0.029728 | 0.029728 | 0.99107 | -0.062348 | 0.99082 | -0.064105 | 11.0103
4 | -0.064512 | -0.016173 | 0.064642 | 0.016222 | 0.00012947 | 4.9512e-05 | 0.096849 | 0.096849 | 0.096849 | 0.99121 | -0.061379 | 0.99326 | -0.046919 | 35.8699
5 | 0.022348 | 0.0056042 | -0.022338 | -0.0056005 | 1.0152e-05 | 3.7185e-06 | 0.03355 | 0.03355 | 0.03355 | 0.99121 | -0.061379 | 0.99074 | -0.064658 | 12.426
6 | 0.0078393 | 0.0019646 | -0.0078388 | -0.0019645 | 5.0537e-07 | 1.1912e-07 | 0.011773 | 0.011773 | 0.011773 | 0.99082 | -0.064105 | 0.99075 | -0.06457 | 4.3604
7 | 0.011955 | 0.0029962 | -0.011953 | -0.0029954 | 2.3978e-06 | 7.6875e-07 | 0.017955 | 0.017955 | 0.017955 | 0.99082 | -0.064105 | 0.99062 | -0.065554 | 6.6499
8 | -0.069304 | -0.01739 | 0.069397 | 0.017426 | 9.3245e-05 | 3.5684e-05 | 0.10383 | 0.10383 | 0.10383 | 0.99326 | -0.046919 | 0.99464 | -0.037238 | 38.4564
9 | 0.022338 | 0.0056005 | -0.02232 | -0.0055942 | 1.7251e-05 | 6.319e-06 | 0.03355 | 0.03355 | 0.03355 | 0.99074 | -0.064658 | 0.98995 | -0.070237 | 12.426
10 | 0.0033051 | 0.00082825 | -0.003305 | -0.00082831 | 1.3331e-07 | -6.0375e-08 | 0.004964 | 0.004964 | 0.004964 | 0.99075 | -0.06457 | 0.99071 | -0.064862 | 1.8385
11 | 0.0046546 | 0.0011663 | -0.0046536 | -0.0011663 | 1.0527e-06 | -3.93e-08 | 0.0069917 | 0.0069918 | 0.0069918 | 0.99062 | -0.065554 | 0.99038 | -0.067188 | 2.5896
12 | -0.0082108 | -0.0020578 | 0.0082119 | 0.0020581 | 1.1739e-06 | 2.9289e-07 | 0.012346 | 0.012345 | 0.012346 | 0.98965 | -0.072364 | 0.9898 | -0.071331 | 4.5724
13 | -0.012233 | -0.0030659 | 0.012235 | 0.0030665 | 1.8534e-06 | 5.9994e-07 | 0.018391 | 0.01839 | 0.018391 | 0.9898 | -0.071331 | 0.98995 | -0.070237 | 6.8113
14 | 0.064066 | 0.016093 | -0.063939 | -0.016045 | 0.00012679 | 4.8471e-05 | 0.095344 | 0.095344 | 0.095344 | 1 | 0 | 0.99796 | -0.014259 | 35.3127
15 | 0.14303 | 0.036126 | -0.14279 | -0.036034 | 0.00023995 | 9.1842e-05 | 0.21293 | 0.21293 | 0.21293 | 1 | 0 | 0.99827 | -0.011951 | 39.4316
16 | 0.059663 | 0.014973 | -0.059604 | -0.014951 | 5.9586e-05 | 2.276e-05 | 0.088968 | 0.088969 | 0.088969 | 0.99796 | -0.014259 | 0.99693 | -0.021461 | 32.9513
17 | 0.14279 | 0.036034 | -0.14245 | -0.035906 | 0.00033635 | 0.00012874 | 0.21293 | 0.21293 | 0.21293 | 0.99827 | -0.011951 | 0.99584 | -0.028773 | 39.4317
18 | 0.027576 | 0.0069198 | -0.027568 | -0.0069167 | 8.293e-06 | 3.0874e-06 | 0.041163 | 0.041163 | 0.041163 | 0.99693 | -0.021461 | 0.99662 | -0.023628 | 15.2456
19 | 0.032027 | 0.0080307 | -0.032 | -0.0080204 | 2.7551e-05 | 1.0345e-05 | 0.047805 | 0.047805 | 0.047805 | 0.99693 | -0.021461 | 0.99605 | -0.027674 | 17.7057
20 | 0.060791 | 0.015392 | -0.060539 | -0.015296 | 0.00025262 | 9.6528e-05 | 0.090891 | 0.090892 | 0.090892 | 0.99584 | -0.028773 | 0.99158 | -0.058302 | 33.6636
21 | 0.081663 | 0.020513 | -0.081567 | -0.020476 | 9.6015e-05 | 3.6795e-05 | 0.12204 | 0.12204 | 0.12204 | 0.99584 | -0.028773 | 0.99464 | -0.037238 | 45.1999
22 | 0.022298 | 0.005596 | -0.022261 | -0.0055825 | 3.6894e-05 | 1.3496e-05 | 0.033295 | 0.033296 | 0.033296 | 0.99662 | -0.023628 | 0.99492 | -0.035567 | 12.3317
23 | 0.024748 | 0.0062028 | -0.024742 | -0.0062006 | 5.976e-06 | 2.2073e-06 | 0.036971 | 0.036971 | 0.036971 | 0.99605 | -0.027674 | 0.9958 | -0.029418 | 13.693
24 | 0.060539 | 0.015296 | -0.060452 | -0.015263 | 8.6485e-05 | 3.3047e-05 | 0.090892 | 0.090892 | 0.090892 | 0.99158 | -0.058302 | 0.99012 | -0.068469 | 33.6636
25 | 0.022261 | 0.0055825 | -0.022233 | -0.0055721 | 2.836e-05 | 1.0376e-05 | 0.033296 | 0.033296 | 0.033296 | 0.99492 | -0.035567 | 0.99361 | -0.04477 | 12.3318
26 | 0.015239 | 0.0038191 | -0.015237 | -0.0038184 | 2.2088e-06 | 7.6073e-07 | 0.022772 | 0.022772 | 0.022772 | 0.9958 | -0.029418 | 0.99565 | -0.030465 | 8.4341
27 | 0.055459 | 0.014011 | -0.05512 | -0.013882 | 0.0003382 | 0.00012908 | 0.083387 | 0.083387 | 0.083387 | 0.99012 | -0.068469 | 0.98389 | -0.11208 | 30.8842
28 | 0.05512 | 0.013882 | -0.054902 | -0.013799 | 0.00021878 | 8.351e-05 | 0.083387 | 0.083388 | 0.083388 | 0.98389 | -0.11208 | 0.97986 | -0.14059 | 30.8843
29 | 0.0028798 | 0.0007213 | -0.0028793 | -0.00072163 | 4.449e-07 | -3.294e-07 | 0.0043038 | 0.0043039 | 0.0043039 | 0.99565 | -0.030465 | 0.99549 | -0.031582 | 1.594
30 | 0.010207 | 0.0025588 | -0.010201 | -0.0025571 | 5.6953e-06 | 1.7122e-06 | 0.0155 | 0.0155 | 0.0155 | 0.97986 | -0.14059 | 0.9793 | -0.14462 | 5.7408
31 | 0.044695 | 0.01124 | -0.044402 | -0.011129 | 0.00029275 | 0.00011132 | 0.067888 | 0.067888 | 0.067888 | 0.97986 | -0.14059 | 0.97324 | -0.1879 | 25.1437
32 | 0.010201 | 0.0025571 | -0.010191 | -0.002554 | 1.0217e-05 | 3.0732e-06 | 0.0155 | 0.015501 | 0.015501 | 0.9793 | -0.14462 | 0.97829 | -0.15186 | 5.7409
33 | 0.016832 | 0.0042189 | -0.016828 | -0.0042176 | 3.7031e-06 | 1.3129e-06 | 0.025735 | 0.025735 | 0.025735 | 0.97324 | -0.1879 | 0.97302 | -0.18949 | 9.5315

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21182 | 0.053203

## res_load
| p_mw | q_mvar
0 | 0.0088782 | 0.0022251
1 | 0.0019808 | 0.00049645
2 | 0.0115 | 0.0028822
3 | 0.0046617 | 0.0011683
4 | 0.0045337 | 0.0011362
5 | 0.0072984 | 0.0018292
6 | 0.0082108 | 0.0020578
7 | 0.0040211 | 0.0010078
8 | 0.010086 | 0.0025277
9 | 0.0039226 | 0.0009831
10 | 0.004276 | 0.0010717
11 | 0.0052696 | 0.0013207
12 | 0.0072523 | 0.0018176
13 | 0.012171 | 0.0030502
14 | 0.0095021 | 0.0023815
15 | 0.0049936 | 0.0012515
16 | 0.0046536 | 0.0011663
17 | 0.003305 | 0.00082831
18 | 0.012357 | 0.0030971
19 | 0.0028793 | 0.00072163
20 | 0.022233 | 0.0055721
21 | 0.02757 | 0.0069097
22 | 0.010191 | 0.002554
23 | 0.016828 | 0.0042176

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1