## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2054-35_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2054-35_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2054-35_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2054-35_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2054-35_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2054-35_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_2054-35_0_4_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_2054-35_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2054-35_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_2054-35_0_4_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_2054-35_0_4_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_2054-35_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2054-35_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_2054-35_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2054-35_0_4_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_2054-35_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2054-35_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2054-35_0_4_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2054-35_0_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_2054-35_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2054-35_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2054-35_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_2054-35_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2054-35_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_2054-35_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_2054-35_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_2054-35_0_4_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_2054-35_0_4_node_26 | 0.4 | n |  | TRUE
28 | bus_MV_454_1_node_130 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2054-35_0_4_load_0 | 0 | 0.017333 | 0.0043441 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2054-35_0_4_load_1 | 1 | 0.012953 | 0.0032463 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2054-35_0_4_load_4 | 4 | 0.0090233 | 0.0022614 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2054-35_0_4_load_13 | 8 | 0.026375 | 0.0066102 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2054-35_0_4_load_28 | 9 | 0.00041265 | 0.00010342 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2054-35_0_4_load_23 | 10 | 0.0017003 | 0.00042614 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2054-35_0_4_load_5 | 12 | 0.004422 | 0.0011082 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2054-35_0_4_load_21 | 14 | 0.0075034 | 0.0018805 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2054-35_0_4_load_12 | 15 | 0.020881 | 0.0052332 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2054-35_0_4_load_10 | 16 | 0.05249 | 0.013155 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2054-35_0_4_load_22 | 17 | 0.0083623 | 0.0020958 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2054-35_0_4_load_14 | 19 | 0.049872 | 0.012499 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2054-35_0_4_load_15 | 20 | 0.0051685 | 0.0012954 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2054-35_0_4_load_20 | 23 | 0.0077555 | 0.0019437 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2054-35_0_4_load_17 | 24 | 0.0074339 | 0.0018631 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2054-35_0_4_load_19 | 25 | 0.0049126 | 0.0012312 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2054-35_0_4_load_26 | 27 | 0.00033481 | 8.3912e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2054-35_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.028559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2054-35_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.033196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2054-35_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.016271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2054-35_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.024191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2054-35_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.052898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2054-35_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.11208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2054-35_0_4_line_6 | NAYY 4x150 SE | 3 | 7 | 0.072065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2054-35_0_4_line_7 | NAYY 4x150 SE | 4 | 8 | 0.080063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2054-35_0_4_line_8 | NAYY 4x150 SE | 5 | 9 | 0.035365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2054-35_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.092452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2054-35_0_4_line_10 | NAYY 4x150 SE | 7 | 11 | 0.017137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2054-35_0_4_line_11 | NAYY 4x150 SE | 7 | 12 | 0.037821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2054-35_0_4_line_12 | NAYY 4x150 SE | 10 | 18 | 0.037969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2054-35_0_4_line_13 | NAYY 4x150 SE | 11 | 13 | 0.002884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_2054-35_0_4_line_14 | NAYY 4x150 SE | 11 | 14 | 0.02307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_2054-35_0_4_line_15 | NAYY 4x150 SE | 13 | 15 | 0.062655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2054-35_0_4_line_16 | NAYY 4x150 SE | 13 | 16 | 0.044582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2054-35_0_4_line_17 | NAYY 4x150 SE | 14 | 17 | 0.032491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2054-35_0_4_line_18 | NAYY 4x150 SE | 15 | 19 | 0.027218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2054-35_0_4_line_19 | NAYY 4x150 SE | 18 | 26 | 0.046024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2054-35_0_4_line_20 | NAYY 4x150 SE | 19 | 20 | 0.0028686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2054-35_0_4_line_21 | NAYY 4x150 SE | 20 | 21 | 0.043666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2054-35_0_4_line_22 | NAYY 4x150 SE | 21 | 22 | 0.043644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2054-35_0_4_line_23 | NAYY 4x150 SE | 22 | 23 | 0.020674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2054-35_0_4_line_24 | NAYY 4x150 SE | 22 | 24 | 0.019064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2054-35_0_4_line_25 | NAYY 4x150 SE | 24 | 25 | 0.0097456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2054-35_0_4_line_26 | NAYY 4x150 SE | 26 | 27 | 0.0663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2054-35_0_4_trafo_21 | 0.25 MVA 20/0.4 kV | 28 | 14 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2554868.2514 | 1187883.9744 | 2554891.6153 | 1187900.3976
1 | 2554841.0935 | 1187864.8842 | 2554868.2514 | 1187883.9744
2 | 2554905.0377 | 1187909.5923 | 2554897.4547 | 1187904.5023 | 2554891.6153 | 1187900.3976
3 | 2554841.0935 | 1187864.8842 | 2554827.1939 | 1187884.6831
4 | 2554905.0377 | 1187909.5923 | 2554903.4554 | 1187913.2062 | 2554903.1341 | 1187917.133 | 2554904.1013 | 1187920.9501 | 2554906.2698 | 1187924.2466 | 2554909.3851 | 1187926.6577 | 2554912.6667 | 1187927.8447 | 2554916.1468 | 1187928.0519 | 2554919.543 | 1187927.2481 | 2554922.5583 | 1187925.5021 | 2554924.9498 | 1187922.9716 | 2554933.3985 | 1187929.567 | 2554936.5482 | 1187933.501
5 | 2554905.0377 | 1187909.5923 | 2554907.5039 | 1187906.85 | 2554910.6938 | 1187904.9916 | 2554914.3036 | 1187904.1861 | 2554917.983 | 1187904.5141 | 2554920.0664 | 1187894.5151 | 2554921.2004 | 1187882.0442 | 2554921.5935 | 1187854.2927 | 2554919.9987 | 1187819.8747 | 2554919.1961 | 1187807.5407
6 | 2554880.3906 | 1187970.2227 | 2554890.5366 | 1187956.1162 | 2554903.6955 | 1187934.8941 | 2554909.3851 | 1187926.6577 | 2554906.2698 | 1187924.2466 | 2554904.1013 | 1187920.9501 | 2554903.1341 | 1187917.133 | 2554903.4554 | 1187913.2062 | 2554905.0377 | 1187909.5923
7 | 2554835.6345 | 1187942.7201 | 2554805.7777 | 1187921.8713 | 2554807.0559 | 1187913.3681 | 2554827.1939 | 1187884.6831
8 | 2554936.5482 | 1187933.501 | 2554959.986 | 1187915.7367 | 2554964.9416 | 1187912.3197
9 | 2554919.1961 | 1187807.5407 | 2554930.407 | 1187807.1226 | 2554948.5132 | 1187806.5857 | 2554995.6507 | 1187807.6644 | 2555011.5762 | 1187808.8424
10 | 2554880.3906 | 1187970.2227 | 2554869.2757 | 1187983.2916
11 | 2554880.3906 | 1187970.2227 | 2554909.5882 | 1187994.2624
12 | 2555049.2077 | 1187813.3087 | 2555045.4926 | 1187812.3028 | 2555034.5247 | 1187810.5399 | 2555011.5762 | 1187808.8424
13 | 2554869.2757 | 1187983.2916 | 2554867.3467 | 1187985.4407
14 | 2554869.2757 | 1187983.2916 | 2554850.0828 | 1187970.491
15 | 2554867.3467 | 1187985.4407 | 2554865.6295 | 1187987.3547 | 2554832.1169 | 1188024.495 | 2554825.8039 | 1188032.3252
16 | 2554867.3467 | 1187985.4407 | 2554901.792 | 1188013.7436
17 | 2554850.0828 | 1187970.491 | 2554823.0517 | 1187952.4628
18 | 2554825.8039 | 1188032.3252 | 2554815.4604 | 1188045.1545 | 2554809.1198 | 1188053.8212
19 | 2555049.2077 | 1187813.3087 | 2555060.2957 | 1187819.8733 | 2555067.6619 | 1187827.5888 | 2555073.242 | 1187838.2082 | 2555075.5312 | 1187848.4299
20 | 2554809.1198 | 1188053.8212 | 2554807.4261 | 1188056.1363
21 | 2554783.4758 | 1188092.6003 | 2554791.1264 | 1188079.4352 | 2554799.8391 | 1188066.5066 | 2554807.4261 | 1188056.1363
22 | 2554783.4758 | 1188092.6003 | 2554781.4577 | 1188096.073 | 2554747.9092 | 1188074.9821
23 | 2554747.9092 | 1188074.9821 | 2554730.1582 | 1188064.3843
24 | 2554747.9092 | 1188074.9821 | 2554757.6332 | 1188058.5843
25 | 2554762.6041 | 1188050.2017 | 2554757.6332 | 1188058.5843
26 | 2555075.5312 | 1187848.4299 | 2555072.3038 | 1187861.5503 | 2555068.7194 | 1187870.8045 | 2555059.5557 | 1187883.7361 | 2555050.846 | 1187891.0945 | 2555043.3858 | 1187894.1968 | 2555035.8727 | 1187894.7461

## bus_geodata
| x | y | coords
0 | 2554868.2514 | 1187883.9744
1 | 2554891.6153 | 1187900.3976
2 | 2554841.0935 | 1187864.8842
3 | 2554905.0377 | 1187909.5923
4 | 2554827.1939 | 1187884.6831
5 | 2554936.5482 | 1187933.501
6 | 2554919.1961 | 1187807.5407
7 | 2554880.3906 | 1187970.2227
8 | 2554835.6345 | 1187942.7201
9 | 2554964.9416 | 1187912.3197
10 | 2555011.5762 | 1187808.8424
11 | 2554869.2757 | 1187983.2916
12 | 2554909.5882 | 1187994.2624
13 | 2554867.3467 | 1187985.4407
14 | 2554850.0828 | 1187970.491
15 | 2554825.8039 | 1188032.3252
16 | 2554901.792 | 1188013.7436
17 | 2554823.0517 | 1187952.4628
18 | 2555049.2077 | 1187813.3087
19 | 2554809.1198 | 1188053.8212
20 | 2554807.4261 | 1188056.1363
21 | 2554783.4758 | 1188092.6003
22 | 2554747.9092 | 1188074.9821
23 | 2554730.1582 | 1188064.3843
24 | 2554757.6332 | 1188058.5843
25 | 2554762.6041 | 1188050.2017
26 | 2555075.5312 | 1187848.4299
27 | 2555035.8727 | 1187894.7461
28 | 2554869.2757 | 1187983.2916

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98488 | -0.10574 | 0.017333 | 0.0043441
1 | 0.98707 | -0.09028 | 0.012953 | 0.0032463
2 | 0.98317 | -0.11786 | 0 | 0
3 | 0.98862 | -0.079346 | 0 | 0
4 | 0.98193 | -0.12671 | 0.0090233 | 0.0022614
5 | 0.98859 | -0.079573 | 0 | 0
6 | 0.98829 | -0.081709 | 0 | 0
7 | 0.99574 | -0.029521 | 0 | 0
8 | 0.97885 | -0.14864 | 0.026375 | 0.0066102
9 | 0.98857 | -0.079722 | 0.00041265 | 0.00010342
10 | 0.98802 | -0.08365 | 0.0017003 | 0.00042614
11 | 0.99754 | -0.017016 | 0 | 0
12 | 0.9955 | -0.031206 | 0.004422 | 0.0011082
13 | 0.99724 | -0.019165 | 0 | 0
14 | 1 | 0 | -0.23309 | -0.058587
15 | 0.98853 | -0.080087 | 0.020881 | 0.0052332
16 | 0.99388 | -0.04273 | 0.05249 | 0.013155
17 | 0.99961 | -0.0027132 | 0.0083623 | 0.0020958
18 | 0.988 | -0.083785 | 0 | 0
19 | 0.98557 | -0.10104 | 0.049872 | 0.012499
20 | 0.98547 | -0.10179 | 0.0051685 | 0.0012954
21 | 0.9842 | -0.11082 | 0 | 0
22 | 0.98292 | -0.11988 | 0 | 0
23 | 0.98269 | -0.12154 | 0.0077555 | 0.0019437
24 | 0.98258 | -0.12231 | 0.0074339 | 0.0018631
25 | 0.98251 | -0.12281 | 0.0049126 | 0.0012312
26 | 0.98798 | -0.083946 | 0 | 0
27 | 0.98795 | -0.084175 | 0.00033481 | 8.3912e-05
28 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.052915 | -0.013285 | 0.053029 | 0.013328 | 0.00011393 | 4.3453e-05 | 0.079956 | 0.079956 | 0.079956 | 0.98488 | -0.10574 | 0.98707 | -0.09028 | 29.6132
1 | 0.035582 | 0.0089406 | -0.035522 | -0.008918 | 5.9885e-05 | 2.2611e-05 | 0.053768 | 0.053768 | 0.053768 | 0.98488 | -0.10574 | 0.98317 | -0.11786 | 19.914
2 | -0.065982 | -0.016574 | 0.066083 | 0.016613 | 0.00010048 | 3.8438e-05 | 0.099482 | 0.099482 | 0.099482 | 0.98707 | -0.09028 | 0.98862 | -0.079346 | 36.8452
3 | 0.035522 | 0.008918 | -0.035479 | -0.0089015 | 4.364e-05 | 1.6478e-05 | 0.053768 | 0.053768 | 0.053768 | 0.98317 | -0.11786 | 0.98193 | -0.12671 | 19.9141
4 | 0.00041267 | 0.0001023 | -0.00041266 | -0.00010297 | 1.2723e-08 | -6.7336e-07 | 0.00062073 | 0.00062097 | 0.00062097 | 0.98862 | -0.079346 | 0.98859 | -0.079573 | 0.22999
5 | 0.0020363 | 0.00050597 | -0.0020357 | -0.00050716 | 6.5644e-07 | -1.1841e-06 | 0.0030634 | 0.003064 | 0.003064 | 0.98862 | -0.079346 | 0.98829 | -0.081709 | 1.1348
6 | -0.068532 | -0.017221 | 0.06901 | 0.017404 | 0.00047861 | 0.00018315 | 0.10317 | 0.10317 | 0.10317 | 0.98862 | -0.079346 | 0.99574 | -0.029521 | 38.2097
7 | 0.026455 | 0.0066401 | -0.026375 | -0.0066102 | 8.0312e-05 | 2.988e-05 | 0.040094 | 0.040094 | 0.040094 | 0.98193 | -0.12671 | 0.97885 | -0.14864 | 14.8498
8 | 0.00041266 | 0.00010297 | -0.00041265 | -0.00010342 | 8.5117e-09 | -4.5015e-07 | 0.00062097 | 0.00062113 | 0.00062113 | 0.98859 | -0.079573 | 0.98857 | -0.079722 | 0.23005
9 | 0.0020357 | 0.00050716 | -0.0020351 | -0.00050813 | 5.4166e-07 | -9.7601e-07 | 0.003064 | 0.0030644 | 0.0030644 | 0.98829 | -0.081709 | 0.98802 | -0.08365 | 1.135
10 | -0.073433 | -0.018512 | 0.073562 | 0.018562 | 0.00012886 | 4.9339e-05 | 0.10978 | 0.10978 | 0.10978 | 0.99574 | -0.029521 | 0.99754 | -0.017016 | 40.6576
11 | 0.004423 | 0.0011082 | -0.004422 | -0.0011082 | 1.031e-06 | -9.5304e-08 | 0.0066095 | 0.0066097 | 0.0066097 | 0.99574 | -0.029521 | 0.9955 | -0.031206 | 2.448
12 | 0.00033484 | 8.1996e-05 | -0.00033483 | -8.248e-05 | 6.0109e-09 | -4.8394e-07 | 0.00050361 | 0.00050378 | 0.00050378 | 0.98802 | -0.08365 | 0.988 | -0.083785 | 0.18658
13 | 0.14983 | 0.037724 | -0.14979 | -0.037707 | 4.4972e-05 | 1.7222e-05 | 0.22356 | 0.22356 | 0.22356 | 0.99754 | -0.017016 | 0.99724 | -0.019165 | 41.4
14 | -0.22339 | -0.056286 | 0.22393 | 0.05649 | 0.00053318 | 0.00020416 | 0.33334 | 0.33334 | 0.33334 | 0.99754 | -0.017016 | 1 | 0 | 41.1525
15 | 0.097124 | 0.024486 | -0.096302 | -0.024171 | 0.0008217 | 0.00031523 | 0.14497 | 0.14497 | 0.14497 | 0.99724 | -0.019165 | 0.98853 | -0.080087 | 53.6938
16 | 0.052662 | 0.013221 | -0.05249 | -0.013155 | 0.00017181 | 6.5501e-05 | 0.078587 | 0.078587 | 0.078587 | 0.99724 | -0.019165 | 0.99388 | -0.04273 | 29.1064
17 | 0.0083654 | 0.0020966 | -0.0083623 | -0.0020958 | 3.1416e-06 | 7.8221e-07 | 0.012448 | 0.012448 | 0.012448 | 1 | 0 | 0.99961 | -0.0027132 | 4.6104
18 | 0.075421 | 0.018938 | -0.075202 | -0.018854 | 0.00021896 | 8.3866e-05 | 0.11354 | 0.11354 | 0.11354 | 0.98853 | -0.080087 | 0.98557 | -0.10104 | 42.0527
19 | 0.00033483 | 8.248e-05 | -0.00033482 | -8.3067e-05 | 7.2916e-09 | -5.8658e-07 | 0.00050378 | 0.00050398 | 0.00050398 | 0.988 | -0.083785 | 0.98798 | -0.083946 | 0.18666
20 | 0.02533 | 0.0063544 | -0.025327 | -0.0063535 | 2.6182e-06 | 9.7045e-07 | 0.038245 | 0.038245 | 0.038245 | 0.98557 | -0.10104 | 0.98547 | -0.10179 | 14.1649
21 | 0.020159 | 0.0050581 | -0.020133 | -0.005049 | 2.5249e-05 | 9.1556e-06 | 0.030441 | 0.030441 | 0.030441 | 0.98547 | -0.10179 | 0.9842 | -0.11082 | 11.2745
22 | 0.020133 | 0.005049 | -0.020108 | -0.0050398 | 2.5237e-05 | 9.1525e-06 | 0.030441 | 0.030441 | 0.030441 | 0.9842 | -0.11082 | 0.98292 | -0.11988 | 11.2745
23 | 0.0077573 | 0.0019441 | -0.0077555 | -0.0019437 | 1.7791e-06 | 4.223e-07 | 0.011743 | 0.011744 | 0.011744 | 0.98292 | -0.11988 | 0.98269 | -0.12154 | 4.3495
24 | 0.012351 | 0.0030957 | -0.012347 | -0.0030943 | 4.159e-06 | 1.358e-06 | 0.018698 | 0.018698 | 0.018698 | 0.98292 | -0.11988 | 0.98258 | -0.12231 | 6.9251
25 | 0.0049129 | 0.0012312 | -0.0049126 | -0.0012312 | 3.3662e-07 | 6.0395e-09 | 0.00744 | 0.0074401 | 0.0074401 | 0.98258 | -0.12231 | 0.98251 | -0.12281 | 2.7556
26 | 0.00033482 | 8.3067e-05 | -0.00033481 | -8.3912e-05 | 1.0514e-08 | -8.4495e-07 | 0.00050398 | 0.00050428 | 0.00050428 | 0.98798 | -0.083946 | 0.98795 | -0.084175 | 0.18677

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24059 | 0.060467

## res_load
| p_mw | q_mvar
0 | 0.017333 | 0.0043441
1 | 0.012953 | 0.0032463
2 | 0.0090233 | 0.0022614
3 | 0.026375 | 0.0066102
4 | 0.00041265 | 0.00010342
5 | 0.0017003 | 0.00042614
6 | 0.004422 | 0.0011082
7 | 0.0075034 | 0.0018805
8 | 0.020881 | 0.0052332
9 | 0.05249 | 0.013155
10 | 0.0083623 | 0.0020958
11 | 0.049872 | 0.012499
12 | 0.0051685 | 0.0012954
13 | 0.0077555 | 0.0019437
14 | 0.0074339 | 0.0018631
15 | 0.0049126 | 0.0012312
16 | 0.00033481 | 8.3912e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1