## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2054-36_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2054-36_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2054-36_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2054-36_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2054-36_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2054-36_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2054-36_0_2_node_52 | 0.4 | n |  | TRUE
7 | bus_LV_2054-36_0_2_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_2054-36_0_2_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_2054-36_0_2_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_2054-36_0_2_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_2054-36_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2054-36_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2054-36_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2054-36_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2054-36_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2054-36_0_2_node_37 | 0.4 | n |  | TRUE
17 | bus_LV_2054-36_0_2_node_44 | 0.4 | n |  | TRUE
18 | bus_LV_2054-36_0_2_node_39 | 0.4 | n |  | TRUE
19 | bus_LV_2054-36_0_2_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_2054-36_0_2_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_2054-36_0_2_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2054-36_0_2_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_2054-36_0_2_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2054-36_0_2_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2054-36_0_2_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_2054-36_0_2_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_2054-36_0_2_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2054-36_0_2_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_2054-36_0_2_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2054-36_0_2_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_2054-36_0_2_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_2054-36_0_2_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_2054-36_0_2_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_2054-36_0_2_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_2054-36_0_2_node_45 | 0.4 | n |  | TRUE
36 | bus_LV_2054-36_0_2_node_55 | 0.4 | n |  | TRUE
37 | bus_LV_2054-36_0_2_node_46 | 0.4 | n |  | TRUE
38 | bus_LV_2054-36_0_2_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_2054-36_0_2_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_2054-36_0_2_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_2054-36_0_2_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_2054-36_0_2_node_53 | 0.4 | n |  | TRUE
43 | bus_LV_2054-36_0_2_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_2054-36_0_2_node_54 | 0.4 | n |  | TRUE
45 | bus_LV_2054-36_0_2_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_2054-36_0_2_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_2054-36_0_2_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_2054-36_0_2_node_48 | 0.4 | n |  | TRUE
49 | bus_LV_2054-36_0_2_node_49 | 0.4 | n |  | TRUE
50 | bus_LV_2054-36_0_2_node_50 | 0.4 | n |  | TRUE
51 | bus_LV_2054-36_0_2_node_51 | 0.4 | n |  | TRUE
52 | bus_MV_477_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2054-36_0_2_load_0 | 0 | 0.0091164 | 0.0022848 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2054-36_0_2_load_1 | 1 | 0.0030503 | 0.00076448 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2054-36_0_2_load_3 | 3 | 0.014371 | 0.0036017 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2054-36_0_2_load_5 | 5 | 0.00048949 | 0.00012268 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2054-36_0_2_load_52 | 6 | 0.016772 | 0.0042036 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2054-36_0_2_load_30 | 7 | 0.0021708 | 0.00054406 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2054-36_0_2_load_13 | 8 | 0.0068647 | 0.0017205 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2054-36_0_2_load_28 | 9 | 0.004421 | 0.001108 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2054-36_0_2_load_11 | 10 | 0.0031274 | 0.00078379 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2054-36_0_2_load_6 | 11 | 0.0047542 | 0.0011915 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2054-36_0_2_load_7 | 12 | 0.0026481 | 0.00066367 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2054-36_0_2_load_8 | 13 | 0.0010569 | 0.00026489 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2054-36_0_2_load_9 | 14 | 0.00064004 | 0.00016041 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2054-36_0_2_load_44 | 17 | 0.001325 | 0.00033209 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2054-36_0_2_load_39 | 18 | 0.001329 | 0.00033308 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2054-36_0_2_load_36 | 19 | 0.00090037 | 0.00022566 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2054-36_0_2_load_22 | 20 | 0.00093271 | 0.00023376 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2054-36_0_2_load_12 | 21 | 0.0004197 | 0.00010519 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2054-36_0_2_load_14 | 22 | 0.00067819 | 0.00016997 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2054-36_0_2_load_21 | 23 | 0.00045037 | 0.00011287 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2054-36_0_2_load_15 | 24 | 0.0015644 | 0.00039208 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2054-36_0_2_load_16 | 25 | 0.0010835 | 0.00027154 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2054-36_0_2_load_17 | 26 | 0.0070488 | 0.0017666 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2054-36_0_2_load_19 | 27 | 0.0033749 | 0.00084583 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2054-36_0_2_load_32 | 28 | 0.0020519 | 0.00051426 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2054-36_0_2_load_27 | 30 | 0.0016233 | 0.00040683 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2054-36_0_2_load_23 | 31 | 0.0032275 | 0.00080889 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2054-36_0_2_load_24 | 33 | 0.0060913 | 0.0015266 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2054-36_0_2_load_26 | 34 | 0.0088666 | 0.0022222 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2054-36_0_2_load_45 | 35 | 0.0032116 | 0.00080491 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2054-36_0_2_load_46 | 37 | 0.0014264 | 0.00035748 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2054-36_0_2_load_31 | 38 | 0.0044098 | 0.0011052 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2054-36_0_2_load_29 | 40 | 0.00052128 | 0.00013065 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2054-36_0_2_load_35 | 41 | 0.0064176 | 0.0016084 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2054-36_0_2_load_53 | 42 | 0.0025056 | 0.00062797 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2054-36_0_2_load_43 | 43 | 0.0044411 | 0.001113 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2054-36_0_2_load_54 | 44 | 0.0013672 | 0.00034266 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2054-36_0_2_load_40 | 46 | 0.0024181 | 0.00060603 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2054-36_0_2_load_42 | 47 | 0.00063438 | 0.00015899 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2054-36_0_2_load_48 | 48 | 0.0013376 | 0.00033523 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2054-36_0_2_load_49 | 49 | 0.0074564 | 0.0018688 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2054-36_0_2_load_50 | 50 | 0.00074812 | 0.0001875 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2054-36_0_2_load_51 | 51 | 0.0013983 | 0.00035045 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2054-36_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.019072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2054-36_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.040437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2054-36_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.01065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2054-36_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.022912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2054-36_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.0083149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2054-36_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.028138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2054-36_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0053161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2054-36_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.020814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2054-36_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.017296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2054-36_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.033641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2054-36_0_2_line_10 | NAYY 4x150 SE | 9 | 40 | 0.01738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2054-36_0_2_line_11 | NAYY 4x150 SE | 10 | 21 | 0.025849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2054-36_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.00025964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2054-36_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.028975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2054-36_0_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.01801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2054-36_0_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.004796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2054-36_0_2_line_16 | NAYY 4x150 SE | 15 | 16 | 0.02094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2054-36_0_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.035003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2054-36_0_2_line_18 | NAYY 4x150 SE | 16 | 18 | 0.009802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2054-36_0_2_line_19 | NAYY 4x150 SE | 16 | 19 | 0.023322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2054-36_0_2_line_20 | NAYY 4x150 SE | 17 | 20 | 0.0062292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2054-36_0_2_line_21 | NAYY 4x150 SE | 20 | 23 | 0.0052729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2054-36_0_2_line_22 | NAYY 4x150 SE | 21 | 22 | 0.0064942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2054-36_0_2_line_23 | NAYY 4x150 SE | 22 | 23 | 0.021465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2054-36_0_2_line_24 | NAYY 4x150 SE | 24 | 25 | 0.027329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2054-36_0_2_line_25 | NAYY 4x150 SE | 24 | 26 | 0.0049427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2054-36_0_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.02487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2054-36_0_2_line_27 | NAYY 4x150 SE | 27 | 28 | 0.024138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2054-36_0_2_line_28 | NAYY 4x150 SE | 28 | 32 | 0.017753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2054-36_0_2_line_29 | NAYY 4x150 SE | 29 | 30 | 0.019305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2054-36_0_2_line_30 | NAYY 4x150 SE | 29 | 31 | 0.0057473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2054-36_0_2_line_31 | NAYY 4x150 SE | 30 | 36 | 0.019657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2054-36_0_2_line_32 | NAYY 4x150 SE | 31 | 33 | 0.0090683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2054-36_0_2_line_33 | NAYY 4x150 SE | 32 | 39 | 0.011467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2054-36_0_2_line_34 | NAYY 4x150 SE | 32 | 41 | 0.056295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2054-36_0_2_line_35 | NAYY 4x150 SE | 33 | 34 | 0.051763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2054-36_0_2_line_36 | NAYY 4x150 SE | 34 | 35 | 0.0023993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2054-36_0_2_line_37 | NAYY 4x150 SE | 35 | 37 | 0.042306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2054-36_0_2_line_38 | NAYY 4x150 SE | 36 | 38 | 0.035715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2054-36_0_2_line_39 | NAYY 4x150 SE | 36 | 39 | 0.011164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2054-36_0_2_line_40 | NAYY 4x150 SE | 38 | 40 | 0.0030958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2054-36_0_2_line_41 | NAYY 4x150 SE | 39 | 42 | 0.020096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2054-36_0_2_line_42 | NAYY 4x150 SE | 41 | 43 | 0.0095258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2054-36_0_2_line_43 | NAYY 4x150 SE | 42 | 44 | 0.013045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2054-36_0_2_line_44 | NAYY 4x150 SE | 43 | 45 | 0.0080701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2054-36_0_2_line_45 | NAYY 4x150 SE | 44 | 51 | 0.0093136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2054-36_0_2_line_46 | NAYY 4x150 SE | 45 | 47 | 0.022801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2054-36_0_2_line_47 | NAYY 4x150 SE | 45 | 46 | 0.032939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2054-36_0_2_line_48 | NAYY 4x150 SE | 48 | 49 | 0.016209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2054-36_0_2_line_49 | NAYY 4x150 SE | 48 | 50 | 0.034251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2054-36_0_2_line_50 | NAYY 4x150 SE | 49 | 51 | 0.0064178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2054-36_0_2_trafo_31 | 0.25 MVA 20/0.4 kV | 52 | 38 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2560230.514 | 1189980.2116 | 2560249.578 | 1189980.7615
1 | 2560190.0936 | 1189979.0458 | 2560230.514 | 1189980.2116
2 | 2560249.578 | 1189980.7615 | 2560249.578 | 1189980.7615 | 2560249.5071 | 1189970.1118
3 | 2560190.0936 | 1189979.0458 | 2560192.6642 | 1189956.2829
4 | 2560190.0936 | 1189979.0458 | 2560189.2237 | 1189987.315
5 | 2560249.5071 | 1189970.1118 | 2560249.3955 | 1189953.3589 | 2560238.0259 | 1189953.9449
6 | 2560192.6642 | 1189956.2829 | 2560193.3824 | 1189951.0155
7 | 2560187.0459 | 1190008.0152 | 2560189.2237 | 1189987.315
8 | 2560193.3824 | 1189951.0155 | 2560195.7192 | 1189933.8782
9 | 2560187.0459 | 1190008.0152 | 2560154.7297 | 1189998.6691
10 | 2560198.0675 | 1189916.6575 | 2560195.7192 | 1189933.8782
11 | 2560129.8982 | 1189991.4877 | 2560154.7297 | 1189998.6691
12 | 2560032.9816 | 1189945.7447 | 2560032.7703 | 1189945.5938
13 | 2560056.561 | 1189962.5834 | 2560032.9816 | 1189945.7447
14 | 2560018.1139 | 1189935.1272 | 2560032.7703 | 1189945.5938
15 | 2560060.464 | 1189965.3707 | 2560056.561 | 1189962.5834
16 | 2560060.464 | 1189965.3707 | 2560049.0515 | 1189982.9455
17 | 2560060.464 | 1189965.3707 | 2560090.4094 | 1189980.0673 | 2560091.9902 | 1189980.5245
18 | 2560057.7901 | 1189987.4339 | 2560049.0515 | 1189982.9455
19 | 2560049.0515 | 1189982.9455 | 2560036.9004 | 1190002.8522
20 | 2560097.9742 | 1189982.2551 | 2560091.9902 | 1189980.5245
21 | 2560097.9742 | 1189982.2551 | 2560103.0394 | 1189983.72
22 | 2560129.8982 | 1189991.4877 | 2560123.6597 | 1189989.6835
23 | 2560103.0394 | 1189983.72 | 2560123.6597 | 1189989.6835
24 | 2560162.4322 | 1189778.9525 | 2560179.1975 | 1189800.535
25 | 2560182.2296 | 1189804.4383 | 2560179.1975 | 1189800.535
26 | 2560197.4865 | 1189824.0788 | 2560182.2296 | 1189804.4383
27 | 2560197.4865 | 1189824.0788 | 2560210.256 | 1189844.5626
28 | 2560219.648 | 1189859.6283 | 2560210.256 | 1189844.5626
29 | 2560173.4558 | 1189862.7157 | 2560190.8958 | 1189870.9941
30 | 2560173.4558 | 1189862.7157 | 2560170.7729 | 1189867.7983
31 | 2560208.6538 | 1189879.4234 | 2560190.8958 | 1189870.9941
32 | 2560166.5397 | 1189875.818 | 2560170.7729 | 1189867.7983
33 | 2560214.0793 | 1189869.6597 | 2560219.648 | 1189859.6283
34 | 2560219.648 | 1189859.6283 | 2560262.0695 | 1189822.6207
35 | 2560133.755 | 1189878.098 | 2560144.4471 | 1189884.4321 | 2560153.8606 | 1189896.3313 | 2560161.3541 | 1189885.6422 | 2560166.5397 | 1189875.818
36 | 2560131.6907 | 1189876.8751 | 2560133.755 | 1189878.098
37 | 2560131.6907 | 1189876.8751 | 2560116.3337 | 1189867.7775 | 2560109.5488 | 1189850.9803 | 2560104.2008 | 1189848.3591 | 2560103.8169 | 1189848.3902
38 | 2560208.6538 | 1189879.4234 | 2560199.1491 | 1189908.7249 | 2560198.4857 | 1189913.5901
39 | 2560208.6538 | 1189879.4234 | 2560214.0793 | 1189869.6597
40 | 2560198.4857 | 1189913.5901 | 2560198.0675 | 1189916.6575
41 | 2560214.0793 | 1189869.6597 | 2560231.66 | 1189879.3936
42 | 2560262.0695 | 1189822.6207 | 2560269.2478 | 1189816.3585
43 | 2560231.66 | 1189879.3936 | 2560243.0722 | 1189885.7123
44 | 2560275.329 | 1189811.0534 | 2560269.2478 | 1189816.3585
45 | 2560251.2203 | 1189890.2236 | 2560243.0722 | 1189885.7123
46 | 2560275.329 | 1189811.0534 | 2560289.3304 | 1189793.0571
47 | 2560275.329 | 1189811.0534 | 2560308.0253 | 1189815.0471
48 | 2560272.0452 | 1189898.9342 | 2560256.835 | 1189893.3323
49 | 2560304.1854 | 1189910.7713 | 2560272.0452 | 1189898.9342
50 | 2560256.835 | 1189893.3323 | 2560256.835 | 1189893.3323 | 2560251.2203 | 1189890.2236

## bus_geodata
| x | y | coords
0 | 2560230.514 | 1189980.2116
1 | 2560249.578 | 1189980.7615
2 | 2560190.0936 | 1189979.0458
3 | 2560249.5071 | 1189970.1118
4 | 2560192.6642 | 1189956.2829
5 | 2560189.2237 | 1189987.315
6 | 2560238.0259 | 1189953.9449
7 | 2560193.3824 | 1189951.0155
8 | 2560187.0459 | 1190008.0152
9 | 2560195.7192 | 1189933.8782
10 | 2560154.7297 | 1189998.6691
11 | 2560032.9816 | 1189945.7447
12 | 2560032.7703 | 1189945.5938
13 | 2560056.561 | 1189962.5834
14 | 2560018.1139 | 1189935.1272
15 | 2560060.464 | 1189965.3707
16 | 2560049.0515 | 1189982.9455
17 | 2560091.9902 | 1189980.5245
18 | 2560057.7901 | 1189987.4339
19 | 2560036.9004 | 1190002.8522
20 | 2560097.9742 | 1189982.2551
21 | 2560129.8982 | 1189991.4877
22 | 2560123.6597 | 1189989.6835
23 | 2560103.0394 | 1189983.72
24 | 2560179.1975 | 1189800.535
25 | 2560162.4322 | 1189778.9525
26 | 2560182.2296 | 1189804.4383
27 | 2560197.4865 | 1189824.0788
28 | 2560210.256 | 1189844.5626
29 | 2560173.4558 | 1189862.7157
30 | 2560190.8958 | 1189870.9941
31 | 2560170.7729 | 1189867.7983
32 | 2560219.648 | 1189859.6283
33 | 2560166.5397 | 1189875.818
34 | 2560133.755 | 1189878.098
35 | 2560131.6907 | 1189876.8751
36 | 2560208.6538 | 1189879.4234
37 | 2560103.8169 | 1189848.3902
38 | 2560198.4857 | 1189913.5901
39 | 2560214.0793 | 1189869.6597
40 | 2560198.0675 | 1189916.6575
41 | 2560262.0695 | 1189822.6207
42 | 2560231.66 | 1189879.3936
43 | 2560269.2478 | 1189816.3585
44 | 2560243.0722 | 1189885.7123
45 | 2560275.329 | 1189811.0534
46 | 2560308.0253 | 1189815.0471
47 | 2560289.3304 | 1189793.0571
48 | 2560272.0452 | 1189898.9342
49 | 2560256.835 | 1189893.3323
50 | 2560304.1854 | 1189910.7713
51 | 2560251.2203 | 1189890.2236
52 | 2560208.6538 | 1189879.4234

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99068 | -0.065255 | 0.0091164 | 0.0022848
1 | 0.98974 | -0.071894 | 0.0030503 | 0.00076448
2 | 0.9932 | -0.047488 | 0 | 0
3 | 0.98926 | -0.075275 | 0.014371 | 0.0036017
4 | 0.99547 | -0.031538 | 0 | 0
5 | 0.99289 | -0.049646 | 0.00048949 | 0.00012268
6 | 0.98858 | -0.080092 | 0.016772 | 0.0042036
7 | 0.996 | -0.027848 | 0.0021708 | 0.00054406
8 | 0.99214 | -0.05495 | 0.0068647 | 0.0017205
9 | 0.99777 | -0.015492 | 0.004421 | 0.001108
10 | 0.99126 | -0.061191 | 0.0031274 | 0.00078379
11 | 0.98893 | -0.077617 | 0.0047542 | 0.0011915
12 | 0.98893 | -0.077626 | 0.0026481 | 0.00066367
13 | 0.98927 | -0.075239 | 0.0010569 | 0.00026489
14 | 0.98891 | -0.077743 | 0.00064004 | 0.00016041
15 | 0.98933 | -0.074794 | 0 | 0
16 | 0.98926 | -0.075271 | 0 | 0
17 | 0.9899 | -0.070748 | 0.001325 | 0.00033209
18 | 0.98925 | -0.075403 | 0.001329 | 0.00033308
19 | 0.98923 | -0.075485 | 0.00090037 | 0.00022566
20 | 0.99002 | -0.069945 | 0.00093271 | 0.00023376
21 | 0.99069 | -0.065172 | 0.0004197 | 0.00010519
22 | 0.99055 | -0.066145 | 0.00067819 | 0.00016997
23 | 0.99012 | -0.069215 | 0.00045037 | 0.00011287
24 | 0.99412 | -0.041188 | 0.0015644 | 0.00039208
25 | 0.99408 | -0.041488 | 0.0010835 | 0.00027154
26 | 0.99414 | -0.041056 | 0.0070488 | 0.0017666
27 | 0.99449 | -0.038621 | 0.0033749 | 0.00084583
28 | 0.99494 | -0.035436 | 0.0020519 | 0.00051426
29 | 0.99518 | -0.033722 | 0 | 0
30 | 0.99582 | -0.029282 | 0.0016233 | 0.00040683
31 | 0.995 | -0.035045 | 0.0032275 | 0.00080889
32 | 0.99533 | -0.032729 | 0 | 0
33 | 0.99474 | -0.036837 | 0.0060913 | 0.0015266
34 | 0.99374 | -0.043899 | 0.0088666 | 0.0022222
35 | 0.99372 | -0.044011 | 0.0032116 | 0.00080491
36 | 0.9965 | -0.024447 | 0 | 0
37 | 0.99364 | -0.044622 | 0.0014264 | 0.00035748
38 | 1 | 0 | -0.14622 | -0.036578
39 | 0.9958 | -0.029374 | 0 | 0
40 | 0.99966 | -0.0023515 | 0.00052128 | 0.00013065
41 | 0.9942 | -0.040633 | 0.0064176 | 0.0016084
42 | 0.99538 | -0.032373 | 0.0025056 | 0.00062797
43 | 0.9941 | -0.041354 | 0.0044411 | 0.001113
44 | 0.99515 | -0.033991 | 0.0013672 | 0.00034266
45 | 0.99406 | -0.041604 | 0 | 0
46 | 0.99395 | -0.042409 | 0.0024181 | 0.00060603
47 | 0.99404 | -0.04175 | 0.00063438 | 0.00015899
48 | 0.99486 | -0.035978 | 0.0013376 | 0.00033523
49 | 0.99491 | -0.035637 | 0.0074564 | 0.0018688
50 | 0.99483 | -0.036237 | 0.00074812 | 0.0001875
51 | 0.995 | -0.035019 | 0.0013983 | 0.00035045
52 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.034251 | 0.008591 | -0.03422 | -0.0085792 | 3.1501e-05 | 1.187e-05 | 0.051448 | 0.051448 | 0.051448 | 0.99068 | -0.065255 | 0.98974 | -0.071894 | 19.0549
1 | -0.043367 | -0.010876 | 0.043474 | 0.010916 | 0.00010707 | 4.066e-05 | 0.065141 | 0.065141 | 0.065141 | 0.99068 | -0.065255 | 0.9932 | -0.047488 | 24.1264
2 | 0.031169 | 0.0078147 | -0.031155 | -0.0078092 | 1.4594e-05 | 5.4764e-06 | 0.046862 | 0.046862 | 0.046862 | 0.98974 | -0.071894 | 0.98926 | -0.075275 | 17.3564
3 | -0.069162 | -0.01736 | 0.069315 | 0.017419 | 0.00015353 | 5.8754e-05 | 0.10363 | 0.10363 | 0.10363 | 0.9932 | -0.047488 | 0.99547 | -0.031538 | 38.3806
4 | 0.025687 | 0.0064438 | -0.025679 | -0.006441 | 7.6853e-06 | 2.8483e-06 | 0.038487 | 0.038487 | 0.038487 | 0.9932 | -0.047488 | 0.99289 | -0.049646 | 14.2544
5 | 0.016784 | 0.0042075 | -0.016772 | -0.0042036 | 1.1191e-05 | 3.9431e-06 | 0.025246 | 0.025246 | 0.025246 | 0.98926 | -0.075275 | 0.98858 | -0.080092 | 9.3503
6 | -0.069315 | -0.017419 | 0.069351 | 0.017433 | 3.5623e-05 | 1.3632e-05 | 0.10363 | 0.10363 | 0.10363 | 0.99547 | -0.031538 | 0.996 | -0.027848 | 38.3806
7 | 0.02519 | 0.0063183 | -0.025171 | -0.0063115 | 1.8512e-05 | 6.8511e-06 | 0.037753 | 0.037753 | 0.037753 | 0.99289 | -0.049646 | 0.99214 | -0.05495 | 13.9827
8 | -0.071522 | -0.017977 | 0.071645 | 0.018024 | 0.00012327 | 4.7185e-05 | 0.10687 | 0.10687 | 0.10687 | 0.996 | -0.027848 | 0.99777 | -0.015492 | 39.5818
9 | 0.018307 | 0.004591 | -0.018291 | -0.0045853 | 1.5826e-05 | 5.6529e-06 | 0.027458 | 0.027458 | 0.027458 | 0.99214 | -0.05495 | 0.99126 | -0.061191 | 10.1695
10 | -0.076066 | -0.019132 | 0.076205 | 0.019185 | 0.00013962 | 5.3473e-05 | 0.11346 | 0.11346 | 0.11346 | 0.99777 | -0.015492 | 0.99966 | -0.0023515 | 42.0237
11 | 0.015164 | 0.0038016 | -0.015155 | -0.0037987 | 8.3578e-06 | 2.8815e-06 | 0.022763 | 0.022763 | 0.022763 | 0.99126 | -0.061191 | 0.99069 | -0.065172 | 8.4308
12 | 0.0032881 | 0.00082385 | -0.0032881 | -0.00082386 | 3.9657e-09 | -1.806e-09 | 0.0049475 | 0.0049475 | 0.0049475 | 0.98893 | -0.077617 | 0.98893 | -0.077626 | 1.8324
13 | -0.0080424 | -0.0020154 | 0.008045 | 0.002016 | 2.6475e-06 | 6.4639e-07 | 0.012101 | 0.012101 | 0.012101 | 0.98893 | -0.077617 | 0.98927 | -0.075239 | 4.4819
14 | 0.00064005 | 0.00016018 | -0.00064004 | -0.00016041 | 1.0423e-08 | -2.2706e-07 | 0.00096299 | 0.00096307 | 0.00096307 | 0.98893 | -0.077626 | 0.98891 | -0.077743 | 0.35669
15 | -0.0091019 | -0.0022809 | 0.0091025 | 0.0022811 | 5.6094e-07 | 1.5416e-07 | 0.013691 | 0.013691 | 0.013691 | 0.98927 | -0.075239 | 0.98933 | -0.074794 | 5.0706
16 | 0.0022296 | 0.00055811 | -0.0022294 | -0.00055833 | 1.4692e-07 | -2.1236e-07 | 0.0033532 | 0.0033533 | 0.0033533 | 0.98933 | -0.074794 | 0.98926 | -0.075271 | 1.242
17 | -0.011332 | -0.0028392 | 0.011338 | 0.0028412 | 6.3448e-06 | 1.9906e-06 | 0.017044 | 0.017044 | 0.017044 | 0.98933 | -0.074794 | 0.9899 | -0.070748 | 6.3125
18 | 0.001329 | 0.00033296 | -0.001329 | -0.00033308 | 2.4442e-08 | -1.1645e-07 | 0.001999 | 0.0019991 | 0.0019991 | 0.98926 | -0.075271 | 0.98925 | -0.075403 | 0.74039
19 | 0.0009004 | 0.00022537 | -0.00090037 | -0.00022566 | 2.6692e-08 | -2.8916e-07 | 0.0013542 | 0.0013544 | 0.0013544 | 0.98926 | -0.075271 | 0.98923 | -0.075485 | 0.50161
20 | -0.012663 | -0.0031733 | 0.012665 | 0.0031737 | 1.4085e-06 | 4.6162e-07 | 0.019035 | 0.019035 | 0.019035 | 0.9899 | -0.070748 | 0.99002 | -0.069945 | 7.0502
21 | -0.013598 | -0.0034075 | 0.013599 | 0.0034079 | 1.3743e-06 | 4.6076e-07 | 0.020437 | 0.020437 | 0.020437 | 0.99002 | -0.069945 | 0.99012 | -0.069215 | 7.5694
22 | 0.014735 | 0.0036935 | -0.014733 | -0.0036928 | 1.9851e-06 | 6.7989e-07 | 0.022133 | 0.022133 | 0.022133 | 0.99069 | -0.065172 | 0.99055 | -0.066145 | 8.1973
23 | 0.014055 | 0.0035228 | -0.014049 | -0.0035208 | 5.9713e-06 | 2.0204e-06 | 0.021114 | 0.021114 | 0.021114 | 0.99055 | -0.066145 | 0.99012 | -0.069215 | 7.8201
24 | 0.0010835 | 0.0002712 | -0.0010835 | -0.00027154 | 4.4851e-08 | -3.3707e-07 | 0.0016217 | 0.0016218 | 0.0016218 | 0.99412 | -0.041188 | 0.99408 | -0.041488 | 0.60067
25 | -0.0026479 | -0.00066328 | 0.002648 | 0.00066324 | 4.8447e-08 | -4.5452e-08 | 0.0039633 | 0.0039633 | 0.0039633 | 0.99412 | -0.041188 | 0.99414 | -0.041056 | 1.4679
26 | -0.0096968 | -0.0024298 | 0.0097 | 0.0024308 | 3.2691e-06 | 9.3475e-07 | 0.014514 | 0.014514 | 0.014514 | 0.99414 | -0.041056 | 0.99449 | -0.038621 | 5.3755
27 | -0.013075 | -0.0032766 | 0.013081 | 0.0032785 | 5.7647e-06 | 1.9039e-06 | 0.019563 | 0.019563 | 0.019563 | 0.99449 | -0.038621 | 0.99494 | -0.035436 | 7.2457
28 | -0.015133 | -0.0037928 | 0.015138 | 0.0037947 | 5.6744e-06 | 1.9518e-06 | 0.022632 | 0.022632 | 0.022632 | 0.99494 | -0.035436 | 0.99533 | -0.032729 | 8.3823
29 | -0.022846 | -0.0057273 | 0.02286 | 0.0057324 | 1.4057e-05 | 5.1556e-06 | 0.03416 | 0.03416 | 0.03416 | 0.99518 | -0.033722 | 0.99582 | -0.029282 | 12.6519
30 | 0.022846 | 0.0057273 | -0.022842 | -0.0057258 | 4.1849e-06 | 1.5349e-06 | 0.03416 | 0.03416 | 0.03416 | 0.99518 | -0.033722 | 0.995 | -0.035045 | 12.6519
31 | -0.024483 | -0.0061393 | 0.0245 | 0.0061453 | 1.6418e-05 | 6.0588e-06 | 0.036586 | 0.036586 | 0.036586 | 0.99582 | -0.029282 | 0.9965 | -0.024447 | 13.5503
32 | 0.019614 | 0.0049169 | -0.019609 | -0.0049151 | 4.869e-06 | 1.7549e-06 | 0.029333 | 0.029333 | 0.029333 | 0.995 | -0.035045 | 0.99474 | -0.036837 | 10.8643
33 | -0.029066 | -0.0072858 | 0.029079 | 0.0072908 | 1.3511e-05 | 5.0475e-06 | 0.043454 | 0.043454 | 0.043454 | 0.99533 | -0.032729 | 0.9958 | -0.029374 | 16.0941
34 | 0.013928 | 0.0034911 | -0.013912 | -0.003486 | 1.523e-05 | 5.1269e-06 | 0.020822 | 0.020822 | 0.020822 | 0.99533 | -0.032729 | 0.9942 | -0.040633 | 7.7119
35 | 0.013518 | 0.0033885 | -0.013505 | -0.0033841 | 1.3208e-05 | 4.4087e-06 | 0.020222 | 0.020222 | 0.020222 | 0.99474 | -0.036837 | 0.99374 | -0.043899 | 7.4895
36 | 0.0046382 | 0.0011619 | -0.0046381 | -0.0011619 | 7.2212e-08 | -3.3098e-09 | 0.006945 | 0.006945 | 0.006945 | 0.99374 | -0.043899 | 0.99372 | -0.044011 | 2.5722
37 | 0.0014265 | 0.00035698 | -0.0014264 | -0.00035748 | 1.2044e-07 | -5.0171e-07 | 0.0021358 | 0.002136 | 0.002136 | 0.99372 | -0.044011 | 0.99364 | -0.044622 | 0.79112
38 | -0.068434 | -0.017163 | 0.068666 | 0.017252 | 0.00023274 | 8.9047e-05 | 0.10219 | 0.10219 | 0.10219 | 0.9965 | -0.024447 | 1 | 0 | 37.8489
39 | 0.043934 | 0.011018 | -0.043904 | -0.011007 | 2.9985e-05 | 1.1387e-05 | 0.065606 | 0.065606 | 0.065606 | 0.9965 | -0.024447 | 0.9958 | -0.029374 | 24.2987
40 | 0.076752 | 0.019326 | -0.076727 | -0.019316 | 2.5211e-05 | 9.656e-06 | 0.11424 | 0.11424 | 0.11424 | 1 | 0 | 0.99966 | -0.0023515 | 42.311
41 | 0.014825 | 0.0037157 | -0.014819 | -0.0037136 | 6.1536e-06 | 2.1055e-06 | 0.022153 | 0.022153 | 0.022153 | 0.9958 | -0.029374 | 0.99538 | -0.032373 | 8.2047
42 | 0.0074947 | 0.0018775 | -0.0074939 | -0.0018774 | 7.479e-07 | 1.6414e-07 | 0.011217 | 0.011217 | 0.011217 | 0.9942 | -0.040633 | 0.9941 | -0.041354 | 4.1545
43 | 0.012313 | 0.0030856 | -0.01231 | -0.0030847 | 2.7579e-06 | 8.9121e-07 | 0.018407 | 0.018407 | 0.018407 | 0.99538 | -0.032373 | 0.99515 | -0.033991 | 6.8174
44 | 0.0030529 | 0.00076434 | -0.0030528 | -0.00076441 | 1.0514e-07 | -6.4184e-08 | 0.0045694 | 0.0045694 | 0.0045694 | 0.9941 | -0.041354 | 0.99406 | -0.041604 | 1.6924
45 | 0.010943 | 0.002742 | -0.010941 | -0.0027416 | 1.556e-06 | 4.7747e-07 | 0.016363 | 0.016363 | 0.016363 | 0.99515 | -0.033991 | 0.995 | -0.035019 | 6.0602
46 | 0.00063439 | 0.0001587 | -0.00063438 | -0.00015899 | 1.2829e-08 | -2.9066e-07 | 0.00094951 | 0.00094962 | 0.00094962 | 0.99406 | -0.041604 | 0.99404 | -0.04175 | 0.35171
47 | 0.0024184 | 0.00060571 | -0.0024181 | -0.00060603 | 2.6935e-07 | -3.2338e-07 | 0.0036199 | 0.0036201 | 0.0036201 | 0.99406 | -0.041604 | 0.99395 | -0.042409 | 1.3408
48 | -0.0020857 | -0.00052229 | 0.0020858 | 0.00052212 | 9.8422e-08 | -1.7263e-07 | 0.0031195 | 0.0031194 | 0.0031195 | 0.99486 | -0.035978 | 0.99491 | -0.035637 | 1.1554
49 | 0.00074815 | 0.00018706 | -0.00074812 | -0.0001875 | 2.6758e-08 | -4.3443e-07 | 0.0011188 | 0.001119 | 0.001119 | 0.99486 | -0.035978 | 0.99483 | -0.036237 | 0.41445
50 | -0.0095423 | -0.0023909 | 0.0095431 | 0.0023911 | 8.1566e-07 | 2.3036e-07 | 0.014271 | 0.014271 | 0.014271 | 0.99491 | -0.035637 | 0.995 | -0.035019 | 5.2857

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15063 | 0.037683

## res_load
| p_mw | q_mvar
0 | 0.0091164 | 0.0022848
1 | 0.0030503 | 0.00076448
2 | 0.014371 | 0.0036017
3 | 0.00048949 | 0.00012268
4 | 0.016772 | 0.0042036
5 | 0.0021708 | 0.00054406
6 | 0.0068647 | 0.0017205
7 | 0.004421 | 0.001108
8 | 0.0031274 | 0.00078379
9 | 0.0047542 | 0.0011915
10 | 0.0026481 | 0.00066367
11 | 0.0010569 | 0.00026489
12 | 0.00064004 | 0.00016041
13 | 0.001325 | 0.00033209
14 | 0.001329 | 0.00033308
15 | 0.00090037 | 0.00022566
16 | 0.00093271 | 0.00023376
17 | 0.0004197 | 0.00010519
18 | 0.00067819 | 0.00016997
19 | 0.00045037 | 0.00011287
20 | 0.0015644 | 0.00039208
21 | 0.0010835 | 0.00027154
22 | 0.0070488 | 0.0017666
23 | 0.0033749 | 0.00084583
24 | 0.0020519 | 0.00051426
25 | 0.0016233 | 0.00040683
26 | 0.0032275 | 0.00080889
27 | 0.0060913 | 0.0015266
28 | 0.0088666 | 0.0022222
29 | 0.0032116 | 0.00080491
30 | 0.0014264 | 0.00035748
31 | 0.0044098 | 0.0011052
32 | 0.00052128 | 0.00013065
33 | 0.0064176 | 0.0016084
34 | 0.0025056 | 0.00062797
35 | 0.0044411 | 0.001113
36 | 0.0013672 | 0.00034266
37 | 0.0024181 | 0.00060603
38 | 0.00063438 | 0.00015899
39 | 0.0013376 | 0.00033523
40 | 0.0074564 | 0.0018688
41 | 0.00074812 | 0.0001875
42 | 0.0013983 | 0.00035045

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1