## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2054-37_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2054-37_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2054-37_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2054-37_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2054-37_0_3_node_35 | 0.4 | n |  | TRUE
5 | bus_LV_2054-37_0_3_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2054-37_0_3_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_2054-37_0_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_2054-37_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_2054-37_0_3_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_2054-37_0_3_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_2054-37_0_3_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_2054-37_0_3_node_72 | 0.4 | n |  | TRUE
13 | bus_LV_2054-37_0_3_node_88 | 0.4 | n |  | TRUE
14 | bus_LV_2054-37_0_3_node_46 | 0.4 | n |  | TRUE
15 | bus_LV_2054-37_0_3_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2054-37_0_3_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_2054-37_0_3_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_2054-37_0_3_node_113 | 0.4 | n |  | TRUE
19 | bus_LV_2054-37_0_3_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_2054-37_0_3_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_2054-37_0_3_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_2054-37_0_3_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_2054-37_0_3_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2054-37_0_3_node_59 | 0.4 | n |  | TRUE
25 | bus_LV_2054-37_0_3_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_2054-37_0_3_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_2054-37_0_3_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_2054-37_0_3_node_115 | 0.4 | n |  | TRUE
29 | bus_LV_2054-37_0_3_node_47 | 0.4 | n |  | TRUE
30 | bus_LV_2054-37_0_3_node_48 | 0.4 | n |  | TRUE
31 | bus_LV_2054-37_0_3_node_70 | 0.4 | n |  | TRUE
32 | bus_LV_2054-37_0_3_node_79 | 0.4 | n |  | TRUE
33 | bus_LV_2054-37_0_3_node_60 | 0.4 | n |  | TRUE
34 | bus_LV_2054-37_0_3_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_2054-37_0_3_node_62 | 0.4 | n |  | TRUE
36 | bus_LV_2054-37_0_3_node_63 | 0.4 | n |  | TRUE
37 | bus_LV_2054-37_0_3_node_64 | 0.4 | n |  | TRUE
38 | bus_LV_2054-37_0_3_node_65 | 0.4 | n |  | TRUE
39 | bus_LV_2054-37_0_3_node_114 | 0.4 | n |  | TRUE
40 | bus_LV_2054-37_0_3_node_116 | 0.4 | n |  | TRUE
41 | bus_LV_2054-37_0_3_node_71 | 0.4 | n |  | TRUE
42 | bus_LV_2054-37_0_3_node_73 | 0.4 | n |  | TRUE
43 | bus_LV_2054-37_0_3_node_89 | 0.4 | n |  | TRUE
44 | bus_MV_0_node_36 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2054-37_0_3_load_0 | 0 | 0.0020389 | 0.00051101 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2054-37_0_3_load_1 | 1 | 0.001867 | 0.00046791 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2054-37_0_3_load_2 | 2 | 0.0021713 | 0.00054418 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2054-37_0_3_load_3 | 3 | 0.0014945 | 0.00037456 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2054-37_0_3_load_35 | 4 | 0.0017404 | 0.0004362 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2054-37_0_3_load_9 | 5 | 0.0025705 | 0.00064424 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2054-37_0_3_load_10 | 6 | 0.001081 | 0.00027093 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2054-37_0_3_load_14 | 10 | 0.00084733 | 0.00021236 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2054-37_0_3_load_72 | 12 | 0.002686 | 0.00067316 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2054-37_0_3_load_88 | 13 | 0.0028088 | 0.00070395 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2054-37_0_3_load_46 | 14 | 0.0018317 | 0.00045906 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2054-37_0_3_load_15 | 15 | 0.0028875 | 0.00072368 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2054-37_0_3_load_16 | 16 | 0.00040375 | 0.00010119 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2054-37_0_3_load_17 | 17 | 0.0013819 | 0.00034634 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2054-37_0_3_load_113 | 18 | 0.00068614 | 0.00017196 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2054-37_0_3_load_18 | 19 | 0.0020033 | 0.00050208 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2054-37_0_3_load_19 | 21 | 0.0005087 | 0.00012749 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2054-37_0_3_load_20 | 22 | 0.00040015 | 0.00010029 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2054-37_0_3_load_21 | 23 | 0.00044503 | 0.00011153 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2054-37_0_3_load_32 | 25 | 0.00085631 | 0.00021461 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2054-37_0_3_load_33 | 26 | 0.0019396 | 0.00048611 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2054-37_0_3_load_34 | 27 | 0.0028375 | 0.00071114 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2054-37_0_3_load_115 | 28 | 0.0034002 | 0.00085218 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2054-37_0_3_load_47 | 29 | 0.0027343 | 0.00068529 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2054-37_0_3_load_48 | 30 | 0.0023512 | 0.00058927 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2054-37_0_3_load_70 | 31 | 0.0019016 | 0.00047658 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2054-37_0_3_load_79 | 32 | 0.0013625 | 0.00034148 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2054-37_0_3_load_60 | 33 | 0.001032 | 0.00025865 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2054-37_0_3_load_63 | 36 | 0.0011766 | 0.00029487 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2054-37_0_3_load_64 | 37 | 0.0039332 | 0.00098575 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2054-37_0_3_load_65 | 38 | 0.0036272 | 0.00090906 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2054-37_0_3_load_116 | 40 | 0.0022669 | 0.00056814 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2054-37_0_3_load_71 | 41 | 0.0027261 | 0.00068324 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2054-37_0_3_load_73 | 42 | 0.0024575 | 0.00061591 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2054-37_0_3_load_89 | 43 | 0.0032771 | 0.00082131 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2054-37_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2054-37_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.031954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2054-37_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.012011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2054-37_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.014435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2054-37_0_3_line_4 | NAYY 4x150 SE | 4 | 26 | 0.010422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2054-37_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.0024846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2054-37_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.026503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2054-37_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.021066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2054-37_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.022699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2054-37_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.044693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2054-37_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.020424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2054-37_0_3_line_11 | NAYY 4x150 SE | 8 | 12 | 0.064725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2054-37_0_3_line_12 | NAYY 4x150 SE | 9 | 13 | 0.047767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2054-37_0_3_line_13 | NAYY 4x150 SE | 10 | 14 | 0.021103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2054-37_0_3_line_14 | NAYY 4x150 SE | 11 | 28 | 0.062587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2054-37_0_3_line_15 | NAYY 4x150 SE | 11 | 27 | 0.019555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2054-37_0_3_line_16 | NAYY 4x150 SE | 12 | 41 | 0.0050917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2054-37_0_3_line_17 | NAYY 4x150 SE | 13 | 43 | 0.027207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2054-37_0_3_line_18 | NAYY 4x150 SE | 14 | 29 | 0.024839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2054-37_0_3_line_19 | NAYY 4x150 SE | 15 | 16 | 0.034071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2054-37_0_3_line_20 | NAYY 4x150 SE | 15 | 17 | 0.017687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2054-37_0_3_line_21 | NAYY 4x150 SE | 16 | 18 | 0.12444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2054-37_0_3_line_22 | NAYY 4x150 SE | 17 | 19 | 0.027777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2054-37_0_3_line_23 | NAYY 4x150 SE | 19 | 20 | 0.050778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2054-37_0_3_line_24 | NAYY 4x150 SE | 20 | 24 | 0.043527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2054-37_0_3_line_25 | NAYY 4x150 SE | 21 | 22 | 0.0039065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2054-37_0_3_line_26 | NAYY 4x150 SE | 22 | 23 | 0.024129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2054-37_0_3_line_27 | NAYY 4x150 SE | 23 | 24 | 0.036486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2054-37_0_3_line_28 | NAYY 4x150 SE | 24 | 32 | 0.028355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2054-37_0_3_line_29 | NAYY 4x150 SE | 25 | 26 | 0.020769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2054-37_0_3_line_30 | NAYY 4x150 SE | 25 | 27 | 0.0071236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2054-37_0_3_line_31 | NAYY 4x150 SE | 28 | 39 | 0.026791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2054-37_0_3_line_32 | NAYY 4x150 SE | 29 | 30 | 0.025515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2054-37_0_3_line_33 | NAYY 4x150 SE | 30 | 31 | 0.031383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2054-37_0_3_line_34 | NAYY 4x150 SE | 32 | 36 | 0.030073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2054-37_0_3_line_35 | NAYY 4x150 SE | 33 | 34 | 0.033534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2054-37_0_3_line_36 | NAYY 4x150 SE | 33 | 35 | 0.0098614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2054-37_0_3_line_37 | NAYY 4x150 SE | 34 | 36 | 0.022143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2054-37_0_3_line_38 | NAYY 4x150 SE | 35 | 37 | 0.018273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2054-37_0_3_line_39 | NAYY 4x150 SE | 35 | 38 | 0.019017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2054-37_0_3_line_40 | NAYY 4x150 SE | 37 | 39 | 0.016052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2054-37_0_3_line_41 | NAYY 4x150 SE | 38 | 40 | 0.018873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2054-37_0_3_line_42 | NAYY 4x150 SE | 41 | 42 | 0.015448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2054-37_0_3_trafo_36 | 0.25 MVA 20/0.4 kV | 44 | 11 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2559454.4446 | 1191493.8852 | 2559442.4596 | 1191486.7335 | 2559436.0783 | 1191482.9269
1 | 2559454.4446 | 1191493.8852 | 2559481.8845 | 1191510.2593
2 | 2559425.7628 | 1191476.7735 | 2559436.0783 | 1191482.9269
3 | 2559425.7628 | 1191476.7735 | 2559413.3657 | 1191469.3784
4 | 2559404.4155 | 1191464.0394 | 2559413.3657 | 1191469.3784
5 | 2559337.0309 | 1191474.715 | 2559338.5943 | 1191472.7839
6 | 2559320.3542 | 1191495.3135 | 2559337.0309 | 1191474.715
7 | 2559351.8499 | 1191456.411 | 2559338.5943 | 1191472.7839
8 | 2559320.3542 | 1191495.3135 | 2559299.7055 | 1191504.8706
9 | 2559320.3542 | 1191495.3135 | 2559356.9876 | 1191520.915
10 | 2559363.6677 | 1191439.7325 | 2559351.8499 | 1191456.411
11 | 2559351.8499 | 1191456.411 | 2559308.348 | 1191429.5482 | 2559297.5238 | 1191421.3194
12 | 2559299.7055 | 1191504.8706 | 2559262.0074 | 1191475.5355
13 | 2559374.2854 | 1191533.0036 | 2559356.9876 | 1191520.915
14 | 2559363.6677 | 1191439.7325 | 2559374.6816 | 1191411.3643 | 2559371.068 | 1191403.5401 | 2559350.6506 | 1191391.8303
15 | 2559363.6677 | 1191439.7325 | 2559380.4614 | 1191449.7504
16 | 2559293.4704 | 1191418.2379 | 2559297.5238 | 1191421.3194
17 | 2559240.5354 | 1191458.8269 | 2559262.0074 | 1191475.5355
18 | 2559374.2854 | 1191533.0036 | 2559394.6456 | 1191547.2325
19 | 2559532.5326 | 1191217.7841 | 2559561.7794 | 1191200.3073
20 | 2559532.5326 | 1191217.7841 | 2559517.3502 | 1191226.8565
21 | 2559561.7794 | 1191200.3073 | 2559683.6336 | 1191175.069
22 | 2559493.5059 | 1191241.105 | 2559517.3502 | 1191226.8565
23 | 2559449.9177 | 1191267.1517 | 2559493.5059 | 1191241.105
24 | 2559409.7479 | 1191284.1895 | 2559449.9177 | 1191267.1517
25 | 2559459.9946 | 1191324.6645 | 2559456.9524 | 1191322.2139
26 | 2559438.1617 | 1191307.0775 | 2559456.9524 | 1191322.2139
27 | 2559409.7479 | 1191284.1895 | 2559438.1617 | 1191307.0775
28 | 2559409.7479 | 1191284.1895 | 2559382.2091 | 1191290.9421
29 | 2559404.4155 | 1191464.0394 | 2559386.5792 | 1191453.3998
30 | 2559380.4614 | 1191449.7504 | 2559386.5792 | 1191453.3998
31 | 2559327.4104 | 1191378.5015 | 2559350.6506 | 1191391.8303
32 | 2559415.5594 | 1191561.8482 | 2559394.6456 | 1191547.2325
33 | 2559441.2835 | 1191579.8256 | 2559415.5594 | 1191561.8482
34 | 2559382.2091 | 1191290.9421 | 2559353.0015 | 1191298.1038
35 | 2559331.4956 | 1191303.377 | 2559337.5833 | 1191336.3536
36 | 2559334.4449 | 1191345.7023 | 2559337.5833 | 1191336.3536
37 | 2559331.4956 | 1191303.377 | 2559353.0015 | 1191298.1038
38 | 2559334.4449 | 1191345.7023 | 2559328.6311 | 1191363.0263
39 | 2559334.4449 | 1191345.7023 | 2559316.1437 | 1191340.5348
40 | 2559327.4104 | 1191378.5015 | 2559325.9565 | 1191370.9962 | 2559328.6311 | 1191363.0263
41 | 2559297.472 | 1191339.1729 | 2559310.9941 | 1191339.0807 | 2559316.1437 | 1191340.5348
42 | 2559281.1727 | 1191408.8889 | 2559293.4704 | 1191418.2379

## bus_geodata
| x | y | coords
0 | 2559454.4446 | 1191493.8852
1 | 2559436.0783 | 1191482.9269
2 | 2559481.8845 | 1191510.2593
3 | 2559425.7628 | 1191476.7735
4 | 2559413.3657 | 1191469.3784
5 | 2559337.0309 | 1191474.715
6 | 2559338.5943 | 1191472.7839
7 | 2559320.3542 | 1191495.3135
8 | 2559351.8499 | 1191456.411
9 | 2559299.7055 | 1191504.8706
10 | 2559356.9876 | 1191520.915
11 | 2559363.6677 | 1191439.7325
12 | 2559297.5238 | 1191421.3194
13 | 2559262.0074 | 1191475.5355
14 | 2559374.2854 | 1191533.0036
15 | 2559532.5326 | 1191217.7841
16 | 2559561.7794 | 1191200.3073
17 | 2559517.3502 | 1191226.8565
18 | 2559683.6336 | 1191175.069
19 | 2559493.5059 | 1191241.105
20 | 2559449.9177 | 1191267.1517
21 | 2559459.9946 | 1191324.6645
22 | 2559456.9524 | 1191322.2139
23 | 2559438.1617 | 1191307.0775
24 | 2559409.7479 | 1191284.1895
25 | 2559386.5792 | 1191453.3998
26 | 2559404.4155 | 1191464.0394
27 | 2559380.4614 | 1191449.7504
28 | 2559350.6506 | 1191391.8303
29 | 2559394.6456 | 1191547.2325
30 | 2559415.5594 | 1191561.8482
31 | 2559441.2835 | 1191579.8256
32 | 2559382.2091 | 1191290.9421
33 | 2559337.5833 | 1191336.3536
34 | 2559331.4956 | 1191303.377
35 | 2559334.4449 | 1191345.7023
36 | 2559353.0015 | 1191298.1038
37 | 2559328.6311 | 1191363.0263
38 | 2559316.1437 | 1191340.5348
39 | 2559327.4104 | 1191378.5015
40 | 2559297.472 | 1191339.1729
41 | 2559293.4704 | 1191418.2379
42 | 2559281.1727 | 1191408.8889
43 | 2559240.5354 | 1191458.8269
44 | 2559363.6677 | 1191439.7325

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9986 | -0.009819 | 0.0020389 | 0.00051101
1 | 0.99873 | -0.008917 | 0.001867 | 0.00046791
2 | 0.9985 | -0.010514 | 0.0021713 | 0.00054418
3 | 0.99883 | -0.008186 | 0.0014945 | 0.00037456
4 | 0.99899 | -0.0070918 | 0.0017404 | 0.0004362
5 | 0.99855 | -0.010122 | 0.0025705 | 0.00064424
6 | 0.99862 | -0.0096658 | 0.001081 | 0.00027093
7 | 0.99796 | -0.01431 | 0 | 0
8 | 0.9992 | -0.0055715 | 0 | 0
9 | 0.99776 | -0.015696 | 0 | 0
10 | 0.99734 | -0.018647 | 0.00084733 | 0.00021236
11 | 1 | 0 | -0.068735 | -0.017038
12 | 0.99848 | -0.01067 | 0.002686 | 0.00067316
13 | 0.99735 | -0.018614 | 0.0028088 | 0.00070395
14 | 0.99707 | -0.020517 | 0.0018317 | 0.00045906
15 | 0.9927 | -0.051308 | 0.0028875 | 0.00072368
16 | 0.99265 | -0.051689 | 0.00040375 | 0.00010119
17 | 0.99281 | -0.050593 | 0.0013819 | 0.00034634
18 | 0.99253 | -0.052562 | 0.00068614 | 0.00017196
19 | 0.99302 | -0.049081 | 0.0020033 | 0.00050208
20 | 0.99356 | -0.045288 | 0 | 0
21 | 0.99391 | -0.04278 | 0.0005087 | 0.00012749
22 | 0.99391 | -0.04276 | 0.00040015 | 0.00010029
23 | 0.99395 | -0.042538 | 0.00044503 | 0.00011153
24 | 0.99402 | -0.042037 | 0 | 0
25 | 0.99946 | -0.0037829 | 0.00085631 | 0.00021461
26 | 0.99913 | -0.0061205 | 0.0019396 | 0.00048611
27 | 0.99958 | -0.0029205 | 0.0028375 | 0.00071114
28 | 0.99771 | -0.016012 | 0.0034002 | 0.00085218
29 | 0.99683 | -0.022261 | 0.0027343 | 0.00068529
30 | 0.99667 | -0.023352 | 0.0023512 | 0.00058927
31 | 0.99659 | -0.023953 | 0.0019016 | 0.00047658
32 | 0.99437 | -0.039531 | 0.0013625 | 0.00034148
33 | 0.9957 | -0.030123 | 0.001032 | 0.00025865
34 | 0.99516 | -0.033939 | 0 | 0
35 | 0.99588 | -0.028899 | 0 | 0
36 | 0.99481 | -0.036461 | 0.0011766 | 0.00029487
37 | 0.99635 | -0.025547 | 0.0039332 | 0.00098575
38 | 0.99572 | -0.030027 | 0.0036272 | 0.00090906
39 | 0.99686 | -0.021972 | 0 | 0
40 | 0.99566 | -0.030458 | 0.0022669 | 0.00056814
41 | 0.99844 | -0.010935 | 0.0027261 | 0.00068324
42 | 0.99839 | -0.011315 | 0.0024575 | 0.00061591
43 | 0.99722 | -0.019509 | 0.0032771 | 0.00082131
44 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0042104 | -0.0010548 | 0.004211 | 0.0010548 | 5.2529e-07 | -7.7799e-08 | 0.0062739 | 0.0062738 | 0.0062739 | 0.9986 | -0.009819 | 0.99873 | -0.008917 | 2.3237
1 | 0.0021715 | 0.00054384 | -0.0021713 | -0.00054418 | 2.0876e-07 | -3.3771e-07 | 0.0032356 | 0.0032358 | 0.0032358 | 0.9986 | -0.009819 | 0.9985 | -0.010514 | 1.1984
2 | -0.006078 | -0.0015227 | 0.0060786 | 0.0015228 | 6.146e-07 | 7.9187e-08 | 0.0090554 | 0.0090553 | 0.0090554 | 0.99873 | -0.008917 | 0.99883 | -0.008186 | 3.3539
3 | -0.0075731 | -0.0018973 | 0.0075742 | 0.0018976 | 1.1465e-06 | 2.5198e-07 | 0.011282 | 0.011282 | 0.011282 | 0.99883 | -0.008186 | 0.99899 | -0.0070918 | 4.1784
4 | -0.0093147 | -0.0023338 | 0.0093159 | 0.0023341 | 1.2518e-06 | 3.4499e-07 | 0.013874 | 0.013874 | 0.013874 | 0.99899 | -0.0070918 | 0.99913 | -0.0061205 | 5.1386
5 | -0.018346 | -0.0045976 | 0.018347 | 0.0045981 | 1.1588e-06 | 4.1319e-07 | 0.027339 | 0.027339 | 0.027339 | 0.99855 | -0.010122 | 0.99862 | -0.0096658 | 10.1255
6 | 0.015776 | 0.0039534 | -0.015767 | -0.0039502 | 9.1396e-06 | 3.1687e-06 | 0.023508 | 0.023508 | 0.023508 | 0.99855 | -0.010122 | 0.99796 | -0.01431 | 8.7068
7 | -0.019428 | -0.004869 | 0.019439 | 0.0048729 | 1.1017e-05 | 3.9615e-06 | 0.02895 | 0.02895 | 0.02895 | 0.99862 | -0.0096658 | 0.9992 | -0.0055715 | 10.7221
8 | 0.0060899 | 0.0015255 | -0.0060887 | -0.0015254 | 1.1678e-06 | 1.5265e-07 | 0.0090802 | 0.0090803 | 0.0090803 | 0.99796 | -0.01431 | 0.99776 | -0.015696 | 3.3631
9 | 0.0096767 | 0.0024247 | -0.0096709 | -0.002423 | 5.8058e-06 | 1.6494e-06 | 0.014428 | 0.014429 | 0.014429 | 0.99796 | -0.01431 | 0.99734 | -0.018647 | 5.3439
10 | -0.027315 | -0.0068464 | 0.027336 | 0.0068542 | 2.1088e-05 | 7.843e-06 | 0.040678 | 0.040678 | 0.040678 | 0.9992 | -0.0055715 | 1 | 0 | 15.0658
11 | 0.0078755 | 0.0019735 | -0.0078699 | -0.0019722 | 5.5554e-06 | 1.2895e-06 | 0.011728 | 0.011728 | 0.011728 | 0.9992 | -0.0055715 | 0.99848 | -0.01067 | 4.3438
12 | 0.0060887 | 0.0015254 | -0.0060863 | -0.0015251 | 2.4576e-06 | 3.2164e-07 | 0.0090803 | 0.0090805 | 0.0090805 | 0.99776 | -0.015696 | 0.99735 | -0.018614 | 3.3631
13 | 0.0088235 | 0.0022107 | -0.0088212 | -0.0022101 | 2.2821e-06 | 6.0242e-07 | 0.013164 | 0.013164 | 0.013164 | 0.99734 | -0.018647 | 0.99707 | -0.020517 | 4.8757
14 | 0.025639 | 0.0064339 | -0.025582 | -0.0064129 | 5.6853e-05 | 2.1047e-05 | 0.038154 | 0.038154 | 0.038154 | 1 | 0 | 0.99771 | -0.016012 | 14.1312
15 | 0.01496 | 0.0037496 | -0.014954 | -0.0037476 | 6.0471e-06 | 2.0694e-06 | 0.022261 | 0.022262 | 0.022262 | 1 | 0 | 0.99958 | -0.0029205 | 8.245
16 | 0.005184 | 0.001299 | -0.0051838 | -0.001299 | 1.8963e-07 | 6.3408e-09 | 0.0077255 | 0.0077256 | 0.0077256 | 0.99848 | -0.01067 | 0.99844 | -0.010935 | 2.8613
17 | 0.0032775 | 0.00082111 | -0.0032771 | -0.00082131 | 4.0594e-07 | -1.9887e-07 | 0.0048898 | 0.00489 | 0.00489 | 0.99735 | -0.018614 | 0.99722 | -0.019509 | 1.8111
18 | 0.0069896 | 0.001751 | -0.0069879 | -0.0017507 | 1.6864e-06 | 3.2474e-07 | 0.010431 | 0.010431 | 0.010431 | 0.99707 | -0.020517 | 0.99683 | -0.022261 | 3.8633
19 | 0.00109 | 0.00027116 | -0.00109 | -0.00027158 | 5.6713e-08 | -4.1865e-07 | 0.0016332 | 0.0016333 | 0.0016333 | 0.9927 | -0.051308 | 0.99265 | -0.051689 | 0.60494
20 | -0.0039775 | -0.00099484 | 0.0039779 | 0.00099476 | 3.9221e-07 | -7.7834e-08 | 0.0059614 | 0.0059614 | 0.0059614 | 0.9927 | -0.051308 | 0.99281 | -0.050593 | 2.2079
21 | 0.00068623 | 0.00017039 | -0.00068614 | -0.00017196 | 8.2123e-08 | -1.5769e-06 | 0.0010281 | 0.0010287 | 0.0010287 | 0.99265 | -0.051689 | 0.99253 | -0.052562 | 0.38099
22 | -0.0053599 | -0.0013411 | 0.005361 | 0.0013412 | 1.1183e-06 | 7.0862e-08 | 0.0080326 | 0.0080324 | 0.0080326 | 0.99281 | -0.050593 | 0.99302 | -0.049081 | 2.975
23 | -0.0073643 | -0.0018432 | 0.0073681 | 0.0018441 | 3.8578e-06 | 8.2652e-07 | 0.011034 | 0.011034 | 0.011034 | 0.99302 | -0.049081 | 0.99356 | -0.045288 | 4.0868
24 | -0.0073681 | -0.0018441 | 0.0073714 | 0.0018448 | 3.3068e-06 | 7.0789e-07 | 0.011034 | 0.011034 | 0.011034 | 0.99356 | -0.045288 | 0.99402 | -0.042037 | 4.0867
25 | -0.0005087 | -0.00012749 | 0.0005087 | 0.00012744 | 1.4138e-09 | -5.0084e-08 | 0.00076158 | 0.00076157 | 0.00076158 | 0.99391 | -0.04278 | 0.99391 | -0.04276 | 0.28207
26 | -0.00090885 | -0.00022773 | 0.00090888 | 0.00022743 | 2.7873e-08 | -3.02e-07 | 0.0013606 | 0.0013605 | 0.0013606 | 0.99391 | -0.04276 | 0.99395 | -0.042538 | 0.50394
27 | -0.0013539 | -0.00033896 | 0.001354 | 0.00033852 | 9.3515e-08 | -4.3695e-07 | 0.0020268 | 0.0020266 | 0.0020268 | 0.99395 | -0.042538 | 0.99402 | -0.042037 | 0.75066
28 | -0.0087254 | -0.0021833 | 0.0087285 | 0.0021841 | 3.018e-06 | 7.931e-07 | 0.013061 | 0.01306 | 0.013061 | 0.99402 | -0.042037 | 0.99437 | -0.039531 | 4.8372
29 | 0.011259 | 0.0028214 | -0.011256 | -0.0028202 | 3.6415e-06 | 1.1285e-06 | 0.016763 | 0.016763 | 0.016763 | 0.99946 | -0.0037829 | 0.99913 | -0.0061205 | 6.2085
30 | -0.012116 | -0.003036 | 0.012117 | 0.0030364 | 1.4462e-06 | 4.6288e-07 | 0.018038 | 0.018038 | 0.018038 | 0.99946 | -0.0037829 | 0.99958 | -0.0029205 | 6.6806
31 | 0.022182 | 0.0055607 | -0.022164 | -0.005554 | 1.8297e-05 | 6.6879e-06 | 0.033083 | 0.033083 | 0.033083 | 0.99771 | -0.016012 | 0.99686 | -0.021972 | 12.253
32 | 0.0042536 | 0.0010654 | -0.0042529 | -0.0010655 | 6.4186e-07 | -8.5696e-08 | 0.0063493 | 0.0063494 | 0.0063494 | 0.99683 | -0.022261 | 0.99667 | -0.023352 | 2.3516
33 | 0.0019017 | 0.00047623 | -0.0019016 | -0.00047658 | 1.5786e-07 | -3.4824e-07 | 0.0028391 | 0.0028393 | 0.0028393 | 0.99667 | -0.023352 | 0.99659 | -0.023953 | 1.0516
34 | -0.010091 | -0.0025256 | 0.010095 | 0.0025268 | 4.2783e-06 | 1.2552e-06 | 0.015099 | 0.015099 | 0.015099 | 0.99437 | -0.039531 | 0.99481 | -0.036461 | 5.5923
35 | 0.011282 | 0.0028248 | -0.011276 | -0.0028229 | 5.9474e-06 | 1.8515e-06 | 0.016859 | 0.016859 | 0.016859 | 0.9957 | -0.030123 | 0.99516 | -0.033939 | 6.2441
36 | -0.012314 | -0.0030834 | 0.012316 | 0.0030841 | 2.0836e-06 | 6.7309e-07 | 0.018401 | 0.018401 | 0.018401 | 0.9957 | -0.030123 | 0.99588 | -0.028899 | 6.8152
37 | 0.011276 | 0.0028229 | -0.011272 | -0.0028217 | 3.9272e-06 | 1.2229e-06 | 0.016859 | 0.016859 | 0.016859 | 0.99516 | -0.033939 | 0.99481 | -0.036461 | 6.2441
38 | -0.018211 | -0.0045612 | 0.018219 | 0.0045642 | 8.4419e-06 | 3.009e-06 | 0.027209 | 0.027209 | 0.027209 | 0.99588 | -0.028899 | 0.99635 | -0.025547 | 10.0775
39 | 0.0058952 | 0.0014771 | -0.0058943 | -0.001477 | 9.2068e-07 | 1.0671e-07 | 0.0088083 | 0.0088084 | 0.0088084 | 0.99588 | -0.028899 | 0.99572 | -0.030027 | 3.2624
40 | -0.022153 | -0.00555 | 0.022164 | 0.005554 | 1.0963e-05 | 4.0073e-06 | 0.033083 | 0.033083 | 0.033083 | 0.99635 | -0.025547 | 0.99686 | -0.021972 | 12.2531
41 | 0.0022671 | 0.00056795 | -0.0022669 | -0.00056814 | 1.3517e-07 | -1.9348e-07 | 0.0033878 | 0.0033879 | 0.0033879 | 0.99572 | -0.030027 | 0.99566 | -0.030458 | 1.2548
42 | 0.0024576 | 0.00061576 | -0.0024575 | -0.00061591 | 1.2932e-07 | -1.5228e-07 | 0.0036627 | 0.0036627 | 0.0036627 | 0.99844 | -0.010935 | 0.99839 | -0.011315 | 1.3566

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.068735 | 0.017038

## res_load
| p_mw | q_mvar
0 | 0.0020389 | 0.00051101
1 | 0.001867 | 0.00046791
2 | 0.0021713 | 0.00054418
3 | 0.0014945 | 0.00037456
4 | 0.0017404 | 0.0004362
5 | 0.0025705 | 0.00064424
6 | 0.001081 | 0.00027093
7 | 0.00084733 | 0.00021236
8 | 0.002686 | 0.00067316
9 | 0.0028088 | 0.00070395
10 | 0.0018317 | 0.00045906
11 | 0.0028875 | 0.00072368
12 | 0.00040375 | 0.00010119
13 | 0.0013819 | 0.00034634
14 | 0.00068614 | 0.00017196
15 | 0.0020033 | 0.00050208
16 | 0.0005087 | 0.00012749
17 | 0.00040015 | 0.00010029
18 | 0.00044503 | 0.00011153
19 | 0.00085631 | 0.00021461
20 | 0.0019396 | 0.00048611
21 | 0.0028375 | 0.00071114
22 | 0.0034002 | 0.00085218
23 | 0.0027343 | 0.00068529
24 | 0.0023512 | 0.00058927
25 | 0.0019016 | 0.00047658
26 | 0.0013625 | 0.00034148
27 | 0.001032 | 0.00025865
28 | 0.0011766 | 0.00029487
29 | 0.0039332 | 0.00098575
30 | 0.0036272 | 0.00090906
31 | 0.0022669 | 0.00056814
32 | 0.0027261 | 0.00068324
33 | 0.0024575 | 0.00061591
34 | 0.0032771 | 0.00082131

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1