## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2054-41_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2054-41_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2054-41_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2054-41_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2054-41_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2054-41_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2054-41_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2054-41_0_2_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_2054-41_0_2_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_2054-41_0_2_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_2054-41_0_2_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_2054-41_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2054-41_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2054-41_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2054-41_0_2_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2054-41_0_2_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_2054-41_0_2_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_2054-41_0_2_node_31 | 0.4 | n |  | TRUE
18 | bus_LV_2054-41_0_2_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_2054-41_0_2_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2054-41_0_2_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2054-41_0_2_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2054-41_0_2_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2054-41_0_2_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2054-41_0_2_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_2054-41_0_2_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_2054-41_0_2_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_2054-41_0_2_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2054-41_0_2_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_2054-41_0_2_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_2054-41_0_2_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_2054-41_0_2_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_2054-41_0_2_node_25 | 0.4 | n |  | TRUE
33 | bus_MV_454_2_node_144 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2054-41_0_2_load_0 | 0 | 0.0019081 | 0.00047821 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2054-41_0_2_load_1 | 1 | 0.0010018 | 0.00025107 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2054-41_0_2_load_2 | 2 | 0.0017223 | 0.00043165 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2054-41_0_2_load_3 | 3 | 0.00075671 | 0.00018965 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2054-41_0_2_load_5 | 5 | 0.001369 | 0.00034309 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2054-41_0_2_load_6 | 6 | 0.00228 | 0.00057142 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2054-41_0_2_load_13 | 9 | 0.004243 | 0.0010634 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2054-41_0_2_load_7 | 12 | 0.00047006 | 0.00011781 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2054-41_0_2_load_8 | 13 | 0.0063511 | 0.0015917 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2054-41_0_2_load_19 | 15 | 0.0041443 | 0.0010387 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2054-41_0_2_load_16 | 16 | 0.0032234 | 0.00080786 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2054-41_0_2_load_31 | 17 | 0.0034428 | 0.00086285 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2054-41_0_2_load_29 | 18 | 0.0023633 | 0.00059231 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2054-41_0_2_load_15 | 19 | 0.003093 | 0.00077518 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2054-41_0_2_load_12 | 20 | 0.00064062 | 0.00016055 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2054-41_0_2_load_18 | 22 | 0.011637 | 0.0029165 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2054-41_0_2_load_21 | 23 | 0.0016757 | 0.00041998 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2054-41_0_2_load_22 | 24 | 0.0031057 | 0.00077836 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2054-41_0_2_load_20 | 25 | 0.0035745 | 0.00089587 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2054-41_0_2_load_32 | 26 | 0.010262 | 0.0025718 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2054-41_0_2_load_23 | 27 | 0.0068628 | 0.00172 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2054-41_0_2_load_33 | 28 | 0.009643 | 0.0024168 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2054-41_0_2_load_28 | 29 | 0.0039349 | 0.00098619 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2054-41_0_2_load_30 | 31 | 0.003274 | 0.00082054 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2054-41_0_2_load_25 | 32 | 0.0051906 | 0.0013009 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2054-41_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.029537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2054-41_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.028507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2054-41_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.026907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2054-41_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.049047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2054-41_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.040403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2054-41_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.03805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2054-41_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.035986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2054-41_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.02644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2054-41_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.14962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2054-41_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.021405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2054-41_0_2_line_10 | NAYY 4x150 SE | 8 | 11 | 0.025909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2054-41_0_2_line_11 | NAYY 4x150 SE | 9 | 20 | 0.025402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2054-41_0_2_line_12 | NAYY 4x150 SE | 10 | 17 | 0.032767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2054-41_0_2_line_13 | NAYY 4x150 SE | 10 | 18 | 0.028751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2054-41_0_2_line_14 | NAYY 4x150 SE | 11 | 14 | 0.010589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2054-41_0_2_line_15 | NAYY 4x150 SE | 11 | 13 | 0.030646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2054-41_0_2_line_16 | NAYY 4x150 SE | 12 | 13 | 0.0086491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2054-41_0_2_line_17 | NAYY 4x150 SE | 14 | 15 | 0.01375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2054-41_0_2_line_18 | NAYY 4x150 SE | 14 | 16 | 0.045978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2054-41_0_2_line_19 | NAYY 4x150 SE | 16 | 19 | 0.019571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2054-41_0_2_line_20 | NAYY 4x150 SE | 18 | 31 | 0.014055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2054-41_0_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.026246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2054-41_0_2_line_22 | NAYY 4x150 SE | 21 | 22 | 0.026537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2054-41_0_2_line_23 | NAYY 4x150 SE | 22 | 25 | 0.018309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2054-41_0_2_line_24 | NAYY 4x150 SE | 22 | 24 | 0.047346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2054-41_0_2_line_25 | NAYY 4x150 SE | 23 | 24 | 0.021065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2054-41_0_2_line_26 | NAYY 4x150 SE | 24 | 27 | 0.0064619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2054-41_0_2_line_27 | NAYY 4x150 SE | 25 | 26 | 0.019655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2054-41_0_2_line_28 | NAYY 4x150 SE | 26 | 28 | 0.036672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2054-41_0_2_line_29 | NAYY 4x150 SE | 27 | 29 | 0.046568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2054-41_0_2_line_30 | NAYY 4x150 SE | 29 | 30 | 0.032856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2054-41_0_2_line_31 | NAYY 4x150 SE | 30 | 32 | 0.01782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2054-41_0_2_trafo_15 | 0.25 MVA 20/0.4 kV | 33 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2557817.2092 | 1187510.5578 | 2557798.7596 | 1187533.6238
1 | 2557817.2092 | 1187510.5578 | 2557835.0152 | 1187488.2964
2 | 2557781.9527 | 1187554.6361 | 2557798.7596 | 1187533.6238
3 | 2557865.6516 | 1187449.9944 | 2557835.0152 | 1187488.2964
4 | 2557781.9527 | 1187554.6361 | 2557756.7162 | 1187586.1873
5 | 2557865.6516 | 1187449.9944 | 2557841.0497 | 1187461.0295 | 2557830.1356 | 1187462.9795
6 | 2557734.2381 | 1187614.2898 | 2557756.7162 | 1187586.1873
7 | 2557803.7406 | 1187463.7833 | 2557814.1009 | 1187463.799 | 2557827.6396 | 1187463.4254 | 2557830.1356 | 1187462.9795
8 | 2557734.2381 | 1187614.2898 | 2557750.3201 | 1187763.0409
9 | 2557803.7406 | 1187463.7833 | 2557787.847 | 1187449.3989
10 | 2557777.7561 | 1187463.7557 | 2557803.7406 | 1187463.7833
11 | 2557750.3201 | 1187763.0409 | 2557753.0505 | 1187788.296
12 | 2557787.847 | 1187449.3989 | 2557784.1101 | 1187446.3569 | 2557787.3618 | 1187434.7276 | 2557774.7058 | 1187425.0896
13 | 2557787.847 | 1187449.3989 | 2557797.0916 | 1187422.1743
14 | 2557767.1368 | 1187463.7753 | 2557777.7561 | 1187463.7557
15 | 2557777.7561 | 1187463.7557 | 2557775.8771 | 1187469.9057 | 2557764.7738 | 1187491.425
16 | 2557760.8079 | 1187499.1112 | 2557764.7738 | 1187491.425
17 | 2557767.1368 | 1187463.7753 | 2557755.9872 | 1187455.7292
18 | 2557767.1368 | 1187463.7753 | 2557734.6361 | 1187464.6834 | 2557721.2393 | 1187466.0376
19 | 2557721.2393 | 1187466.0376 | 2557720.7995 | 1187466.0821 | 2557706.8883 | 1187469.8826 | 2557702.5233 | 1187471.645
20 | 2557786.2637 | 1187413.2126 | 2557797.0916 | 1187422.1743
21 | 2557678.4732 | 1187482.1127 | 2557687.0183 | 1187477.9054 | 2557702.5233 | 1187471.645
22 | 2557678.4732 | 1187482.1127 | 2557661.7961 | 1187473.4817 | 2557655.0312 | 1187469.6821
23 | 2557639.068 | 1187460.7163 | 2557655.0312 | 1187469.6821
24 | 2557655.0312 | 1187469.6821 | 2557675.0675 | 1187426.7845
25 | 2557694.3751 | 1187418.3599 | 2557675.0675 | 1187426.7845 | 2557675.0675 | 1187426.7845
26 | 2557669.0952 | 1187424.3171 | 2557675.0675 | 1187426.7845
27 | 2557639.068 | 1187460.7163 | 2557624.5403 | 1187452.5567 | 2557621.9278 | 1187451.0974
28 | 2557621.9278 | 1187451.0974 | 2557589.9123 | 1187433.2139
29 | 2557638.4717 | 1187389.2346 | 2557669.0952 | 1187424.3171
30 | 2557638.4717 | 1187389.2346 | 2557647.1444 | 1187389.0174 | 2557652.8382 | 1187387.2094 | 2557656.0271 | 1187383.9851 | 2557658.5105 | 1187378.0754 | 2557659.5577 | 1187370.8418
31 | 2557659.5577 | 1187370.8418 | 2557662.102 | 1187353.2043

## bus_geodata
| x | y | coords
0 | 2557817.2092 | 1187510.5578
1 | 2557798.7596 | 1187533.6238
2 | 2557835.0152 | 1187488.2964
3 | 2557781.9527 | 1187554.6361
4 | 2557865.6516 | 1187449.9944
5 | 2557756.7162 | 1187586.1873
6 | 2557830.1356 | 1187462.9795
7 | 2557734.2381 | 1187614.2898
8 | 2557803.7406 | 1187463.7833
9 | 2557750.3201 | 1187763.0409
10 | 2557787.847 | 1187449.3989
11 | 2557777.7561 | 1187463.7557
12 | 2557760.8079 | 1187499.1112
13 | 2557764.7738 | 1187491.425
14 | 2557767.1368 | 1187463.7753
15 | 2557755.9872 | 1187455.7292
16 | 2557721.2393 | 1187466.0376
17 | 2557774.7058 | 1187425.0896
18 | 2557797.0916 | 1187422.1743
19 | 2557702.5233 | 1187471.645
20 | 2557753.0505 | 1187788.296
21 | 2557678.4732 | 1187482.1127
22 | 2557655.0312 | 1187469.6821
23 | 2557694.3751 | 1187418.3599
24 | 2557675.0675 | 1187426.7845
25 | 2557639.068 | 1187460.7163
26 | 2557621.9278 | 1187451.0974
27 | 2557669.0952 | 1187424.3171
28 | 2557589.9123 | 1187433.2139
29 | 2557638.4717 | 1187389.2346
30 | 2557659.5577 | 1187370.8418
31 | 2557786.2637 | 1187413.2126
32 | 2557662.102 | 1187353.2043
33 | 2557702.5233 | 1187471.645

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99302 | -0.049022 | 0.0019081 | 0.00047821
1 | 0.99268 | -0.051426 | 0.0010018 | 0.00025107
2 | 0.99343 | -0.046152 | 0.0017223 | 0.00043165
3 | 0.99241 | -0.053344 | 0.00075671 | 0.00018965
4 | 0.99425 | -0.040366 | 0 | 0
5 | 0.99204 | -0.055914 | 0.001369 | 0.00034309
6 | 0.99488 | -0.035881 | 0.00228 | 0.00057142
7 | 0.99179 | -0.057703 | 0 | 0
8 | 0.99541 | -0.03216 | 0 | 0
9 | 0.99074 | -0.065139 | 0.004243 | 0.0010634
10 | 0.99513 | -0.034121 | 0 | 0
11 | 0.99627 | -0.026149 | 0 | 0
12 | 0.99596 | -0.028293 | 0.00047006 | 0.00011781
13 | 0.99597 | -0.028252 | 0.0063511 | 0.0015917
14 | 0.99672 | -0.022969 | 0 | 0
15 | 0.99664 | -0.023541 | 0.0041443 | 0.0010387
16 | 0.99896 | -0.0072847 | 0.0032234 | 0.00080786
17 | 0.99497 | -0.035258 | 0.0034428 | 0.00086285
18 | 0.9949 | -0.035755 | 0.0023633 | 0.00059231
19 | 1 | 0 | -0.094367 | -0.023503
20 | 0.99072 | -0.065305 | 0.00064062 | 0.00016055
21 | 0.9979 | -0.014677 | 0 | 0
22 | 0.99577 | -0.029579 | 0.011637 | 0.0029165
23 | 0.99431 | -0.039855 | 0.0016757 | 0.00041998
24 | 0.99436 | -0.039498 | 0.0031057 | 0.00077836
25 | 0.99516 | -0.03391 | 0.0035745 | 0.00089587
26 | 0.9946 | -0.037856 | 0.010262 | 0.0025718
27 | 0.99421 | -0.040542 | 0.0068628 | 0.00172
28 | 0.99409 | -0.041426 | 0.009643 | 0.0024168
29 | 0.9936 | -0.044838 | 0.0039349 | 0.00098619
30 | 0.99336 | -0.046564 | 0 | 0
31 | 0.99483 | -0.036219 | 0.003274 | 0.00082054
32 | 0.99323 | -0.0475 | 0.0051906 | 0.0013009
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0080241 | 0.0020088 | -0.0080214 | -0.0020082 | 2.6643e-06 | 6.4277e-07 | 0.012023 | 0.012023 | 0.012023 | 0.99302 | -0.049022 | 0.99268 | -0.051426 | 4.4531
1 | -0.0099322 | -0.002487 | 0.0099361 | 0.0024882 | 3.9398e-06 | 1.1464e-06 | 0.014882 | 0.014882 | 0.014882 | 0.99302 | -0.049022 | 0.99343 | -0.046152 | 5.512
2 | 0.0070197 | 0.0017571 | -0.0070178 | -0.0017567 | 1.8587e-06 | 3.6715e-07 | 0.010522 | 0.010522 | 0.010522 | 0.99268 | -0.051426 | 0.99241 | -0.053344 | 3.8969
3 | -0.011658 | -0.0029198 | 0.011668 | 0.0029228 | 9.3322e-06 | 2.9537e-06 | 0.017462 | 0.017462 | 0.017462 | 0.99343 | -0.046152 | 0.99425 | -0.040366 | 6.4674
4 | 0.0062611 | 0.0015671 | -0.0062589 | -0.0015667 | 2.2216e-06 | 3.3262e-07 | 0.0093871 | 0.0093873 | 0.0093873 | 0.99241 | -0.053344 | 0.99204 | -0.055914 | 3.4768
5 | -0.011668 | -0.0029228 | 0.011675 | 0.0029251 | 7.2396e-06 | 2.2907e-06 | 0.017462 | 0.017462 | 0.017462 | 0.99425 | -0.040366 | 0.99488 | -0.035881 | 6.4673
6 | 0.0048899 | 0.0012236 | -0.0048887 | -0.0012236 | 1.2078e-06 | 3.7365e-11 | 0.0073339 | 0.0073341 | 0.0073341 | 0.99204 | -0.055914 | 0.99179 | -0.057703 | 2.7163
7 | -0.013955 | -0.0034965 | 0.013962 | 0.0034989 | 7.1871e-06 | 2.4208e-06 | 0.020872 | 0.020872 | 0.020872 | 0.99488 | -0.035881 | 0.99541 | -0.03216 | 7.7303
8 | 0.0048887 | 0.0012236 | -0.0048837 | -0.0012236 | 5.0223e-06 | 2.9158e-09 | 0.0073341 | 0.0073348 | 0.0073348 | 0.99179 | -0.057703 | 0.99074 | -0.065139 | 2.7166
9 | 0.0090846 | 0.0022762 | -0.0090821 | -0.0022755 | 2.4633e-06 | 6.6924e-07 | 0.01358 | 0.01358 | 0.01358 | 0.99541 | -0.03216 | 0.99513 | -0.034121 | 5.0297
10 | -0.023047 | -0.005775 | 0.023066 | 0.0057821 | 1.9189e-05 | 7.0434e-06 | 0.034452 | 0.034452 | 0.034452 | 0.99541 | -0.03216 | 0.99627 | -0.026149 | 12.7599
11 | 0.00064063 | 0.00016023 | -0.00064062 | -0.00016055 | 1.4673e-08 | -3.2147e-07 | 0.00096207 | 0.00096218 | 0.00096218 | 0.99074 | -0.065139 | 0.99072 | -0.065305 | 0.35636
12 | 0.0034433 | 0.00086263 | -0.0034428 | -0.00086285 | 5.4203e-07 | -2.1716e-07 | 0.0051487 | 0.0051488 | 0.0051488 | 0.99513 | -0.034121 | 0.99497 | -0.035258 | 1.907
13 | 0.0056388 | 0.0014129 | -0.0056375 | -0.0014127 | 1.2755e-06 | 1.1711e-07 | 0.0084315 | 0.0084317 | 0.0084317 | 0.99513 | -0.034121 | 0.9949 | -0.035755 | 3.1228
14 | -0.029889 | -0.0074919 | 0.029902 | 0.0074968 | 1.3169e-05 | 4.9269e-06 | 0.044643 | 0.044643 | 0.044643 | 0.99627 | -0.026149 | 0.99672 | -0.022969 | 16.5343
15 | 0.0068232 | 0.0017098 | -0.0068212 | -0.0017094 | 1.986e-06 | 3.6493e-07 | 0.010191 | 0.010191 | 0.010191 | 0.99627 | -0.026149 | 0.99597 | -0.028252 | 3.7745
16 | -0.00047006 | -0.00011781 | 0.00047006 | 0.0001177 | 2.6618e-09 | -1.1153e-07 | 0.0007023 | 0.00070226 | 0.0007023 | 0.99596 | -0.028293 | 0.99597 | -0.028252 | 0.26011
17 | 0.0041447 | 0.0010386 | -0.0041443 | -0.0010387 | 3.2849e-07 | -5.2847e-08 | 0.0061876 | 0.0061876 | 0.0061876 | 0.99672 | -0.022969 | 0.99664 | -0.023541 | 2.2917
18 | -0.034047 | -0.0085354 | 0.034121 | 0.0085633 | 7.4127e-05 | 2.791e-05 | 0.05083 | 0.05083 | 0.05083 | 0.99672 | -0.022969 | 0.99896 | -0.0072847 | 18.826
19 | -0.037344 | -0.0093712 | 0.037382 | 0.0093855 | 3.7794e-05 | 1.428e-05 | 0.055631 | 0.055631 | 0.055631 | 0.99896 | -0.0072847 | 1 | 0 | 20.6042
20 | 0.0032742 | 0.00082044 | -0.003274 | -0.00082054 | 2.1033e-07 | -1.0161e-07 | 0.004897 | 0.004897 | 0.004897 | 0.9949 | -0.035755 | 0.99483 | -0.036219 | 1.8137
21 | 0.056184 | 0.014117 | -0.05607 | -0.014074 | 0.00011451 | 4.3697e-05 | 0.083616 | 0.083616 | 0.083616 | 1 | 0 | 0.9979 | -0.014677 | 30.9689
22 | 0.05607 | 0.014074 | -0.055954 | -0.014029 | 0.00011578 | 4.4183e-05 | 0.083616 | 0.083616 | 0.083616 | 0.9979 | -0.014677 | 0.99577 | -0.029579 | 30.969
23 | 0.023509 | 0.0058949 | -0.023495 | -0.0058897 | 1.41e-05 | 5.1852e-06 | 0.035131 | 0.035131 | 0.035131 | 0.99577 | -0.029579 | 0.99516 | -0.03391 | 13.0116
24 | 0.020808 | 0.0052179 | -0.02078 | -0.0052075 | 2.8567e-05 | 1.0372e-05 | 0.031095 | 0.031095 | 0.031095 | 0.99577 | -0.029579 | 0.99436 | -0.039498 | 11.5168
25 | -0.0016757 | -0.00041998 | 0.0016758 | 0.00041974 | 8.2664e-08 | -2.4145e-07 | 0.0025078 | 0.0025077 | 0.0025078 | 0.99431 | -0.039855 | 0.99436 | -0.039498 | 0.92881
26 | 0.015998 | 0.0040094 | -0.015996 | -0.0040086 | 2.311e-06 | 8.0504e-07 | 0.02394 | 0.02394 | 0.02394 | 0.99436 | -0.039498 | 0.99421 | -0.040542 | 8.8668
27 | 0.01992 | 0.0049939 | -0.019909 | -0.0049899 | 1.0882e-05 | 3.93e-06 | 0.029786 | 0.029787 | 0.029787 | 0.99516 | -0.03391 | 0.9946 | -0.037856 | 11.0321
28 | 0.0096478 | 0.0024181 | -0.009643 | -0.0024168 | 4.7676e-06 | 1.358e-06 | 0.014434 | 0.014434 | 0.014434 | 0.9946 | -0.037856 | 0.99409 | -0.041426 | 5.346
29 | 0.0091329 | 0.0022886 | -0.0091275 | -0.0022872 | 5.4293e-06 | 1.4847e-06 | 0.013669 | 0.013669 | 0.013669 | 0.99421 | -0.040542 | 0.9936 | -0.044838 | 5.0626
30 | 0.0051925 | 0.001301 | -0.0051913 | -0.0013009 | 1.2398e-06 | 5.1388e-08 | 0.0077762 | 0.0077763 | 0.0077763 | 0.9936 | -0.044838 | 0.99336 | -0.046564 | 2.8801
31 | 0.0051913 | 0.0013009 | -0.0051906 | -0.0013009 | 6.7243e-07 | 2.7966e-08 | 0.0077763 | 0.0077764 | 0.0077764 | 0.99336 | -0.046564 | 0.99323 | -0.0475 | 2.8802

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.09746 | 0.024278

## res_load
| p_mw | q_mvar
0 | 0.0019081 | 0.00047821
1 | 0.0010018 | 0.00025107
2 | 0.0017223 | 0.00043165
3 | 0.00075671 | 0.00018965
4 | 0.001369 | 0.00034309
5 | 0.00228 | 0.00057142
6 | 0.004243 | 0.0010634
7 | 0.00047006 | 0.00011781
8 | 0.0063511 | 0.0015917
9 | 0.0041443 | 0.0010387
10 | 0.0032234 | 0.00080786
11 | 0.0034428 | 0.00086285
12 | 0.0023633 | 0.00059231
13 | 0.003093 | 0.00077518
14 | 0.00064062 | 0.00016055
15 | 0.011637 | 0.0029165
16 | 0.0016757 | 0.00041998
17 | 0.0031057 | 0.00077836
18 | 0.0035745 | 0.00089587
19 | 0.010262 | 0.0025718
20 | 0.0068628 | 0.00172
21 | 0.009643 | 0.0024168
22 | 0.0039349 | 0.00098619
23 | 0.003274 | 0.00082054
24 | 0.0051906 | 0.0013009

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1