## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2055-15_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2055-15_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2055-15_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2055-15_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2055-15_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2055-15_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2055-15_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2055-15_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2055-15_0_3_node_133 | 0.4 | n |  | TRUE
9 | bus_LV_2055-15_0_3_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_2055-15_0_3_node_141 | 0.4 | n |  | TRUE
11 | bus_LV_2055-15_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2055-15_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2055-15_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2055-15_0_3_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_2055-15_0_3_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2055-15_0_3_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_2055-15_0_3_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_2055-15_0_3_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_2055-15_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2055-15_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2055-15_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2055-15_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2055-15_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2055-15_0_3_node_67 | 0.4 | n |  | TRUE
25 | bus_LV_2055-15_0_3_node_73 | 0.4 | n |  | TRUE
26 | bus_LV_2055-15_0_3_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_2055-15_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2055-15_0_3_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_2055-15_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2055-15_0_3_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_2055-15_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_2055-15_0_3_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_2055-15_0_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2055-15_0_3_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_2055-15_0_3_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_2055-15_0_3_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_2055-15_0_3_node_125 | 0.4 | n |  | TRUE
38 | bus_LV_2055-15_0_3_node_122 | 0.4 | n |  | TRUE
39 | bus_LV_2055-15_0_3_node_124 | 0.4 | n |  | TRUE
40 | bus_LV_2055-15_0_3_node_120 | 0.4 | n |  | TRUE
41 | bus_LV_2055-15_0_3_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_2055-15_0_3_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_2055-15_0_3_node_70 | 0.4 | n |  | TRUE
44 | bus_LV_2055-15_0_3_node_66 | 0.4 | n |  | TRUE
45 | bus_LV_2055-15_0_3_node_71 | 0.4 | n |  | TRUE
46 | bus_LV_2055-15_0_3_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_2055-15_0_3_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_2055-15_0_3_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_2055-15_0_3_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_2055-15_0_3_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_2055-15_0_3_node_112 | 0.4 | n |  | TRUE
52 | bus_LV_2055-15_0_3_node_113 | 0.4 | n |  | TRUE
53 | bus_LV_2055-15_0_3_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_2055-15_0_3_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_2055-15_0_3_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_2055-15_0_3_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_2055-15_0_3_node_42 | 0.4 | n |  | TRUE
58 | bus_LV_2055-15_0_3_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_2055-15_0_3_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_2055-15_0_3_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_2055-15_0_3_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_2055-15_0_3_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_2055-15_0_3_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_2055-15_0_3_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_2055-15_0_3_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_2055-15_0_3_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_2055-15_0_3_node_110 | 0.4 | n |  | TRUE
68 | bus_LV_2055-15_0_3_node_105 | 0.4 | n |  | TRUE
69 | bus_LV_2055-15_0_3_node_107 | 0.4 | n |  | TRUE
70 | bus_LV_2055-15_0_3_node_104 | 0.4 | n |  | TRUE
71 | bus_LV_2055-15_0_3_node_72 | 0.4 | n |  | TRUE
72 | bus_LV_2055-15_0_3_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_2055-15_0_3_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_2055-15_0_3_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_2055-15_0_3_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_2055-15_0_3_node_58 | 0.4 | n |  | TRUE
77 | bus_LV_2055-15_0_3_node_59 | 0.4 | n |  | TRUE
78 | bus_LV_2055-15_0_3_node_60 | 0.4 | n |  | TRUE
79 | bus_LV_2055-15_0_3_node_61 | 0.4 | n |  | TRUE
80 | bus_LV_2055-15_0_3_node_62 | 0.4 | n |  | TRUE
81 | bus_LV_2055-15_0_3_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_2055-15_0_3_node_96 | 0.4 | n |  | TRUE
83 | bus_LV_2055-15_0_3_node_97 | 0.4 | n |  | TRUE
84 | bus_LV_2055-15_0_3_node_69 | 0.4 | n |  | TRUE
85 | bus_LV_2055-15_0_3_node_65 | 0.4 | n |  | TRUE
86 | bus_LV_2055-15_0_3_node_98 | 0.4 | n |  | TRUE
87 | bus_LV_2055-15_0_3_node_99 | 0.4 | n |  | TRUE
88 | bus_LV_2055-15_0_3_node_64 | 0.4 | n |  | TRUE
89 | bus_LV_2055-15_0_3_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_2055-15_0_3_node_132 | 0.4 | n |  | TRUE
91 | bus_LV_2055-15_0_3_node_131 | 0.4 | n |  | TRUE
92 | bus_LV_2055-15_0_3_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_2055-15_0_3_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_2055-15_0_3_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_2055-15_0_3_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_2055-15_0_3_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_2055-15_0_3_node_79 | 0.4 | n |  | TRUE
98 | bus_LV_2055-15_0_3_node_80 | 0.4 | n |  | TRUE
99 | bus_LV_2055-15_0_3_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_2055-15_0_3_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_2055-15_0_3_node_83 | 0.4 | n |  | TRUE
102 | bus_LV_2055-15_0_3_node_84 | 0.4 | n |  | TRUE
103 | bus_LV_2055-15_0_3_node_90 | 0.4 | n |  | TRUE
104 | bus_LV_2055-15_0_3_node_85 | 0.4 | n |  | TRUE
105 | bus_LV_2055-15_0_3_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_2055-15_0_3_node_88 | 0.4 | n |  | TRUE
107 | bus_LV_2055-15_0_3_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_2055-15_0_3_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_2055-15_0_3_node_130 | 0.4 | n |  | TRUE
110 | bus_LV_2055-15_0_3_node_128 | 0.4 | n |  | TRUE
111 | bus_LV_2055-15_0_3_node_89 | 0.4 | n |  | TRUE
112 | bus_LV_2055-15_0_3_node_91 | 0.4 | n |  | TRUE
113 | bus_LV_2055-15_0_3_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_2055-15_0_3_node_92 | 0.4 | n |  | TRUE
115 | bus_LV_2055-15_0_3_node_95 | 0.4 | n |  | TRUE
116 | bus_LV_2055-15_0_3_node_100 | 0.4 | n |  | TRUE
117 | bus_LV_2055-15_0_3_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_2055-15_0_3_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_2055-15_0_3_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_2055-15_0_3_node_138 | 0.4 | n |  | TRUE
121 | bus_LV_2055-15_0_3_node_136 | 0.4 | n |  | TRUE
122 | bus_LV_2055-15_0_3_node_106 | 0.4 | n |  | TRUE
123 | bus_LV_2055-15_0_3_node_108 | 0.4 | n |  | TRUE
124 | bus_LV_2055-15_0_3_node_109 | 0.4 | n |  | TRUE
125 | bus_LV_2055-15_0_3_node_111 | 0.4 | n |  | TRUE
126 | bus_LV_2055-15_0_3_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_2055-15_0_3_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_2055-15_0_3_node_116 | 0.4 | n |  | TRUE
129 | bus_LV_2055-15_0_3_node_117 | 0.4 | n |  | TRUE
130 | bus_LV_2055-15_0_3_node_118 | 0.4 | n |  | TRUE
131 | bus_LV_2055-15_0_3_node_119 | 0.4 | n |  | TRUE
132 | bus_LV_2055-15_0_3_node_139 | 0.4 | n |  | TRUE
133 | bus_LV_2055-15_0_3_node_126 | 0.4 | n |  | TRUE
134 | bus_LV_2055-15_0_3_node_140 | 0.4 | n |  | TRUE
135 | bus_LV_2055-15_0_3_node_121 | 0.4 | n |  | TRUE
136 | bus_LV_2055-15_0_3_node_123 | 0.4 | n |  | TRUE
137 | bus_LV_2055-15_0_3_node_127 | 0.4 | n |  | TRUE
138 | bus_LV_2055-15_0_3_node_129 | 0.4 | n |  | TRUE
139 | bus_LV_2055-15_0_3_node_134 | 0.4 | n |  | TRUE
140 | bus_LV_2055-15_0_3_node_135 | 0.4 | n |  | TRUE
141 | bus_MV_454_0_node_286 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2055-15_0_3_load_0 | 0 | 0.002208 | 0.00055339 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2055-15_0_3_load_4 | 4 | 0.00038269 | 9.591e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2055-15_0_3_load_5 | 5 | 0.00095576 | 0.00023954 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2055-15_0_3_load_7 | 7 | 0.0016261 | 0.00040755 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2055-15_0_3_load_133 | 8 | 0.00038299 | 9.5986e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2055-15_0_3_load_14 | 9 | 0.00085705 | 0.0002148 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2055-15_0_3_load_141 | 10 | 0.00044479 | 0.00011148 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2055-15_0_3_load_8 | 11 | 0.00024599 | 6.165e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2055-15_0_3_load_9 | 12 | 0.00030419 | 7.6238e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2055-15_0_3_load_30 | 17 | 0.0020235 | 0.00050713 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2055-15_0_3_load_21 | 18 | 0.0018774 | 0.00047052 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2055-15_0_3_load_11 | 19 | 0.0022022 | 0.00055192 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2055-15_0_3_load_12 | 20 | 0.00078458 | 0.00019663 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2055-15_0_3_load_13 | 21 | 0.0028633 | 0.0007176 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2055-15_0_3_load_17 | 22 | 0.0025754 | 0.00064546 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2055-15_0_3_load_73 | 25 | 0.0022665 | 0.00056804 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2055-15_0_3_load_19 | 28 | 0.0031744 | 0.00079558 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2055-15_0_3_load_22 | 29 | 0.0019849 | 0.00049746 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2055-15_0_3_load_26 | 30 | 0.0016592 | 0.00041584 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2055-15_0_3_load_23 | 32 | 0.0015584 | 0.00039056 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2055-15_0_3_load_27 | 34 | 0.0014145 | 0.0003545 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2055-15_0_3_load_28 | 35 | 0.0011116 | 0.00027859 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2055-15_0_3_load_125 | 37 | 0.0013062 | 0.00032737 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2055-15_0_3_load_120 | 40 | 0.0010631 | 0.00026643 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2055-15_0_3_load_33 | 41 | 0.0018547 | 0.00046483 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2055-15_0_3_load_34 | 42 | 0.0027559 | 0.00069069 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2055-15_0_3_load_70 | 43 | 0.0010759 | 0.00026964 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2055-15_0_3_load_35 | 46 | 0.00099644 | 0.00024973 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2055-15_0_3_load_36 | 47 | 0.0024375 | 0.0006109 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2055-15_0_3_load_37 | 48 | 0.0024802 | 0.00062161 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2055-15_0_3_load_38 | 49 | 0.0027098 | 0.00067915 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2055-15_0_3_load_112 | 51 | 0.0022457 | 0.00056283 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2055-15_0_3_load_113 | 52 | 0.0025392 | 0.00063638 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2055-15_0_3_load_40 | 53 | 0.0021012 | 0.0005266 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2055-15_0_3_load_47 | 60 | 0.0021065 | 0.00052795 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2055-15_0_3_load_48 | 61 | 0.002859 | 0.00071655 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2055-15_0_3_load_49 | 62 | 0.0020873 | 0.00052313 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2055-15_0_3_load_50 | 63 | 0.0019296 | 0.00048361 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2055-15_0_3_load_52 | 65 | 0.0028714 | 0.00071964 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2055-15_0_3_load_53 | 66 | 0.0025052 | 0.00062785 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2055-15_0_3_load_110 | 67 | 0.0016562 | 0.00041509 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2055-15_0_3_load_107 | 69 | 0.0014219 | 0.00035637 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2055-15_0_3_load_104 | 70 | 0.0025599 | 0.00064158 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2055-15_0_3_load_72 | 71 | 0.0021219 | 0.00053179 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2055-15_0_3_load_54 | 72 | 0.0017938 | 0.00044957 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2055-15_0_3_load_57 | 75 | 0.0018156 | 0.00045504 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2055-15_0_3_load_58 | 76 | 0.0016016 | 0.0004014 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2055-15_0_3_load_59 | 77 | 0.0017994 | 0.00045098 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2055-15_0_3_load_62 | 80 | 0.0040895 | 0.0010249 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2055-15_0_3_load_96 | 82 | 0.0026403 | 0.00066171 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2055-15_0_3_load_69 | 84 | 0.0031293 | 0.00078429 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2055-15_0_3_load_65 | 85 | 0.00091843 | 0.00023018 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2055-15_0_3_load_98 | 86 | 0.0042743 | 0.0010712 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2055-15_0_3_load_99 | 87 | 0.0010467 | 0.00026232 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2055-15_0_3_load_64 | 88 | 0.001204 | 0.00030176 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2055-15_0_3_load_68 | 89 | 0.0027637 | 0.00069265 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2055-15_0_3_load_132 | 90 | 0.0012209 | 0.000306 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2055-15_0_3_load_131 | 91 | 0.0010759 | 0.00026964 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2055-15_0_3_load_74 | 92 | 0.00080926 | 0.00020282 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2055-15_0_3_load_75 | 93 | 0.00069327 | 0.00017375 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2055-15_0_3_load_77 | 95 | 0.0010261 | 0.00025716 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2055-15_0_3_load_78 | 96 | 0.00096516 | 0.00024189 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2055-15_0_3_load_79 | 97 | 0.0024141 | 0.00060503 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2055-15_0_3_load_80 | 98 | 0.0026588 | 0.00066636 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2055-15_0_3_load_81 | 99 | 0.0026284 | 0.00065875 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2055-15_0_3_load_82 | 100 | 0.0025749 | 0.00064533 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2055-15_0_3_load_83 | 101 | 0.0018331 | 0.00045942 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2055-15_0_3_load_84 | 102 | 0.00079283 | 0.0001987 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2055-15_0_3_load_85 | 104 | 0.001221 | 0.000306 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2055-15_0_3_load_93 | 105 | 0.0024767 | 0.00062071 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2055-15_0_3_load_88 | 106 | 0.0024559 | 0.0006155 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2055-15_0_3_load_86 | 107 | 0.0010759 | 0.00026964 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2055-15_0_3_load_128 | 110 | 0.001221 | 0.000306 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2055-15_0_3_load_89 | 111 | 0.00097915 | 0.0002454 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2055-15_0_3_load_91 | 112 | 0.0010811 | 0.00027095 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2055-15_0_3_load_94 | 113 | 0.00089824 | 0.00022512 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2055-15_0_3_load_92 | 114 | 0.00471 | 0.0011804 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2055-15_0_3_load_95 | 115 | 0.00099548 | 0.00024949 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2055-15_0_3_load_100 | 116 | 0.0010469 | 0.00026237 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2055-15_0_3_load_101 | 117 | 0.0028679 | 0.00071876 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2055-15_0_3_load_102 | 118 | 0.0013423 | 0.00033642 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2055-15_0_3_load_138 | 120 | 0.0013082 | 0.00032787 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2055-15_0_3_load_136 | 121 | 0.0013578 | 0.0003403 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2055-15_0_3_load_108 | 123 | 0.0021955 | 0.00055024 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2055-15_0_3_load_111 | 125 | 0.0015131 | 0.00037921 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2055-15_0_3_load_114 | 126 | 0.0017469 | 0.00043781 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2055-15_0_3_load_116 | 128 | 0.00171 | 0.00042858 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2055-15_0_3_load_118 | 130 | 0.0013168 | 0.00033002 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2055-15_0_3_load_139 | 132 | 0.00061689 | 0.00015461 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2055-15_0_3_load_126 | 133 | 0.0011694 | 0.00029308 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2055-15_0_3_load_140 | 134 | 0.0028151 | 0.00070552 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2055-15_0_3_load_121 | 135 | 0.0010762 | 0.00026972 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2055-15_0_3_load_123 | 136 | 0.0037901 | 0.00094989 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2055-15_0_3_load_127 | 137 | 0.0010969 | 0.00027492 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2055-15_0_3_load_129 | 138 | 0.0023799 | 0.00059645 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2055-15_0_3_load_134 | 139 | 0.0015863 | 0.00039756 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2055-15_0_3_load_135 | 140 | 0.0018829 | 0.00047189 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2055-15_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2055-15_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0088689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2055-15_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.01002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2055-15_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.030828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2055-15_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.042231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2055-15_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.049125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2055-15_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0068482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2055-15_0_3_line_7 | NAYY 4x150 SE | 6 | 10 | 0.011415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2055-15_0_3_line_8 | NAYY 4x150 SE | 7 | 11 | 0.0037728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2055-15_0_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.17472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2055-15_0_3_line_10 | NAYY 4x150 SE | 9 | 20 | 0.0096994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2055-15_0_3_line_11 | NAYY 4x150 SE | 9 | 22 | 0.13097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2055-15_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.013392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2055-15_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.021907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2055-15_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.046133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2055-15_0_3_line_15 | NAYY 4x150 SE | 14 | 18 | 0.013497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2055-15_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.031369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2055-15_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.053167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2055-15_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.023294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2055-15_0_3_line_19 | NAYY 4x150 SE | 16 | 24 | 0.035216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2055-15_0_3_line_20 | NAYY 4x150 SE | 16 | 25 | 0.0068787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_2055-15_0_3_line_21 | NAYY 4x150 SE | 17 | 26 | 0.0085438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2055-15_0_3_line_22 | NAYY 4x150 SE | 18 | 27 | 0.02502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2055-15_0_3_line_23 | NAYY 4x150 SE | 19 | 20 | 0.034173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2055-15_0_3_line_24 | NAYY 4x150 SE | 19 | 21 | 0.024331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2055-15_0_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.038154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2055-15_0_3_line_26 | NAYY 4x150 SE | 23 | 28 | 0.017129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2055-15_0_3_line_27 | NAYY 4x150 SE | 23 | 27 | 0.022752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2055-15_0_3_line_28 | NAYY 4x150 SE | 24 | 43 | 0.029628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2055-15_0_3_line_29 | NAYY 4x150 SE | 24 | 44 | 0.02078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2055-15_0_3_line_30 | NAYY 4x150 SE | 25 | 45 | 0.015509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_2055-15_0_3_line_31 | NAYY 4x150 SE | 26 | 41 | 0.021183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2055-15_0_3_line_32 | NAYY 4x150 SE | 27 | 29 | 0.0023701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2055-15_0_3_line_33 | NAYY 4x150 SE | 29 | 30 | 0.024481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2055-15_0_3_line_34 | NAYY 4x150 SE | 30 | 31 | 0.012973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2055-15_0_3_line_35 | NAYY 4x150 SE | 31 | 34 | 0.037088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2055-15_0_3_line_36 | NAYY 4x150 SE | 31 | 32 | 0.030491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2055-15_0_3_line_37 | NAYY 4x150 SE | 32 | 33 | 0.0085284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2055-15_0_3_line_38 | NAYY 4x150 SE | 33 | 35 | 0.007758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2055-15_0_3_line_39 | NAYY 4x150 SE | 33 | 36 | 0.02279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2055-15_0_3_line_40 | NAYY 4x150 SE | 36 | 37 | 0.007815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2055-15_0_3_line_41 | NAYY 4x150 SE | 36 | 38 | 0.004723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2055-15_0_3_line_42 | NAYY 4x150 SE | 38 | 39 | 0.016372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2055-15_0_3_line_43 | NAYY 4x150 SE | 38 | 40 | 0.016948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2055-15_0_3_line_44 | NAYY 4x150 SE | 39 | 133 | 0.006864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2055-15_0_3_line_45 | NAYY 4x150 SE | 39 | 131 | 0.012252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2055-15_0_3_line_46 | NAYY 4x150 SE | 40 | 135 | 0.0040424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2055-15_0_3_line_47 | NAYY 4x150 SE | 41 | 42 | 0.030512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2055-15_0_3_line_48 | NAYY 4x150 SE | 42 | 46 | 0.0018974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2055-15_0_3_line_49 | NAYY 4x150 SE | 43 | 90 | 0.010923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2055-15_0_3_line_50 | NAYY 4x150 SE | 44 | 89 | 0.005451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2055-15_0_3_line_51 | NAYY 4x150 SE | 44 | 88 | 0.018693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2055-15_0_3_line_52 | NAYY 4x150 SE | 45 | 71 | 0.013873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2055-15_0_3_line_53 | NAYY 4x150 SE | 45 | 66 | 0.014061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_2055-15_0_3_line_54 | NAYY 4x150 SE | 46 | 47 | 0.028249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2055-15_0_3_line_55 | NAYY 4x150 SE | 47 | 48 | 0.029157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2055-15_0_3_line_56 | NAYY 4x150 SE | 48 | 49 | 0.030083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2055-15_0_3_line_57 | NAYY 4x150 SE | 49 | 50 | 0.018873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2055-15_0_3_line_58 | NAYY 4x150 SE | 50 | 51 | 0.006614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2055-15_0_3_line_59 | NAYY 4x150 SE | 51 | 52 | 0.0050021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2055-15_0_3_line_60 | NAYY 4x150 SE | 53 | 54 | 0.0082293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2055-15_0_3_line_61 | NAYY 4x150 SE | 54 | 55 | 0.025404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_2055-15_0_3_line_62 | NAYY 4x150 SE | 54 | 56 | 0.004328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
63 | LV_2055-15_0_3_line_63 | NAYY 4x150 SE | 55 | 59 | 0.005355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
64 | LV_2055-15_0_3_line_64 | NAYY 4x150 SE | 55 | 60 | 0.013087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2055-15_0_3_line_65 | NAYY 4x150 SE | 56 | 61 | 0.013716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2055-15_0_3_line_66 | NAYY 4x150 SE | 56 | 57 | 0.005203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
67 | LV_2055-15_0_3_line_67 | NAYY 4x150 SE | 57 | 58 | 0.024429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2055-15_0_3_line_68 | NAYY 4x150 SE | 58 | 62 | 0.008976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2055-15_0_3_line_69 | NAYY 4x150 SE | 58 | 63 | 0.013379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2055-15_0_3_line_70 | NAYY 4x150 SE | 58 | 64 | 0.029915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2055-15_0_3_line_71 | NAYY 4x150 SE | 59 | 65 | 0.017178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2055-15_0_3_line_72 | NAYY 4x150 SE | 59 | 66 | 0.0059903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
73 | LV_2055-15_0_3_line_73 | NAYY 4x150 SE | 64 | 67 | 0.013799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2055-15_0_3_line_74 | NAYY 4x150 SE | 64 | 68 | 0.029426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2055-15_0_3_line_75 | NAYY 4x150 SE | 68 | 69 | 0.012603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2055-15_0_3_line_76 | NAYY 4x150 SE | 68 | 70 | 0.010633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2055-15_0_3_line_77 | NAYY 4x150 SE | 70 | 122 | 0.018454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2055-15_0_3_line_78 | NAYY 4x150 SE | 72 | 73 | 0.0087447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2055-15_0_3_line_79 | NAYY 4x150 SE | 72 | 74 | 0.020014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2055-15_0_3_line_80 | NAYY 4x150 SE | 73 | 75 | 0.008711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2055-15_0_3_line_81 | NAYY 4x150 SE | 73 | 76 | 0.020106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2055-15_0_3_line_82 | NAYY 4x150 SE | 74 | 77 | 0.010121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2055-15_0_3_line_83 | NAYY 4x150 SE | 74 | 78 | 0.027392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2055-15_0_3_line_84 | NAYY 4x150 SE | 76 | 79 | 0.0053288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2055-15_0_3_line_85 | NAYY 4x150 SE | 78 | 80 | 0.006459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2055-15_0_3_line_86 | NAYY 4x150 SE | 78 | 81 | 0.02363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2055-15_0_3_line_87 | NAYY 4x150 SE | 79 | 82 | 0.008997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2055-15_0_3_line_88 | NAYY 4x150 SE | 79 | 83 | 0.027154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2055-15_0_3_line_89 | NAYY 4x150 SE | 81 | 84 | 0.003749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2055-15_0_3_line_90 | NAYY 4x150 SE | 81 | 85 | 0.015884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2055-15_0_3_line_91 | NAYY 4x150 SE | 83 | 86 | 0.008237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2055-15_0_3_line_92 | NAYY 4x150 SE | 83 | 87 | 0.017208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2055-15_0_3_line_93 | NAYY 4x150 SE | 85 | 88 | 0.0080297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2055-15_0_3_line_94 | NAYY 4x150 SE | 87 | 116 | 0.0060113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2055-15_0_3_line_95 | NAYY 4x150 SE | 90 | 91 | 0.013428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2055-15_0_3_line_96 | NAYY 4x150 SE | 91 | 108 | 0.024145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2055-15_0_3_line_97 | NAYY 4x150 SE | 92 | 93 | 0.0072066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2055-15_0_3_line_98 | NAYY 4x150 SE | 92 | 94 | 0.0036061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2055-15_0_3_line_99 | NAYY 4x150 SE | 93 | 95 | 0.019511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2055-15_0_3_line_100 | NAYY 4x150 SE | 94 | 96 | 0.015767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2055-15_0_3_line_101 | NAYY 4x150 SE | 94 | 97 | 0.0077297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2055-15_0_3_line_102 | NAYY 4x150 SE | 95 | 98 | 0.0016627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2055-15_0_3_line_103 | NAYY 4x150 SE | 96 | 99 | 0.0097205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2055-15_0_3_line_104 | NAYY 4x150 SE | 97 | 100 | 0.0036642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2055-15_0_3_line_105 | NAYY 4x150 SE | 98 | 101 | 0.00063709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2055-15_0_3_line_106 | NAYY 4x150 SE | 99 | 102 | 0.0013138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2055-15_0_3_line_107 | NAYY 4x150 SE | 101 | 103 | 0.015572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2055-15_0_3_line_108 | NAYY 4x150 SE | 102 | 104 | 0.025261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2055-15_0_3_line_109 | NAYY 4x150 SE | 103 | 105 | 0.015685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2055-15_0_3_line_110 | NAYY 4x150 SE | 103 | 106 | 0.022442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2055-15_0_3_line_111 | NAYY 4x150 SE | 104 | 107 | 0.0021072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2055-15_0_3_line_112 | NAYY 4x150 SE | 106 | 111 | 0.021387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2055-15_0_3_line_113 | NAYY 4x150 SE | 106 | 112 | 0.019744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2055-15_0_3_line_114 | NAYY 4x150 SE | 107 | 108 | 0.013266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2055-15_0_3_line_115 | NAYY 4x150 SE | 108 | 109 | 0.024161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2055-15_0_3_line_116 | NAYY 4x150 SE | 109 | 110 | 0.014027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2055-15_0_3_line_117 | NAYY 4x150 SE | 110 | 137 | 0.0002755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2055-15_0_3_line_118 | NAYY 4x150 SE | 112 | 113 | 0.023541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2055-15_0_3_line_119 | NAYY 4x150 SE | 113 | 114 | 0.001799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2055-15_0_3_line_120 | NAYY 4x150 SE | 114 | 115 | 0.0059164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2055-15_0_3_line_121 | NAYY 4x150 SE | 116 | 117 | 0.036689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2055-15_0_3_line_122 | NAYY 4x150 SE | 117 | 118 | 0.00092525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2055-15_0_3_line_123 | NAYY 4x150 SE | 118 | 119 | 0.021576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2055-15_0_3_line_124 | NAYY 4x150 SE | 119 | 120 | 0.030461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_2055-15_0_3_line_125 | NAYY 4x150 SE | 120 | 121 | 0.005125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_2055-15_0_3_line_126 | NAYY 4x150 SE | 121 | 139 | 0.022635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_2055-15_0_3_line_127 | NAYY 4x150 SE | 122 | 123 | 0.013836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_2055-15_0_3_line_128 | NAYY 4x150 SE | 122 | 124 | 0.015981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_2055-15_0_3_line_129 | NAYY 4x150 SE | 124 | 125 | 0.0094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_2055-15_0_3_line_130 | NAYY 4x150 SE | 126 | 127 | 0.021455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_2055-15_0_3_line_131 | NAYY 4x150 SE | 127 | 128 | 0.015944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_2055-15_0_3_line_132 | NAYY 4x150 SE | 127 | 129 | 0.012508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_2055-15_0_3_line_133 | NAYY 4x150 SE | 129 | 130 | 0.006004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_2055-15_0_3_line_134 | NAYY 4x150 SE | 129 | 131 | 0.009787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_2055-15_0_3_line_135 | NAYY 4x150 SE | 131 | 132 | 0.030444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_2055-15_0_3_line_136 | NAYY 4x150 SE | 132 | 134 | 0.0038178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_2055-15_0_3_line_137 | NAYY 4x150 SE | 135 | 136 | 0.0077363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_2055-15_0_3_line_138 | NAYY 4x150 SE | 137 | 138 | 0.00097637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_2055-15_0_3_line_139 | NAYY 4x150 SE | 139 | 140 | 0.0050385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2055-15_0_3_trafo_42 | 0.25 MVA 20/0.4 kV | 141 | 57 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2550853.1334 | 1185710.1688 | 2550852.137 | 1185719.849 | 2550850.8257 | 1185731.4882
1 | 2550849.8327 | 1185740.3014 | 2550850.8257 | 1185731.4882
2 | 2550855.0443 | 1185700.3365 | 2550854.4541 | 1185702.8094 | 2550853.1334 | 1185710.1688
3 | 2550849.8327 | 1185740.3014 | 2550849.7617 | 1185740.9468 | 2550848.0461 | 1185749.4656 | 2550838.6225 | 1185760.727 | 2550835.5526 | 1185766.0219 | 2550835.2668 | 1185766.644
4 | 2550831.1133 | 1185734.7634 | 2550842.5741 | 1185715.1139 | 2550847.4547 | 1185707.2694 | 2550855.0443 | 1185700.3365
5 | 2550841.87 | 1185659.2223 | 2550854.1265 | 1185668.5488 | 2550857.5269 | 1185673.7237 | 2550859.6754 | 1185678.8644 | 2550858.9205 | 1185684.5071 | 2550855.0443 | 1185700.3365
6 | 2550832.1765 | 1185772.7413 | 2550833.236 | 1185771.0659 | 2550835.2668 | 1185766.644
7 | 2550835.5456 | 1185668.7351 | 2550841.87 | 1185659.2223
8 | 2550832.1765 | 1185772.7413 | 2550830.16 | 1185775.93
9 | 2550915.2639 | 1185913.9835 | 2551029.8452 | 1185782.0845
10 | 2550922.1027 | 1185920.8617 | 2550915.2639 | 1185913.9835
11 | 2550784.2999 | 1185913.3435 | 2550915.2639 | 1185913.9835
12 | 2550822.1914 | 1185786.6598 | 2550827.1793 | 1185780.6432 | 2550830.16 | 1185775.93
13 | 2550807.9365 | 1185803.2807 | 2550811.3944 | 1185799.6836 | 2550822.1914 | 1185786.6598
14 | 2550777.2829 | 1185834.8949 | 2550777.4779 | 1185832.6254 | 2550777.8188 | 1185828.6203 | 2550782.2336 | 1185827.2388 | 2550800.6705 | 1185811.4783 | 2550802.2727 | 1185809.5863 | 2550807.9365 | 1185803.2807
15 | 2550777.2829 | 1185834.8949 | 2550770.1546 | 1185846.3564
16 | 2550752.6427 | 1185826.66 | 2550754.2252 | 1185823.3118 | 2550771.9173 | 1185832.0041 | 2550774.4189 | 1185832.7617 | 2550776.349 | 1185832.6902 | 2550777.4779 | 1185832.6254 | 2550777.2829 | 1185834.8949
17 | 2550717.9332 | 1185797.6412 | 2550720.5661 | 1185793.9619 | 2550741.6528 | 1185814.5105 | 2550745.1619 | 1185818.0613 | 2550748.1473 | 1185820.1156 | 2550750.3413 | 1185821.4983 | 2550754.2252 | 1185823.3118 | 2550752.6427 | 1185826.66
18 | 2550752.6427 | 1185826.66 | 2550748.8777 | 1185834.6509 | 2550740.571 | 1185846.4878
19 | 2550698.7609 | 1185772.3632 | 2550720.5661 | 1185793.9619 | 2550717.9332 | 1185797.6412
20 | 2550717.9332 | 1185797.6412 | 2550713.9347 | 1185803.2385
21 | 2550735.6631 | 1185853.4813 | 2550740.571 | 1185846.4878
22 | 2550756.9407 | 1185867.6027 | 2550770.1546 | 1185846.3564
23 | 2550946.1973 | 1185945.0952 | 2550922.1027 | 1185920.8617
24 | 2550946.1973 | 1185945.0952 | 2550963.3522 | 1185962.349
25 | 2550772.3186 | 1185884.4075 | 2550790.7168 | 1185904.7338 | 2550784.2999 | 1185913.3435
26 | 2550763.4193 | 1185899.0555 | 2550772.3186 | 1185884.4075
27 | 2550756.9407 | 1185867.6027 | 2550772.3186 | 1185884.4075
28 | 2550698.7609 | 1185772.3632 | 2550687.1979 | 1185760.1407 | 2550677.9678 | 1185751.2683
29 | 2550698.7609 | 1185772.3632 | 2550686.5449 | 1185789.1954
30 | 2550704.9196 | 1185815.8585 | 2550713.9347 | 1185803.2385
31 | 2550735.6631 | 1185853.4813 | 2550723.4637 | 1185870.7987
32 | 2550756.9407 | 1185867.6027 | 2550755.5856 | 1185869.5471
33 | 2550741.589 | 1185889.6316 | 2550755.5856 | 1185869.5471
34 | 2550734.1718 | 1185900.2749 | 2550741.589 | 1185889.6316
35 | 2550754.6376 | 1185925.1755 | 2550756.8793 | 1185922.1776 | 2550757.5771 | 1185919.8039 | 2550756.8868 | 1185917.5306 | 2550755.5324 | 1185916.1521 | 2550734.1718 | 1185900.2749
36 | 2550734.1718 | 1185900.2749 | 2550716.7391 | 1185925.2906
37 | 2550711.8631 | 1185932.2876 | 2550716.7391 | 1185925.2906
38 | 2550705.2966 | 1185928.1283 | 2550711.8631 | 1185932.2876
39 | 2550698.8309 | 1185950.9831 | 2550707.0967 | 1185939.1307 | 2550711.8631 | 1185932.2876
40 | 2550692.4671 | 1185946.422 | 2550696.9348 | 1185949.6202 | 2550698.8309 | 1185950.9831
41 | 2550696.131 | 1185954.8631 | 2550698.8309 | 1185950.9831
42 | 2550686.6645 | 1185968.2374 | 2550696.131 | 1185954.8631
43 | 2550696.131 | 1185954.8631 | 2550709.9745 | 1185964.6396
44 | 2550681.0157 | 1185964.3152 | 2550686.6645 | 1185968.2374
45 | 2550686.6645 | 1185968.2374 | 2550679.643 | 1185978.2898
46 | 2550709.9745 | 1185964.6396 | 2550713.2765 | 1185966.9715
47 | 2550723.4637 | 1185870.7987 | 2550705.8914 | 1185895.7431
48 | 2550704.7986 | 1185897.2943 | 2550705.8914 | 1185895.7431
49 | 2550677.9678 | 1185751.2683 | 2550670.0932 | 1185743.6987
50 | 2550682.0323 | 1185786.1198 | 2550686.5449 | 1185789.1954
51 | 2550686.5449 | 1185789.1954 | 2550675.5707 | 1185804.3286
52 | 2550704.9196 | 1185815.8585 | 2550716.3553 | 1185823.7575
53 | 2550704.9196 | 1185815.8585 | 2550696.7461 | 1185827.3004
54 | 2550704.7986 | 1185897.2943 | 2550688.5299 | 1185920.3881
55 | 2550688.5299 | 1185920.3881 | 2550671.7382 | 1185944.2244
56 | 2550671.7382 | 1185944.2244 | 2550654.4132 | 1185968.8177
57 | 2550643.5442 | 1185984.2466 | 2550654.4132 | 1185968.8177
58 | 2550643.5442 | 1185984.2466 | 2550639.717 | 1185989.6409
59 | 2550636.8226 | 1185993.7206 | 2550639.717 | 1185989.6409
60 | 2550675.3544 | 1185857.2141 | 2550671.3331 | 1185854.4902 | 2550669.355 | 1185857.2215
61 | 2550690.1484 | 1185836.5362 | 2550675.3544 | 1185857.2141
62 | 2550672.85 | 1185860.7478 | 2550675.3544 | 1185857.2141
63 | 2550693.2641 | 1185832.1748 | 2550690.1484 | 1185836.5362
64 | 2550690.1484 | 1185836.5362 | 2550686.0717 | 1185833.5682 | 2550681.593 | 1185840.2501
65 | 2550678.8127 | 1185873.1054 | 2550672.85 | 1185860.7478
66 | 2550672.85 | 1185860.7478 | 2550669.8249 | 1185864.9862
67 | 2550655.6121 | 1185884.8811 | 2550669.8249 | 1185864.9862
68 | 2550655.6121 | 1185884.8811 | 2550652.633 | 1185882.6712 | 2550650.3882 | 1185877.8982
69 | 2550660.5606 | 1185897.3138 | 2550655.6121 | 1185884.8811
70 | 2550638.2008 | 1185909.2383 | 2550655.6121 | 1185884.8811
71 | 2550693.2641 | 1185832.1748 | 2550707.1225 | 1185842.3772
72 | 2550693.2641 | 1185832.1748 | 2550696.7461 | 1185827.3004
73 | 2550644.4455 | 1185921.5491 | 2550638.2008 | 1185909.2383
74 | 2550638.2008 | 1185909.2383 | 2550621.0839 | 1185933.204
75 | 2550626.0483 | 1185944.7916 | 2550621.0839 | 1185933.204
76 | 2550621.0839 | 1185933.204 | 2550614.9012 | 1185941.8545
77 | 2550604.1708 | 1185956.8679 | 2550614.9012 | 1185941.8545
78 | 2550614.669 | 1185888.3101 | 2550619.7871 | 1185881.2197
79 | 2550631.5013 | 1185864.9915 | 2550619.7871 | 1185881.2197
80 | 2550614.669 | 1185888.3101 | 2550610.8877 | 1185880.4592
81 | 2550614.669 | 1185888.3101 | 2550602.8657 | 1185904.5864
82 | 2550631.5013 | 1185864.9915 | 2550627.1371 | 1185855.8559
83 | 2550631.5013 | 1185864.9915 | 2550647.6489 | 1185842.8349
84 | 2550599.7373 | 1185908.9004 | 2550602.8657 | 1185904.5864
85 | 2550642.481 | 1185838.9421 | 2550647.6489 | 1185842.8349
86 | 2550661.5322 | 1185823.6875 | 2550647.6489 | 1185842.8349
87 | 2550599.7373 | 1185908.9004 | 2550595.186 | 1185901.1337
88 | 2550599.7373 | 1185908.9004 | 2550583.7795 | 1185930.8999
89 | 2550658.3864 | 1185821.6345 | 2550661.5322 | 1185823.6875
90 | 2550661.5322 | 1185823.6875 | 2550670.8567 | 1185810.829
91 | 2550581.0139 | 1185923.1407 | 2550583.7795 | 1185930.8999
92 | 2550583.7795 | 1185930.8999 | 2550574.0464 | 1185945.091
93 | 2550670.8567 | 1185810.829 | 2550675.5707 | 1185804.3286
94 | 2550570.6463 | 1185950.0483 | 2550574.0464 | 1185945.091
95 | 2550660.3132 | 1185734.4982 | 2550661.3376 | 1185735.4516 | 2550668.7363 | 1185742.3944 | 2550670.0932 | 1185743.6987
96 | 2550642.574 | 1185718.1192 | 2550646.2189 | 1185721.4687 | 2550653.1089 | 1185727.7931 | 2550660.3132 | 1185734.4982
97 | 2550600.1224 | 1185775.078 | 2550595.7699 | 1185780.8217
98 | 2550602.3004 | 1185772.2039 | 2550600.1224 | 1185775.078
99 | 2550595.7699 | 1185780.8217 | 2550591.4149 | 1185786.5684 | 2550589.9731 | 1185788.4703 | 2550583.9884 | 1185796.3737
100 | 2550602.3004 | 1185772.2039 | 2550608.5661 | 1185763.9476 | 2550611.8273 | 1185759.641
101 | 2550602.3004 | 1185772.2039 | 2550596.1868 | 1185767.4741
102 | 2550582.9847 | 1185797.6992 | 2550583.9884 | 1185796.3737
103 | 2550611.8273 | 1185759.641 | 2550617.6955 | 1185751.8916
104 | 2550593.9999 | 1185770.414 | 2550596.1868 | 1185767.4741 | 2550596.1868 | 1185767.4741
105 | 2550582.9847 | 1185797.6992 | 2550582.6001 | 1185798.2071
106 | 2550618.4886 | 1185750.8443 | 2550617.6955 | 1185751.8916
107 | 2550573.1997 | 1185810.6212 | 2550582.6001 | 1185798.2071
108 | 2550633.5327 | 1185730.5527 | 2550625.7549 | 1185741.2486 | 2550618.4886 | 1185750.8443
109 | 2550573.1997 | 1185810.6212 | 2550567.8144 | 1185809.9765 | 2550557.6272 | 1185808.7463
110 | 2550573.1997 | 1185810.6212 | 2550581.933 | 1185831.2937
111 | 2550633.5327 | 1185730.5527 | 2550634.772 | 1185728.8484
112 | 2550581.933 | 1185831.2937 | 2550581.933 | 1185831.2937 | 2550574.2288 | 1185841.841 | 2550569.8599 | 1185847.8248 | 2550569.3165 | 1185848.5631
113 | 2550581.933 | 1185831.2937 | 2550574.2288 | 1185841.841 | 2550570.2883 | 1185847.2381
114 | 2550642.574 | 1185718.1192 | 2550634.772 | 1185728.8484
115 | 2550642.574 | 1185718.1192 | 2550624.4847 | 1185702.0487
116 | 2550624.4847 | 1185702.0487 | 2550615.1127 | 1185712.4856
117 | 2550614.9286 | 1185712.6906 | 2550615.1127 | 1185712.4856
118 | 2550547.7691 | 1185844.6629 | 2550569.3165 | 1185848.5631 | 2550569.8599 | 1185847.8248 | 2550570.2883 | 1185847.2381
119 | 2550547.7691 | 1185844.6629 | 2550545.9989 | 1185844.3425 | 2550545.9989 | 1185844.3425
120 | 2550545.9989 | 1185844.3425 | 2550545.9989 | 1185844.3425 | 2550545.6097 | 1185843.423 | 2550543.6732 | 1185838.9024
121 | 2550570.6463 | 1185950.0483 | 2550570.2601 | 1185950.6115 | 2550565.6428 | 1185956.086 | 2550560.678 | 1185959.2066 | 2550552.0561 | 1185959.3557 | 2550537.7765 | 1185957.8641
122 | 2550537.7765 | 1185957.8641 | 2550536.8563 | 1185957.768
123 | 2550515.4733 | 1185958.4691 | 2550519.6679 | 1185957.2559 | 2550533.1224 | 1185957.378 | 2550536.8563 | 1185957.768
124 | 2550515.4733 | 1185958.4691 | 2550516.7826 | 1185953.4778 | 2550514.9911 | 1185949.0902 | 2550513.238 | 1185946.57 | 2550510.2707 | 1185943.9486 | 2550499.5194 | 1185935.7303
125 | 2550499.5194 | 1185935.7303 | 2550495.4477 | 1185932.6179
126 | 2550477.489 | 1185918.8399 | 2550485.5958 | 1185925.087 | 2550495.4477 | 1185932.6179
127 | 2550609.0016 | 1185969.8351 | 2550604.1708 | 1185956.8679
128 | 2550594.877 | 1185969.8852 | 2550604.1708 | 1185956.8679
129 | 2550587.0576 | 1185964.6359 | 2550594.877 | 1185969.8852
130 | 2550666.8671 | 1185996.5831 | 2550664.4303 | 1185999.9717 | 2550678.7923 | 1186009.583
131 | 2550666.8671 | 1185996.5831 | 2550673.9871 | 1186001.238 | 2550680.2401 | 1186005.322
132 | 2550666.8671 | 1185996.5831 | 2550674.0318 | 1185986.3183
133 | 2550669.2023 | 1185982.734 | 2550674.0318 | 1185986.3183
134 | 2550679.643 | 1185978.2898 | 2550674.0318 | 1185986.3183
135 | 2550679.643 | 1185978.2898 | 2550700.1378 | 1185992.8398 | 2550700.2127 | 1185994.5068 | 2550699.372 | 1185998.049
136 | 2550697.3536 | 1186001.2897 | 2550699.372 | 1185998.049
137 | 2550719.5958 | 1185971.4343 | 2550713.2765 | 1185966.9715
138 | 2550614.2763 | 1185713.417 | 2550614.9286 | 1185712.6906
139 | 2550477.489 | 1185918.8399 | 2550473.498 | 1185915.7644

## bus_geodata
| x | y | coords
0 | 2550850.8257 | 1185731.4882
1 | 2550853.1334 | 1185710.1688
2 | 2550849.8327 | 1185740.3014
3 | 2550855.0443 | 1185700.3365
4 | 2550835.2668 | 1185766.644
5 | 2550831.1133 | 1185734.7634
6 | 2550841.87 | 1185659.2223
7 | 2550832.1765 | 1185772.7413
8 | 2551029.8452 | 1185782.0845
9 | 2550915.2639 | 1185913.9835
10 | 2550835.5456 | 1185668.7351
11 | 2550830.16 | 1185775.93
12 | 2550822.1914 | 1185786.6598
13 | 2550807.9365 | 1185803.2807
14 | 2550777.2829 | 1185834.8949
15 | 2550752.6427 | 1185826.66
16 | 2550717.9332 | 1185797.6412
17 | 2550740.571 | 1185846.4878
18 | 2550770.1546 | 1185846.3564
19 | 2550946.1973 | 1185945.0952
20 | 2550922.1027 | 1185920.8617
21 | 2550963.3522 | 1185962.349
22 | 2550784.2999 | 1185913.3435
23 | 2550772.3186 | 1185884.4075
24 | 2550698.7609 | 1185772.3632
25 | 2550713.9347 | 1185803.2385
26 | 2550735.6631 | 1185853.4813
27 | 2550756.9407 | 1185867.6027
28 | 2550763.4193 | 1185899.0555
29 | 2550755.5856 | 1185869.5471
30 | 2550741.589 | 1185889.6316
31 | 2550734.1718 | 1185900.2749
32 | 2550716.7391 | 1185925.2906
33 | 2550711.8631 | 1185932.2876
34 | 2550754.6376 | 1185925.1755
35 | 2550705.2966 | 1185928.1283
36 | 2550698.8309 | 1185950.9831
37 | 2550692.4671 | 1185946.422
38 | 2550696.131 | 1185954.8631
39 | 2550686.6645 | 1185968.2374
40 | 2550709.9745 | 1185964.6396
41 | 2550723.4637 | 1185870.7987
42 | 2550705.8914 | 1185895.7431
43 | 2550677.9678 | 1185751.2683
44 | 2550686.5449 | 1185789.1954
45 | 2550704.9196 | 1185815.8585
46 | 2550704.7986 | 1185897.2943
47 | 2550688.5299 | 1185920.3881
48 | 2550671.7382 | 1185944.2244
49 | 2550654.4132 | 1185968.8177
50 | 2550643.5442 | 1185984.2466
51 | 2550639.717 | 1185989.6409
52 | 2550636.8226 | 1185993.7206
53 | 2550669.355 | 1185857.2215
54 | 2550675.3544 | 1185857.2141
55 | 2550690.1484 | 1185836.5362
56 | 2550672.85 | 1185860.7478
57 | 2550669.8249 | 1185864.9862
58 | 2550655.6121 | 1185884.8811
59 | 2550693.2641 | 1185832.1748
60 | 2550681.593 | 1185840.2501
61 | 2550678.8127 | 1185873.1054
62 | 2550650.3882 | 1185877.8982
63 | 2550660.5606 | 1185897.3138
64 | 2550638.2008 | 1185909.2383
65 | 2550707.1225 | 1185842.3772
66 | 2550696.7461 | 1185827.3004
67 | 2550644.4455 | 1185921.5491
68 | 2550621.0839 | 1185933.204
69 | 2550626.0483 | 1185944.7916
70 | 2550614.9012 | 1185941.8545
71 | 2550716.3553 | 1185823.7575
72 | 2550619.7871 | 1185881.2197
73 | 2550614.669 | 1185888.3101
74 | 2550631.5013 | 1185864.9915
75 | 2550610.8877 | 1185880.4592
76 | 2550602.8657 | 1185904.5864
77 | 2550627.1371 | 1185855.8559
78 | 2550647.6489 | 1185842.8349
79 | 2550599.7373 | 1185908.9004
80 | 2550642.481 | 1185838.9421
81 | 2550661.5322 | 1185823.6875
82 | 2550595.186 | 1185901.1337
83 | 2550583.7795 | 1185930.8999
84 | 2550658.3864 | 1185821.6345
85 | 2550670.8567 | 1185810.829
86 | 2550581.0139 | 1185923.1407
87 | 2550574.0464 | 1185945.091
88 | 2550675.5707 | 1185804.3286
89 | 2550682.0323 | 1185786.1198
90 | 2550670.0932 | 1185743.6987
91 | 2550660.3132 | 1185734.4982
92 | 2550600.1224 | 1185775.078
93 | 2550595.7699 | 1185780.8217
94 | 2550602.3004 | 1185772.2039
95 | 2550583.9884 | 1185796.3737
96 | 2550611.8273 | 1185759.641
97 | 2550596.1868 | 1185767.4741
98 | 2550582.9847 | 1185797.6992
99 | 2550617.6955 | 1185751.8916
100 | 2550593.9999 | 1185770.414
101 | 2550582.6001 | 1185798.2071
102 | 2550618.4886 | 1185750.8443
103 | 2550573.1997 | 1185810.6212
104 | 2550633.5327 | 1185730.5527
105 | 2550557.6272 | 1185808.7463
106 | 2550581.933 | 1185831.2937
107 | 2550634.772 | 1185728.8484
108 | 2550642.574 | 1185718.1192
109 | 2550624.4847 | 1185702.0487
110 | 2550615.1127 | 1185712.4856
111 | 2550569.3165 | 1185848.5631
112 | 2550570.2883 | 1185847.2381
113 | 2550547.7691 | 1185844.6629
114 | 2550545.9989 | 1185844.3425
115 | 2550543.6732 | 1185838.9024
116 | 2550570.6463 | 1185950.0483
117 | 2550537.7765 | 1185957.8641
118 | 2550536.8563 | 1185957.768
119 | 2550515.4733 | 1185958.4691
120 | 2550499.5194 | 1185935.7303
121 | 2550495.4477 | 1185932.6179
122 | 2550604.1708 | 1185956.8679
123 | 2550609.0016 | 1185969.8351
124 | 2550594.877 | 1185969.8852
125 | 2550587.0576 | 1185964.6359
126 | 2550678.7923 | 1186009.583
127 | 2550666.8671 | 1185996.5831
128 | 2550680.2401 | 1186005.322
129 | 2550674.0318 | 1185986.3183
130 | 2550669.2023 | 1185982.734
131 | 2550679.643 | 1185978.2898
132 | 2550699.372 | 1185998.049
133 | 2550681.0157 | 1185964.3152
134 | 2550697.3536 | 1186001.2897
135 | 2550713.2765 | 1185966.9715
136 | 2550719.5958 | 1185971.4343
137 | 2550614.9286 | 1185712.6906
138 | 2550614.2763 | 1185713.417
139 | 2550477.489 | 1185918.8399
140 | 2550473.498 | 1185915.7644
141 | 2550672.85 | 1185860.7478

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98277 | -0.12065 | 0.002208 | 0.00055339
1 | 0.98273 | -0.12096 | 0 | 0
2 | 0.98282 | -0.12032 | 0 | 0
3 | 0.98271 | -0.12111 | 0 | 0
4 | 0.98298 | -0.11916 | 0.00038269 | 9.591e-05
5 | 0.98265 | -0.12153 | 0.00095576 | 0.00023954
6 | 0.98267 | -0.12134 | 0 | 0
7 | 0.98302 | -0.11888 | 0.0016261 | 0.00040755
8 | 0.97924 | -0.14587 | 0.00038299 | 9.5986e-05
9 | 0.97934 | -0.14516 | 0.00085705 | 0.0002148
10 | 0.98267 | -0.12139 | 0.00044479 | 0.00011148
11 | 0.98305 | -0.11866 | 0.00024599 | 6.165e-05
12 | 0.98316 | -0.11785 | 0.00030419 | 7.6238e-05
13 | 0.98336 | -0.11645 | 0 | 0
14 | 0.98377 | -0.1135 | 0 | 0
15 | 0.98583 | -0.09887 | 0 | 0
16 | 0.99088 | -0.063348 | 0 | 0
17 | 0.98516 | -0.10367 | 0.0020235 | 0.00050713
18 | 0.983 | -0.11895 | 0.0018774 | 0.00047052
19 | 0.979 | -0.14755 | 0.0022022 | 0.00055192
20 | 0.97925 | -0.14575 | 0.00078458 | 0.00019663
21 | 0.9789 | -0.14828 | 0.0028633 | 0.0007176
22 | 0.98069 | -0.13547 | 0.0025754 | 0.00064546
23 | 0.98122 | -0.13163 | 0 | 0
24 | 0.98684 | -0.091707 | 0 | 0
25 | 0.9916 | -0.058307 | 0.0022665 | 0.00056804
26 | 0.98493 | -0.10526 | 0 | 0
27 | 0.98165 | -0.12859 | 0 | 0
28 | 0.98114 | -0.13219 | 0.0031744 | 0.00079558
29 | 0.98156 | -0.12919 | 0.0019849 | 0.00049746
30 | 0.98077 | -0.13487 | 0.0016592 | 0.00041584
31 | 0.98038 | -0.13766 | 0 | 0
32 | 0.97952 | -0.14378 | 0.0015584 | 0.00039056
33 | 0.9793 | -0.14535 | 0 | 0
34 | 0.9803 | -0.13821 | 0.0014145 | 0.0003545
35 | 0.97929 | -0.14544 | 0.0011116 | 0.00027859
36 | 0.97875 | -0.1493 | 0 | 0
37 | 0.97873 | -0.14941 | 0.0013062 | 0.00032737
38 | 0.97864 | -0.15005 | 0 | 0
39 | 0.97842 | -0.15166 | 0 | 0
40 | 0.9785 | -0.1511 | 0.0010631 | 0.00026643
41 | 0.98438 | -0.10919 | 0.0018547 | 0.00046483
42 | 0.98366 | -0.11428 | 0.0027559 | 0.00069069
43 | 0.9851 | -0.10399 | 0.0010759 | 0.00026964
44 | 0.98568 | -0.099917 | 0 | 0
45 | 0.99325 | -0.046789 | 0 | 0
46 | 0.98363 | -0.11454 | 0.00099644 | 0.00024973
47 | 0.98312 | -0.11816 | 0.0024375 | 0.0006109
48 | 0.9827 | -0.12117 | 0.0024802 | 0.00062161
49 | 0.98237 | -0.1235 | 0.0027098 | 0.00067915
50 | 0.98224 | -0.12443 | 0 | 0
51 | 0.98219 | -0.12476 | 0.0022457 | 0.00056283
52 | 0.98217 | -0.12489 | 0.0025392 | 0.00063638
53 | 0.99887 | -0.0077842 | 0.0021012 | 0.0005266
54 | 0.9989 | -0.0076112 | 0 | 0
55 | 0.99602 | -0.027512 | 0 | 0
56 | 0.99939 | -0.0041867 | 0 | 0
57 | 1 | 0 | -0.17796 | -0.044751
58 | 0.99953 | -0.0032642 | 0 | 0
59 | 0.99542 | -0.031665 | 0 | 0
60 | 0.99598 | -0.027789 | 0.0021065 | 0.00052795
61 | 0.99934 | -0.0045786 | 0.002859 | 0.00071655
62 | 0.99951 | -0.0034514 | 0.0020873 | 0.00052313
63 | 0.9995 | -0.0035222 | 0.0019296 | 0.00048361
64 | 0.99914 | -0.0060625 | 0 | 0
65 | 0.99535 | -0.032162 | 0.0028714 | 0.00071964
66 | 0.99476 | -0.036229 | 0.0025052 | 0.00062785
67 | 0.9991 | -0.0062911 | 0.0016562 | 0.00041509
68 | 0.99881 | -0.0083284 | 0 | 0
69 | 0.99879 | -0.0085078 | 0.0014219 | 0.00035637
70 | 0.99872 | -0.0089959 | 0.0025599 | 0.00064158
71 | 0.9932 | -0.047087 | 0.0021219 | 0.00053179
72 | 0.98071 | -0.13517 | 0.0017938 | 0.00044957
73 | 0.98042 | -0.13724 | 0 | 0
74 | 0.98143 | -0.13007 | 0 | 0
75 | 0.9804 | -0.1374 | 0.0018156 | 0.00045504
76 | 0.97981 | -0.14162 | 0.0016016 | 0.0004014
77 | 0.9814 | -0.13026 | 0.0017994 | 0.00045098
78 | 0.98248 | -0.12259 | 0 | 0
79 | 0.97966 | -0.14269 | 0 | 0
80 | 0.98244 | -0.12286 | 0.0040895 | 0.0010249
81 | 0.98353 | -0.11515 | 0 | 0
82 | 0.97962 | -0.14294 | 0.0026403 | 0.00066171
83 | 0.979 | -0.14742 | 0 | 0
84 | 0.98351 | -0.11527 | 0.0031293 | 0.00078429
85 | 0.9843 | -0.10964 | 0.00091843 | 0.00023018
86 | 0.97894 | -0.14779 | 0.0042743 | 0.0010712
87 | 0.97868 | -0.14965 | 0.0010467 | 0.00026232
88 | 0.9847 | -0.10679 | 0.001204 | 0.00030176
89 | 0.98565 | -0.10007 | 0.0027637 | 0.00069265
90 | 0.98447 | -0.10841 | 0.0012209 | 0.000306
91 | 0.98373 | -0.11368 | 0.0010759 | 0.00026964
92 | 0.97948 | -0.14394 | 0.00080926 | 0.00020282
93 | 0.97927 | -0.14543 | 0.00069327 | 0.00017375
94 | 0.97959 | -0.14317 | 0 | 0
95 | 0.97873 | -0.14932 | 0.0010261 | 0.00025716
96 | 0.98018 | -0.13897 | 0.00096516 | 0.00024189
97 | 0.97953 | -0.14357 | 0.0024141 | 0.00060503
98 | 0.97868 | -0.14963 | 0.0026588 | 0.00066636
99 | 0.98055 | -0.13629 | 0.0026284 | 0.00065875
100 | 0.97952 | -0.14367 | 0.0025749 | 0.00064533
101 | 0.97867 | -0.14973 | 0.0018331 | 0.00045942
102 | 0.98061 | -0.13589 | 0.00079283 | 0.0001987
103 | 0.97836 | -0.15194 | 0 | 0
104 | 0.98171 | -0.12803 | 0.001221 | 0.000306
105 | 0.9783 | -0.15235 | 0.0024767 | 0.00062071
106 | 0.978 | -0.15455 | 0.0024559 | 0.0006155
107 | 0.98181 | -0.12735 | 0.0010759 | 0.00026964
108 | 0.98243 | -0.12291 | 0 | 0
109 | 0.98227 | -0.12409 | 0 | 0
110 | 0.98217 | -0.12477 | 0.001221 | 0.000306
111 | 0.97797 | -0.15477 | 0.00097915 | 0.0002454
112 | 0.97778 | -0.15613 | 0.0010811 | 0.00027095
113 | 0.97755 | -0.15775 | 0.00089824 | 0.00022512
114 | 0.97753 | -0.15786 | 0.00471 | 0.0011804
115 | 0.97753 | -0.15792 | 0.00099548 | 0.00024949
116 | 0.97858 | -0.15037 | 0.0010469 | 0.00026237
117 | 0.97803 | -0.15433 | 0.0028679 | 0.00071876
118 | 0.97802 | -0.1544 | 0.0013423 | 0.00033642
119 | 0.97783 | -0.15578 | 0 | 0
120 | 0.97756 | -0.15774 | 0.0013082 | 0.00032787
121 | 0.97752 | -0.158 | 0.0013578 | 0.0003403
122 | 0.99862 | -0.0096816 | 0 | 0
123 | 0.99858 | -0.0099858 | 0.0021955 | 0.00055024
124 | 0.99858 | -0.0099239 | 0 | 0
125 | 0.99856 | -0.010066 | 0.0015131 | 0.00037921
126 | 0.97809 | -0.15404 | 0.0017469 | 0.00043781
127 | 0.97814 | -0.15364 | 0 | 0
128 | 0.9781 | -0.15393 | 0.00171 | 0.00042858
129 | 0.97821 | -0.15319 | 0 | 0
130 | 0.97819 | -0.15327 | 0.0013168 | 0.00033002
131 | 0.97827 | -0.1527 | 0 | 0
132 | 0.97812 | -0.15379 | 0.00061689 | 0.00015461
133 | 0.97841 | -0.15174 | 0.0011694 | 0.00029308
134 | 0.97811 | -0.15391 | 0.0028151 | 0.00070552
135 | 0.97847 | -0.15131 | 0.0010762 | 0.00026972
136 | 0.97843 | -0.15161 | 0.0037901 | 0.00094989
137 | 0.98217 | -0.12478 | 0.0010969 | 0.00027492
138 | 0.98217 | -0.1248 | 0.0023799 | 0.00059645
139 | 0.9774 | -0.15882 | 0.0015863 | 0.00039756
140 | 0.97739 | -0.15892 | 0.0018829 | 0.00047189
141 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0014007 | 0.00034937 | -0.0014006 | -0.00034962 | 6.0156e-08 | -2.4857e-07 | 0.0021202 | 0.0021203 | 0.0021203 | 0.98277 | -0.12065 | 0.98273 | -0.12096 | 0.7853
1 | -0.0036087 | -0.00090276 | 0.0036089 | 0.00090271 | 1.6519e-07 | -4.885e-08 | 0.0054634 | 0.0054634 | 0.0054634 | 0.98277 | -0.12065 | 0.98282 | -0.12032 | 2.0235
2 | 0.0014006 | 0.00034962 | -0.0014006 | -0.00034974 | 2.811e-08 | -1.1614e-07 | 0.0021203 | 0.0021204 | 0.0021204 | 0.98273 | -0.12096 | 0.98271 | -0.12111 | 0.78532
3 | -0.0036089 | -0.00090271 | 0.0036095 | 0.00090254 | 5.7418e-07 | -1.6989e-07 | 0.0054634 | 0.0054632 | 0.0054634 | 0.98282 | -0.12032 | 0.98298 | -0.11916 | 2.0235
4 | 0.00095581 | 0.00023902 | -0.00095576 | -0.00023954 | 5.5192e-08 | -5.1378e-07 | 0.0014471 | 0.0014473 | 0.0014473 | 0.98271 | -0.12111 | 0.98265 | -0.12153 | 0.53604
5 | 0.00044481 | 0.00011071 | -0.00044479 | -0.00011133 | 1.3899e-08 | -6.1702e-07 | 0.00067326 | 0.00067348 | 0.00067348 | 0.98271 | -0.12111 | 0.98267 | -0.12134 | 0.24944
6 | -0.0039922 | -0.00099845 | 0.0039923 | 0.00099842 | 1.5603e-07 | -2.6804e-08 | 0.0060426 | 0.0060425 | 0.0060426 | 0.98298 | -0.11916 | 0.98302 | -0.11888 | 2.238
7 | 0.00044479 | 0.00011133 | -0.00044479 | -0.00011148 | 3.231e-09 | -1.4337e-07 | 0.00067348 | 0.00067353 | 0.00067353 | 0.98267 | -0.12134 | 0.98267 | -0.12139 | 0.24946
8 | -0.0056185 | -0.001406 | 0.0056186 | 0.001406 | 1.7025e-07 | 1.7651e-08 | 0.008504 | 0.008504 | 0.008504 | 0.98302 | -0.11888 | 0.98305 | -0.11866 | 3.1496
9 | -0.00038299 | -9.5986e-05 | 0.00038303 | 9.3802e-05 | 3.6876e-08 | -2.184e-06 | 0.00058198 | 0.0005812 | 0.00058198 | 0.97924 | -0.14587 | 0.97934 | -0.14516 | 0.21555
10 | 0.0058521 | 0.0014661 | -0.0058516 | -0.001466 | 4.785e-07 | 6.2005e-08 | 0.0088915 | 0.0088916 | 0.0088916 | 0.97934 | -0.14516 | 0.97925 | -0.14575 | 3.2932
11 | -0.0070921 | -0.0017747 | 0.0071016 | 0.0017767 | 9.4874e-06 | 1.9988e-06 | 0.010775 | 0.010774 | 0.010775 | 0.97934 | -0.14516 | 0.98069 | -0.13547 | 3.9907
12 | -0.0058646 | -0.0014676 | 0.0058653 | 0.0014677 | 6.5841e-07 | 8.3429e-08 | 0.0088764 | 0.0088763 | 0.0088764 | 0.98305 | -0.11866 | 0.98316 | -0.11785 | 3.2875
13 | -0.0061695 | -0.001544 | 0.0061707 | 0.0015441 | 1.1916e-06 | 1.8047e-07 | 0.0093367 | 0.0093366 | 0.0093367 | 0.98316 | -0.11785 | 0.98336 | -0.11645 | 3.458
14 | -0.0061707 | -0.0015441 | 0.0061732 | 0.0015445 | 2.5094e-06 | 3.7965e-07 | 0.0093366 | 0.0093364 | 0.0093366 | 0.98336 | -0.11645 | 0.98377 | -0.1135 | 3.458
15 | 0.039223 | 0.0098422 | -0.039193 | -0.0098309 | 2.9649e-05 | 1.1232e-05 | 0.059331 | 0.059331 | 0.059331 | 0.98377 | -0.1135 | 0.983 | -0.11895 | 21.9746
16 | -0.045396 | -0.011387 | 0.045488 | 0.011422 | 9.2298e-05 | 3.51e-05 | 0.068668 | 0.068668 | 0.068668 | 0.98377 | -0.1135 | 0.98583 | -0.09887 | 25.4325
17 | -0.065584 | -0.016463 | 0.065909 | 0.016587 | 0.00032517 | 0.00012438 | 0.099002 | 0.099001 | 0.099002 | 0.98583 | -0.09887 | 0.99088 | -0.063348 | 36.6673
18 | 0.020096 | 0.005041 | -0.020082 | -0.0050361 | 1.3375e-05 | 4.8475e-06 | 0.030334 | 0.030334 | 0.030334 | 0.98583 | -0.09887 | 0.98516 | -0.10367 | 11.2349
19 | 0.079668 | 0.020069 | -0.079353 | -0.019949 | 0.00031473 | 0.0001206 | 0.11968 | 0.11968 | 0.11968 | 0.99088 | -0.063348 | 0.98684 | -0.091707 | 44.3243
20 | -0.14558 | -0.036656 | 0.14568 | 0.036696 | 0.00010263 | 3.9295e-05 | 0.21868 | 0.21868 | 0.21868 | 0.99088 | -0.063348 | 0.9916 | -0.058307 | 40.4957
21 | 0.018059 | 0.004529 | -0.018055 | -0.0045276 | 3.967e-06 | 1.417e-06 | 0.027278 | 0.027278 | 0.027278 | 0.98516 | -0.10367 | 0.98493 | -0.10526 | 10.1029
22 | 0.037316 | 0.0093604 | -0.037266 | -0.0093416 | 4.9821e-05 | 1.8845e-05 | 0.056489 | 0.05649 | 0.05649 | 0.983 | -0.11895 | 0.98165 | -0.12859 | 20.9221
23 | -0.0050658 | -0.0012693 | 0.005067 | 0.0012694 | 1.2641e-06 | 5.6392e-08 | 0.0076995 | 0.0076994 | 0.0076995 | 0.979 | -0.14755 | 0.97925 | -0.14575 | 2.8517
24 | 0.0028636 | 0.00071741 | -0.0028633 | -0.0007176 | 2.876e-07 | -1.9529e-07 | 0.0043523 | 0.0043524 | 0.0043524 | 0.979 | -0.14755 | 0.9789 | -0.14828 | 1.612
25 | -0.009677 | -0.0024221 | 0.0096822 | 0.0024236 | 5.1321e-06 | 1.4922e-06 | 0.014682 | 0.014682 | 0.014682 | 0.98069 | -0.13547 | 0.98122 | -0.13163 | 5.4378
26 | 0.0031747 | 0.00079546 | -0.0031744 | -0.00079558 | 2.4773e-07 | -1.2106e-07 | 0.0048143 | 0.0048144 | 0.0048144 | 0.98122 | -0.13163 | 0.98114 | -0.13219 | 1.7831
27 | -0.012857 | -0.0032191 | 0.012862 | 0.0032209 | 5.3963e-06 | 1.788e-06 | 0.019496 | 0.019496 | 0.019496 | 0.98122 | -0.13163 | 0.98165 | -0.12859 | 7.2208
28 | 0.040642 | 0.010219 | -0.040572 | -0.010193 | 6.9459e-05 | 2.6337e-05 | 0.061294 | 0.061294 | 0.061294 | 0.98684 | -0.091707 | 0.9851 | -0.10399 | 22.7016
29 | 0.038711 | 0.0097295 | -0.038667 | -0.0097128 | 4.4196e-05 | 1.6733e-05 | 0.058381 | 0.058381 | 0.058381 | 0.98684 | -0.091707 | 0.98568 | -0.099917 | 21.6227
30 | -0.14795 | -0.037264 | 0.14818 | 0.037355 | 0.00023865 | 9.1387e-05 | 0.22208 | 0.22208 | 0.22208 | 0.9916 | -0.058307 | 0.99325 | -0.046789 | 41.1256
31 | 0.018055 | 0.0045276 | -0.018045 | -0.0045241 | 9.8355e-06 | 3.5134e-06 | 0.027278 | 0.027278 | 0.027278 | 0.98493 | -0.10526 | 0.98438 | -0.10919 | 10.103
32 | 0.024404 | 0.0061207 | -0.024402 | -0.00612 | 2.0239e-06 | 7.4848e-07 | 0.036994 | 0.036994 | 0.036994 | 0.98165 | -0.12859 | 0.98156 | -0.12919 | 13.7013
33 | 0.022417 | 0.0056225 | -0.022399 | -0.005616 | 1.7643e-05 | 6.4765e-06 | 0.033985 | 0.033985 | 0.033985 | 0.98156 | -0.12919 | 0.98077 | -0.13487 | 12.5869
34 | 0.02074 | 0.0052002 | -0.020732 | -0.0051973 | 8.0156e-06 | 2.9193e-06 | 0.031467 | 0.031467 | 0.031467 | 0.98077 | -0.13487 | 0.98038 | -0.13766 | 11.6545
35 | 0.0014146 | 0.00035408 | -0.0014145 | -0.0003545 | 1.0668e-07 | -4.2659e-07 | 0.0021469 | 0.0021471 | 0.0021471 | 0.98038 | -0.13766 | 0.9803 | -0.13821 | 0.79521
36 | 0.019317 | 0.0048432 | -0.019301 | -0.0048373 | 1.6357e-05 | 5.9069e-06 | 0.02932 | 0.029321 | 0.029321 | 0.98038 | -0.13766 | 0.97952 | -0.14378 | 10.8595
37 | 0.017743 | 0.0044467 | -0.017739 | -0.0044453 | 3.8661e-06 | 1.3796e-06 | 0.026953 | 0.026953 | 0.026953 | 0.97952 | -0.14378 | 0.9793 | -0.14535 | 9.9827
38 | 0.0011116 | 0.0002785 | -0.0011116 | -0.00027859 | 1.381e-08 | -9.2296e-08 | 0.001689 | 0.001689 | 0.001689 | 0.9793 | -0.14535 | 0.97929 | -0.14544 | 0.62557
39 | 0.016627 | 0.0041668 | -0.016618 | -0.0041636 | 9.0768e-06 | 3.2045e-06 | 0.025264 | 0.025264 | 0.025264 | 0.9793 | -0.14535 | 0.97875 | -0.1493 | 9.3571
40 | 0.0013062 | 0.00032728 | -0.0013062 | -0.00032737 | 1.9232e-08 | -9.0817e-08 | 0.0019859 | 0.0019859 | 0.0019859 | 0.97875 | -0.1493 | 0.97873 | -0.14941 | 0.73552
41 | 0.015312 | 0.0038363 | -0.01531 | -0.0038358 | 1.597e-06 | 5.5489e-07 | 0.023278 | 0.023278 | 0.023278 | 0.97875 | -0.1493 | 0.97864 | -0.15005 | 8.6216
42 | 0.0093796 | 0.0023497 | -0.0093776 | -0.0023491 | 2.0778e-06 | 5.9349e-07 | 0.014261 | 0.014261 | 0.014261 | 0.97864 | -0.15005 | 0.97842 | -0.15166 | 5.282
43 | 0.0059305 | 0.0014861 | -0.0059297 | -0.001486 | 8.5989e-07 | 1.1781e-07 | 0.0090172 | 0.0090173 | 0.0090173 | 0.97864 | -0.15005 | 0.9785 | -0.1511 | 3.3397
44 | 0.0011694 | 0.000293 | -0.0011694 | -0.00029308 | 1.3547e-08 | -8.0995e-08 | 0.0017785 | 0.0017785 | 0.0017785 | 0.97842 | -0.15166 | 0.97841 | -0.15174 | 0.6587
45 | 0.0082081 | 0.0020561 | -0.0082069 | -0.0020558 | 1.1913e-06 | 3.0434e-07 | 0.012483 | 0.012483 | 0.012483 | 0.97842 | -0.15166 | 0.97827 | -0.1527 | 4.6233
46 | 0.0048666 | 0.0012196 | -0.0048664 | -0.0012196 | 1.3815e-07 | 2.3606e-09 | 0.0074007 | 0.0074007 | 0.0074007 | 0.9785 | -0.1511 | 0.97847 | -0.15131 | 2.741
47 | 0.01619 | 0.0040592 | -0.016179 | -0.0040552 | 1.1405e-05 | 3.9989e-06 | 0.024474 | 0.024475 | 0.024475 | 0.98438 | -0.10919 | 0.98366 | -0.11428 | 9.0646
48 | 0.013423 | 0.0033645 | -0.013423 | -0.0033644 | 4.8819e-07 | 1.6368e-07 | 0.020306 | 0.020306 | 0.020306 | 0.98366 | -0.11428 | 0.98363 | -0.11454 | 7.5206
49 | 0.039497 | 0.0099232 | -0.039472 | -0.009914 | 2.4267e-05 | 9.1946e-06 | 0.059669 | 0.059669 | 0.059669 | 0.9851 | -0.10399 | 0.98447 | -0.10841 | 22.0997
50 | 0.0027638 | 0.00069261 | -0.0027637 | -0.00069265 | 5.9213e-08 | -4.6704e-08 | 0.0041723 | 0.0041723 | 0.0041723 | 0.98568 | -0.099917 | 0.98565 | -0.10007 | 1.5453
51 | 0.035903 | 0.0090202 | -0.035869 | -0.0090072 | 3.4278e-05 | 1.2946e-05 | 0.054209 | 0.054209 | 0.054209 | 0.98568 | -0.099917 | 0.9847 | -0.10679 | 20.0775
52 | 0.0021219 | 0.00053164 | -0.0021219 | -0.00053179 | 8.7482e-08 | -1.459e-07 | 0.0031789 | 0.003179 | 0.003179 | 0.99325 | -0.046789 | 0.9932 | -0.047087 | 1.1774
53 | -0.15031 | -0.037887 | 0.15053 | 0.037972 | 0.00022261 | 8.5253e-05 | 0.22526 | 0.22526 | 0.22526 | 0.99325 | -0.046789 | 0.99476 | -0.036229 | 41.7142
54 | 0.012426 | 0.0031146 | -0.01242 | -0.0031126 | 6.2291e-06 | 2.0374e-06 | 0.018798 | 0.018798 | 0.018798 | 0.98363 | -0.11454 | 0.98312 | -0.11816 | 6.9624
55 | 0.0099825 | 0.0025017 | -0.0099783 | -0.0025005 | 4.1534e-06 | 1.2279e-06 | 0.015109 | 0.015109 | 0.015109 | 0.98312 | -0.11816 | 0.9827 | -0.12117 | 5.596
56 | 0.0074981 | 0.0018789 | -0.0074956 | -0.0018783 | 2.4198e-06 | 5.4969e-07 | 0.011354 | 0.011354 | 0.011354 | 0.9827 | -0.12117 | 0.98237 | -0.1235 | 4.2051
57 | 0.0047858 | 0.0011992 | -0.0047852 | -0.0011992 | 6.1887e-07 | -8.8852e-10 | 0.0072491 | 0.0072492 | 0.0072492 | 0.98237 | -0.1235 | 0.98224 | -0.12443 | 2.6849
58 | 0.0047852 | 0.0011992 | -0.004785 | -0.0011992 | 2.1689e-07 | -2.9496e-10 | 0.0072492 | 0.0072492 | 0.0072492 | 0.98224 | -0.12443 | 0.98219 | -0.12476 | 2.6849
59 | 0.0025393 | 0.00063634 | -0.0025392 | -0.00063638 | 4.6193e-08 | -4.5541e-08 | 0.0038469 | 0.003847 | 0.003847 | 0.98219 | -0.12476 | 0.98217 | -0.12489 | 1.4248
60 | -0.0021012 | -0.0005266 | 0.0021012 | 0.00052652 | 5.0311e-08 | -8.8371e-08 | 0.0031301 | 0.0031301 | 0.0031301 | 0.99887 | -0.0077842 | 0.9989 | -0.0076112 | 1.1593
61 | 0.15864 | 0.040089 | -0.1582 | -0.03992 | 0.00044311 | 0.00016976 | 0.23644 | 0.23644 | 0.23644 | 0.9989 | -0.0076112 | 0.99602 | -0.027512 | 43.7858
62 | -0.16075 | -0.040616 | 0.16082 | 0.040646 | 7.7503e-05 | 2.9696e-05 | 0.23957 | 0.23957 | 0.23957 | 0.9989 | -0.0076112 | 0.99939 | -0.0041867 | 44.3654
63 | 0.1561 | 0.039392 | -0.156 | -0.039357 | 9.0935e-05 | 3.4836e-05 | 0.2333 | 0.2333 | 0.2333 | 0.99602 | -0.027512 | 0.99542 | -0.031665 | 43.203
64 | 0.0021066 | 0.00052781 | -0.0021065 | -0.00052795 | 8.0884e-08 | -1.3921e-07 | 0.0031472 | 0.0031472 | 0.0031472 | 0.99602 | -0.027512 | 0.99598 | -0.027789 | 1.1656
65 | 0.0028592 | 0.00071643 | -0.002859 | -0.00071655 | 1.5511e-07 | -1.2006e-07 | 0.0042571 | 0.0042571 | 0.0042571 | 0.99939 | -0.0041867 | 0.99934 | -0.0045786 | 1.5767
66 | -0.16368 | -0.041362 | 0.16378 | 0.041399 | 9.6513e-05 | 3.6984e-05 | 0.24383 | 0.24383 | 0.24383 | 0.99939 | -0.0041867 | 1 | 0 | 45.1538
67 | 0.013377 | 0.0033517 | -0.013371 | -0.0033497 | 6.0396e-06 | 2.0026e-06 | 0.019905 | 0.019905 | 0.019905 | 1 | 0 | 0.99953 | -0.0032642 | 7.3722
68 | 0.0020874 | 0.00052303 | -0.0020873 | -0.00052313 | 5.4085e-08 | -9.6844e-08 | 0.0031074 | 0.0031075 | 0.0031075 | 0.99953 | -0.0032642 | 0.99951 | -0.0034514 | 1.1509
69 | 0.0019297 | 0.00048346 | -0.0019296 | -0.00048361 | 6.8896e-08 | -1.4885e-07 | 0.0028727 | 0.0028728 | 0.0028728 | 0.99953 | -0.0032642 | 0.9995 | -0.0035222 | 1.064
70 | 0.0093539 | 0.0023433 | -0.0093502 | -0.0023423 | 3.6196e-06 | 1.0002e-06 | 0.013925 | 0.013925 | 0.013925 | 0.99953 | -0.0032642 | 0.99914 | -0.0060625 | 5.1574
71 | 0.0028716 | 0.00071949 | -0.0028714 | -0.00071964 | 1.9751e-07 | -1.4732e-07 | 0.0042926 | 0.0042926 | 0.0042926 | 0.99542 | -0.031665 | 0.99535 | -0.032162 | 1.5899
72 | 0.15313 | 0.038637 | -0.15303 | -0.0386 | 9.8015e-05 | 3.7542e-05 | 0.229 | 0.229 | 0.229 | 0.99542 | -0.031665 | 0.99476 | -0.036229 | 42.4081
73 | 0.0016563 | 0.00041493 | -0.0016562 | -0.00041509 | 5.2391e-08 | -1.6056e-07 | 0.0024666 | 0.0024667 | 0.0024667 | 0.99914 | -0.0060625 | 0.9991 | -0.0062911 | 0.91359
74 | 0.007694 | 0.0019273 | -0.0076916 | -0.0019268 | 2.4108e-06 | 5.4198e-07 | 0.011458 | 0.011458 | 0.011458 | 0.99914 | -0.0060625 | 0.99881 | -0.0083284 | 4.2439
75 | 0.001422 | 0.00035622 | -0.0014219 | -0.00035637 | 3.5292e-08 | -1.5137e-07 | 0.0021184 | 0.0021184 | 0.0021184 | 0.99881 | -0.0083284 | 0.99879 | -0.0085078 | 0.7846
76 | 0.0062696 | 0.0015706 | -0.006269 | -0.0015705 | 5.7881e-07 | 8.3469e-08 | 0.0093401 | 0.0093401 | 0.0093401 | 0.99881 | -0.0083284 | 0.99872 | -0.0089959 | 3.4593
77 | 0.0037091 | 0.0009289 | -0.0037087 | -0.00092901 | 3.5165e-07 | -1.0621e-07 | 0.005526 | 0.0055261 | 0.0055261 | 0.99872 | -0.0089959 | 0.99862 | -0.0096816 | 2.0467
78 | 0.022818 | 0.0057223 | -0.022812 | -0.0057199 | 6.5413e-06 | 2.4056e-06 | 0.034623 | 0.034623 | 0.034623 | 0.98071 | -0.13517 | 0.98042 | -0.13724 | 12.8234
79 | -0.024612 | -0.0061719 | 0.02463 | 0.0061783 | 1.7418e-05 | 6.4464e-06 | 0.037345 | 0.037345 | 0.037345 | 0.98071 | -0.13517 | 0.98143 | -0.13007 | 13.8315
80 | 0.0018157 | 0.00045495 | -0.0018156 | -0.00045504 | 4.1278e-08 | -9.3972e-08 | 0.0027557 | 0.0027557 | 0.0027557 | 0.98042 | -0.13724 | 0.9804 | -0.1374 | 1.0206
81 | 0.020996 | 0.0052649 | -0.020983 | -0.0052603 | 1.2741e-05 | 4.647e-06 | 0.031868 | 0.031868 | 0.031868 | 0.98042 | -0.13724 | 0.97981 | -0.14162 | 11.8028
82 | 0.0017995 | 0.00045087 | -0.0017994 | -0.00045098 | 4.7011e-08 | -1.0981e-07 | 0.0027283 | 0.0027283 | 0.0027283 | 0.98143 | -0.13007 | 0.9814 | -0.13026 | 1.0105
83 | -0.026429 | -0.0066292 | 0.026457 | 0.0066394 | 2.7448e-05 | 1.021e-05 | 0.040073 | 0.040073 | 0.040073 | 0.98143 | -0.13007 | 0.98248 | -0.12259 | 14.8419
84 | 0.019382 | 0.0048589 | -0.019379 | -0.0048578 | 2.8811e-06 | 1.041e-06 | 0.029435 | 0.029435 | 0.029435 | 0.97981 | -0.14162 | 0.97966 | -0.14269 | 10.902
85 | 0.0040896 | 0.0010249 | -0.0040895 | -0.0010249 | 1.5463e-07 | -2.2319e-08 | 0.006194 | 0.006194 | 0.006194 | 0.98248 | -0.12259 | 0.98244 | -0.12286 | 2.2941
86 | -0.030546 | -0.0076643 | 0.030578 | 0.0076761 | 3.1564e-05 | 1.184e-05 | 0.046267 | 0.046267 | 0.046267 | 0.98248 | -0.12259 | 0.98353 | -0.11515 | 17.1359
87 | 0.0026404 | 0.00066163 | -0.0026403 | -0.00066171 | 9.0297e-08 | -7.8547e-08 | 0.0040104 | 0.0040105 | 0.0040105 | 0.97966 | -0.14269 | 0.97962 | -0.14294 | 1.4854
88 | 0.016739 | 0.0041962 | -0.016728 | -0.0041923 | 1.0953e-05 | 3.8711e-06 | 0.025425 | 0.025425 | 0.025425 | 0.97966 | -0.14269 | 0.979 | -0.14742 | 9.4167
89 | 0.0031294 | 0.00078426 | -0.0031293 | -0.00078429 | 5.244e-08 | -2.7407e-08 | 0.0047346 | 0.0047346 | 0.0047346 | 0.98353 | -0.11515 | 0.98351 | -0.11527 | 1.7536
90 | -0.033707 | -0.0084604 | 0.033733 | 0.0084701 | 2.5781e-05 | 9.714e-06 | 0.051001 | 0.051001 | 0.051001 | 0.98353 | -0.11515 | 0.9843 | -0.10964 | 18.8894
91 | 0.0042745 | 0.0010712 | -0.0042743 | -0.0010712 | 2.1696e-07 | -2.0119e-08 | 0.006497 | 0.0064971 | 0.0064971 | 0.979 | -0.14742 | 0.97894 | -0.14779 | 2.4063
92 | 0.012453 | 0.0031211 | -0.012449 | -0.0031198 | 3.8471e-06 | 1.2633e-06 | 0.018928 | 0.018928 | 0.018928 | 0.979 | -0.14742 | 0.97868 | -0.14965 | 7.0104
93 | -0.034651 | -0.0087003 | 0.034665 | 0.0087055 | 1.3752e-05 | 5.1873e-06 | 0.05239 | 0.05239 | 0.05239 | 0.9843 | -0.10964 | 0.9847 | -0.10679 | 19.4036
94 | 0.011403 | 0.0028575 | -0.011401 | -0.0028572 | 1.1274e-06 | 3.5809e-07 | 0.017337 | 0.017337 | 0.017337 | 0.97868 | -0.14965 | 0.97858 | -0.15037 | 6.421
95 | 0.038251 | 0.009608 | -0.038223 | -0.0095974 | 2.8015e-05 | 1.0605e-05 | 0.057824 | 0.057824 | 0.057824 | 0.98447 | -0.10841 | 0.98373 | -0.11368 | 21.4163
96 | 0.037147 | 0.0093277 | -0.0371 | -0.0093097 | 4.758e-05 | 1.7994e-05 | 0.056197 | 0.056197 | 0.056197 | 0.98373 | -0.11368 | 0.98243 | -0.12291 | 20.8136
97 | 0.019835 | 0.0049727 | -0.019831 | -0.0049713 | 4.0833e-06 | 1.4798e-06 | 0.030133 | 0.030133 | 0.030133 | 0.97948 | -0.14394 | 0.97927 | -0.14543 | 11.1605
98 | -0.020644 | -0.0051756 | 0.020646 | 0.0051764 | 2.2134e-06 | 8.059e-07 | 0.031363 | 0.031363 | 0.031363 | 0.97948 | -0.14394 | 0.97959 | -0.14317 | 11.6159
99 | 0.019137 | 0.0047975 | -0.019127 | -0.0047938 | 1.0296e-05 | 3.7145e-06 | 0.02908 | 0.02908 | 0.02908 | 0.97927 | -0.14543 | 0.97873 | -0.14932 | 10.7704
100 | -0.025636 | -0.0064267 | 0.02565 | 0.0064322 | 1.4919e-05 | 5.5396e-06 | 0.038942 | 0.038942 | 0.038942 | 0.97959 | -0.14317 | 0.98018 | -0.13897 | 14.4228
101 | 0.0049893 | 0.0012503 | -0.004989 | -0.0012503 | 2.7704e-07 | 9.2509e-09 | 0.0075788 | 0.0075788 | 0.0075788 | 0.97959 | -0.14317 | 0.97953 | -0.14357 | 2.807
102 | 0.018101 | 0.0045366 | -0.0181 | -0.0045363 | 7.8576e-07 | 2.8132e-07 | 0.02752 | 0.02752 | 0.02752 | 0.97873 | -0.14932 | 0.97868 | -0.14963 | 10.1926
103 | -0.026616 | -0.0066741 | 0.026626 | 0.0066778 | 9.9033e-06 | 3.6864e-06 | 0.040407 | 0.040407 | 0.040407 | 0.98018 | -0.13897 | 0.98055 | -0.13629 | 14.9655
104 | 0.0025749 | 0.0006453 | -0.0025749 | -0.00064533 | 3.4984e-08 | -3.2668e-08 | 0.0039116 | 0.0039116 | 0.0039116 | 0.97953 | -0.14357 | 0.97952 | -0.14367 | 1.4487
105 | 0.015441 | 0.00387 | -0.015441 | -0.0038699 | 2.1913e-07 | 7.6274e-08 | 0.023478 | 0.023478 | 0.023478 | 0.97868 | -0.14963 | 0.97867 | -0.14973 | 8.6954
106 | -0.029254 | -0.0073366 | 0.029256 | 0.0073372 | 1.6158e-06 | 6.0489e-07 | 0.044395 | 0.044395 | 0.044395 | 0.98055 | -0.13629 | 0.98061 | -0.13589 | 16.4428
107 | 0.013608 | 0.0034105 | -0.013604 | -0.0034091 | 4.1597e-06 | 1.4043e-06 | 0.02069 | 0.020691 | 0.020691 | 0.97867 | -0.14973 | 0.97836 | -0.15194 | 7.6631
108 | -0.030048 | -0.0075359 | 0.030081 | 0.0075481 | 3.2775e-05 | 1.2287e-05 | 0.045599 | 0.045598 | 0.045599 | 0.98061 | -0.13589 | 0.98171 | -0.12803 | 16.8883
109 | 0.0024768 | 0.00062057 | -0.0024767 | -0.00062071 | 1.3889e-07 | -1.4354e-07 | 0.003767 | 0.0037671 | 0.0037671 | 0.97836 | -0.15194 | 0.9783 | -0.15235 | 1.3952
110 | 0.011127 | 0.0027885 | -0.011123 | -0.0027873 | 4.0107e-06 | 1.2609e-06 | 0.016924 | 0.016924 | 0.016924 | 0.97836 | -0.15194 | 0.978 | -0.15455 | 6.268
111 | -0.031302 | -0.0078541 | 0.031305 | 0.0078553 | 2.9604e-06 | 1.112e-06 | 0.047449 | 0.047449 | 0.047449 | 0.98171 | -0.12803 | 0.98181 | -0.12735 | 17.5737
112 | 0.00097918 | 0.00024514 | -0.00097915 | -0.0002454 | 2.9619e-08 | -2.5697e-07 | 0.0014897 | 0.0014898 | 0.0014898 | 0.978 | -0.15455 | 0.97797 | -0.15477 | 0.55178
113 | 0.0076881 | 0.0019266 | -0.0076864 | -0.0019262 | 1.6858e-06 | 4.0067e-07 | 0.011697 | 0.011697 | 0.011697 | 0.978 | -0.15455 | 0.97778 | -0.15613 | 4.3324
114 | -0.032381 | -0.0081249 | 0.032401 | 0.0081324 | 1.994e-05 | 7.5014e-06 | 0.04908 | 0.04908 | 0.04908 | 0.98181 | -0.12735 | 0.98243 | -0.12291 | 18.1776
115 | 0.004699 | 0.0011773 | -0.0046982 | -0.0011774 | 7.6368e-07 | -1.216e-08 | 0.0071171 | 0.0071172 | 0.0071172 | 0.98243 | -0.12291 | 0.98227 | -0.12409 | 2.636
116 | 0.0046982 | 0.0011774 | -0.0046978 | -0.0011774 | 4.4338e-07 | -7.0084e-09 | 0.0071172 | 0.0071173 | 0.0071173 | 0.98227 | -0.12409 | 0.98217 | -0.12477 | 2.636
117 | 0.0034768 | 0.00087136 | -0.0034768 | -0.00087136 | 4.7695e-09 | -1.652e-09 | 0.0052675 | 0.0052675 | 0.0052675 | 0.98217 | -0.12477 | 0.98217 | -0.12478 | 1.9509
118 | 0.0066053 | 0.0016553 | -0.0066038 | -0.001655 | 1.4843e-06 | 2.757e-07 | 0.010052 | 0.010052 | 0.010052 | 0.97778 | -0.15613 | 0.97755 | -0.15775 | 3.7231
119 | 0.0057056 | 0.0014299 | -0.0057055 | -0.0014299 | 8.4674e-08 | 1.0014e-08 | 0.008685 | 0.008685 | 0.008685 | 0.97755 | -0.15775 | 0.97753 | -0.15786 | 3.2167
120 | 0.00099549 | 0.00024942 | -0.00099548 | -0.00024949 | 8.4774e-09 | -7.0909e-08 | 0.0015153 | 0.0015154 | 0.0015154 | 0.97753 | -0.15786 | 0.97753 | -0.15792 | 0.56124
121 | 0.010355 | 0.0025948 | -0.010349 | -0.0025931 | 5.6755e-06 | 1.7222e-06 | 0.015745 | 0.015745 | 0.015745 | 0.97858 | -0.15037 | 0.97803 | -0.15433 | 5.8315
122 | 0.007481 | 0.0018743 | -0.0074809 | -0.0018743 | 7.4793e-08 | 1.7155e-08 | 0.011382 | 0.011382 | 0.011382 | 0.97803 | -0.15433 | 0.97802 | -0.1544 | 4.2154
123 | 0.0061386 | 0.0015379 | -0.0061374 | -0.0015377 | 1.1743e-06 | 1.8097e-07 | 0.0093394 | 0.0093395 | 0.0093395 | 0.97802 | -0.1544 | 0.97783 | -0.15578 | 3.4591
124 | 0.0061374 | 0.0015377 | -0.0061358 | -0.0015374 | 1.658e-06 | 2.5569e-07 | 0.0093395 | 0.0093396 | 0.0093396 | 0.97783 | -0.15578 | 0.97756 | -0.15774 | 3.4591
125 | 0.0048275 | 0.0012096 | -0.0048274 | -0.0012096 | 1.7268e-07 | 2.1666e-09 | 0.0073482 | 0.0073483 | 0.0073483 | 0.97756 | -0.15774 | 0.97752 | -0.158 | 2.7216
126 | 0.0034696 | 0.00086926 | -0.0034692 | -0.00086939 | 3.9398e-07 | -1.3219e-07 | 0.0052814 | 0.0052815 | 0.0052815 | 0.97752 | -0.158 | 0.9774 | -0.15882 | 1.9561
127 | 0.0021956 | 0.0005501 | -0.0021955 | -0.00055024 | 9.2407e-08 | -1.4547e-07 | 0.0032715 | 0.0032716 | 0.0032716 | 0.99862 | -0.0096816 | 0.99858 | -0.0099858 | 1.2117
128 | 0.0015132 | 0.00037891 | -0.0015131 | -0.0003791 | 5.0692e-08 | -1.8958e-07 | 0.0022546 | 0.0022547 | 0.0022547 | 0.99862 | -0.0096816 | 0.99858 | -0.0099239 | 0.83506
129 | 0.0015131 | 0.0003791 | -0.0015131 | -0.00037921 | 2.9819e-08 | -1.115e-07 | 0.0022547 | 0.0022547 | 0.0022547 | 0.99858 | -0.0099239 | 0.99856 | -0.010066 | 0.83508
130 | -0.0017469 | -0.00043781 | 0.001747 | 0.00043757 | 9.4554e-08 | -2.3292e-07 | 0.0026576 | 0.0026575 | 0.0026576 | 0.97809 | -0.15404 | 0.97814 | -0.15364 | 0.9843
131 | 0.0017101 | 0.0004284 | -0.00171 | -0.00042858 | 6.7333e-08 | -1.7422e-07 | 0.0026015 | 0.0026015 | 0.0026015 | 0.97814 | -0.15364 | 0.9781 | -0.15393 | 0.96353
132 | -0.0034571 | -0.00086598 | 0.0034573 | 0.0008659 | 2.1586e-07 | -7.3988e-08 | 0.005259 | 0.0052589 | 0.005259 | 0.97814 | -0.15364 | 0.97821 | -0.15319 | 1.9478
133 | 0.0013168 | 0.00032995 | -0.0013168 | -0.00033002 | 1.5032e-08 | -6.959e-08 | 0.0020031 | 0.0020031 | 0.0020031 | 0.97821 | -0.15319 | 0.97819 | -0.15327 | 0.74189
134 | -0.0047741 | -0.0011959 | 0.0047744 | 0.0011959 | 3.2207e-07 | 1.0002e-09 | 0.007262 | 0.007262 | 0.007262 | 0.97821 | -0.15319 | 0.97827 | -0.1527 | 2.6896
135 | 0.0034325 | 0.00085991 | -0.003432 | -0.0008601 | 5.1784e-07 | -1.8301e-07 | 0.0052209 | 0.0052211 | 0.0052211 | 0.97827 | -0.1527 | 0.97812 | -0.15379 | 1.9337
136 | 0.0028151 | 0.00070549 | -0.0028151 | -0.00070552 | 4.3693e-08 | -3.1113e-08 | 0.0042826 | 0.0042826 | 0.0042826 | 0.97812 | -0.15379 | 0.97811 | -0.15391 | 1.5862
137 | 0.0037903 | 0.00094985 | -0.0037901 | -0.00094989 | 1.6039e-07 | -3.5479e-08 | 0.005764 | 0.0057641 | 0.0057641 | 0.97847 | -0.15131 | 0.97843 | -0.15161 | 2.1348
138 | 0.0023799 | 0.00059644 | -0.0023799 | -0.00059645 | 7.9205e-09 | -9.3101e-09 | 0.0036056 | 0.0036056 | 0.0036056 | 0.98217 | -0.12478 | 0.98217 | -0.1248 | 1.3354
139 | 0.0018829 | 0.00047184 | -0.0018829 | -0.00047189 | 2.5835e-08 | -5.3211e-08 | 0.0028665 | 0.0028666 | 0.0028666 | 0.9774 | -0.15882 | 0.97739 | -0.15892 | 1.0617

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17796 | 0.044751

## res_load
| p_mw | q_mvar
0 | 0.002208 | 0.00055339
1 | 0.00038269 | 9.591e-05
2 | 0.00095576 | 0.00023954
3 | 0.0016261 | 0.00040755
4 | 0.00038299 | 9.5986e-05
5 | 0.00085705 | 0.0002148
6 | 0.00044479 | 0.00011148
7 | 0.00024599 | 6.165e-05
8 | 0.00030419 | 7.6238e-05
9 | 0.0020235 | 0.00050713
10 | 0.0018774 | 0.00047052
11 | 0.0022022 | 0.00055192
12 | 0.00078458 | 0.00019663
13 | 0.0028633 | 0.0007176
14 | 0.0025754 | 0.00064546
15 | 0.0022665 | 0.00056804
16 | 0.0031744 | 0.00079558
17 | 0.0019849 | 0.00049746
18 | 0.0016592 | 0.00041584
19 | 0.0015584 | 0.00039056
20 | 0.0014145 | 0.0003545
21 | 0.0011116 | 0.00027859
22 | 0.0013062 | 0.00032737
23 | 0.0010631 | 0.00026643
24 | 0.0018547 | 0.00046483
25 | 0.0027559 | 0.00069069
26 | 0.0010759 | 0.00026964
27 | 0.00099644 | 0.00024973
28 | 0.0024375 | 0.0006109
29 | 0.0024802 | 0.00062161
30 | 0.0027098 | 0.00067915
31 | 0.0022457 | 0.00056283
32 | 0.0025392 | 0.00063638
33 | 0.0021012 | 0.0005266
34 | 0.0021065 | 0.00052795
35 | 0.002859 | 0.00071655
36 | 0.0020873 | 0.00052313
37 | 0.0019296 | 0.00048361
38 | 0.0028714 | 0.00071964
39 | 0.0025052 | 0.00062785
40 | 0.0016562 | 0.00041509
41 | 0.0014219 | 0.00035637
42 | 0.0025599 | 0.00064158
43 | 0.0021219 | 0.00053179
44 | 0.0017938 | 0.00044957
45 | 0.0018156 | 0.00045504
46 | 0.0016016 | 0.0004014
47 | 0.0017994 | 0.00045098
48 | 0.0040895 | 0.0010249
49 | 0.0026403 | 0.00066171
50 | 0.0031293 | 0.00078429
51 | 0.00091843 | 0.00023018
52 | 0.0042743 | 0.0010712
53 | 0.0010467 | 0.00026232
54 | 0.001204 | 0.00030176
55 | 0.0027637 | 0.00069265
56 | 0.0012209 | 0.000306
57 | 0.0010759 | 0.00026964
58 | 0.00080926 | 0.00020282
59 | 0.00069327 | 0.00017375
60 | 0.0010261 | 0.00025716
61 | 0.00096516 | 0.00024189
62 | 0.0024141 | 0.00060503
63 | 0.0026588 | 0.00066636
64 | 0.0026284 | 0.00065875
65 | 0.0025749 | 0.00064533
66 | 0.0018331 | 0.00045942
67 | 0.00079283 | 0.0001987
68 | 0.001221 | 0.000306
69 | 0.0024767 | 0.00062071
70 | 0.0024559 | 0.0006155
71 | 0.0010759 | 0.00026964
72 | 0.001221 | 0.000306
73 | 0.00097915 | 0.0002454
74 | 0.0010811 | 0.00027095
75 | 0.00089824 | 0.00022512
76 | 0.00471 | 0.0011804
77 | 0.00099548 | 0.00024949
78 | 0.0010469 | 0.00026237
79 | 0.0028679 | 0.00071876
80 | 0.0013423 | 0.00033642
81 | 0.0013082 | 0.00032787
82 | 0.0013578 | 0.0003403
83 | 0.0021955 | 0.00055024
84 | 0.0015131 | 0.00037921
85 | 0.0017469 | 0.00043781
86 | 0.00171 | 0.00042858
87 | 0.0013168 | 0.00033002
88 | 0.00061689 | 0.00015461
89 | 0.0011694 | 0.00029308
90 | 0.0028151 | 0.00070552
91 | 0.0010762 | 0.00026972
92 | 0.0037901 | 0.00094989
93 | 0.0010969 | 0.00027492
94 | 0.0023799 | 0.00059645
95 | 0.0015863 | 0.00039756
96 | 0.0018829 | 0.00047189

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1