## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2055-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2055-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2055-4_0_4_node_151 | 0.4 | n |  | TRUE
3 | bus_LV_2055-4_0_4_node_153 | 0.4 | n |  | TRUE
4 | bus_LV_2055-4_0_4_node_148 | 0.4 | n |  | TRUE
5 | bus_LV_2055-4_0_4_node_2 | 0.4 | n |  | TRUE
6 | bus_LV_2055-4_0_4_node_175 | 0.4 | n |  | TRUE
7 | bus_LV_2055-4_0_4_node_204 | 0.4 | n |  | TRUE
8 | bus_LV_2055-4_0_4_node_128 | 0.4 | n |  | TRUE
9 | bus_LV_2055-4_0_4_node_111 | 0.4 | n |  | TRUE
10 | bus_LV_2055-4_0_4_node_162 | 0.4 | n |  | TRUE
11 | bus_LV_2055-4_0_4_node_120 | 0.4 | n |  | TRUE
12 | bus_LV_2055-4_0_4_node_3 | 0.4 | n |  | TRUE
13 | bus_LV_2055-4_0_4_node_97 | 0.4 | n |  | TRUE
14 | bus_LV_2055-4_0_4_node_48 | 0.4 | n |  | TRUE
15 | bus_LV_2055-4_0_4_node_190 | 0.4 | n |  | TRUE
16 | bus_LV_2055-4_0_4_node_246 | 0.4 | n |  | TRUE
17 | bus_LV_2055-4_0_4_node_92 | 0.4 | n |  | TRUE
18 | bus_LV_2055-4_0_4_node_139 | 0.4 | n |  | TRUE
19 | bus_LV_2055-4_0_4_node_182 | 0.4 | n |  | TRUE
20 | bus_LV_2055-4_0_4_node_114 | 0.4 | n |  | TRUE
21 | bus_LV_2055-4_0_4_node_168 | 0.4 | n |  | TRUE
22 | bus_LV_2055-4_0_4_node_4 | 0.4 | n |  | TRUE
23 | bus_LV_2055-4_0_4_node_118 | 0.4 | n |  | TRUE
24 | bus_LV_2055-4_0_4_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_2055-4_0_4_node_163 | 0.4 | n |  | TRUE
26 | bus_LV_2055-4_0_4_node_240 | 0.4 | n |  | TRUE
27 | bus_LV_2055-4_0_4_node_5 | 0.4 | n |  | TRUE
28 | bus_LV_2055-4_0_4_node_119 | 0.4 | n |  | TRUE
29 | bus_LV_2055-4_0_4_node_164 | 0.4 | n |  | TRUE
30 | bus_LV_2055-4_0_4_node_222 | 0.4 | n |  | TRUE
31 | bus_LV_2055-4_0_4_node_86 | 0.4 | n |  | TRUE
32 | bus_LV_2055-4_0_4_node_133 | 0.4 | n |  | TRUE
33 | bus_LV_2055-4_0_4_node_6 | 0.4 | n |  | TRUE
34 | bus_LV_2055-4_0_4_node_206 | 0.4 | n |  | TRUE
35 | bus_LV_2055-4_0_4_node_71 | 0.4 | n |  | TRUE
36 | bus_LV_2055-4_0_4_node_244 | 0.4 | n |  | TRUE
37 | bus_LV_2055-4_0_4_node_75 | 0.4 | n |  | TRUE
38 | bus_LV_2055-4_0_4_node_106 | 0.4 | n |  | TRUE
39 | bus_LV_2055-4_0_4_node_7 | 0.4 | n |  | TRUE
40 | bus_LV_2055-4_0_4_node_91 | 0.4 | n |  | TRUE
41 | bus_LV_2055-4_0_4_node_181 | 0.4 | n |  | TRUE
42 | bus_LV_2055-4_0_4_node_8 | 0.4 | n |  | TRUE
43 | bus_LV_2055-4_0_4_node_94 | 0.4 | n |  | TRUE
44 | bus_LV_2055-4_0_4_node_252 | 0.4 | n |  | TRUE
45 | bus_LV_2055-4_0_4_node_179 | 0.4 | n |  | TRUE
46 | bus_LV_2055-4_0_4_node_13 | 0.4 | n |  | TRUE
47 | bus_LV_2055-4_0_4_node_122 | 0.4 | n |  | TRUE
48 | bus_LV_2055-4_0_4_node_9 | 0.4 | n |  | TRUE
49 | bus_LV_2055-4_0_4_node_155 | 0.4 | n |  | TRUE
50 | bus_LV_2055-4_0_4_node_144 | 0.4 | n |  | TRUE
51 | bus_LV_2055-4_0_4_node_108 | 0.4 | n |  | TRUE
52 | bus_LV_2055-4_0_4_node_186 | 0.4 | n |  | TRUE
53 | bus_LV_2055-4_0_4_node_10 | 0.4 | n |  | TRUE
54 | bus_LV_2055-4_0_4_node_145 | 0.4 | n |  | TRUE
55 | bus_LV_2055-4_0_4_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_2055-4_0_4_node_237 | 0.4 | n |  | TRUE
57 | bus_LV_2055-4_0_4_node_130 | 0.4 | n |  | TRUE
58 | bus_LV_2055-4_0_4_node_11 | 0.4 | n |  | TRUE
59 | bus_LV_2055-4_0_4_node_16 | 0.4 | n |  | TRUE
60 | bus_LV_2055-4_0_4_node_203 | 0.4 | n |  | TRUE
61 | bus_LV_2055-4_0_4_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_2055-4_0_4_node_201 | 0.4 | n |  | TRUE
63 | bus_LV_2055-4_0_4_node_12 | 0.4 | n |  | TRUE
64 | bus_LV_2055-4_0_4_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_2055-4_0_4_node_80 | 0.4 | n |  | TRUE
66 | bus_LV_2055-4_0_4_node_156 | 0.4 | n |  | TRUE
67 | bus_LV_2055-4_0_4_node_84 | 0.4 | n |  | TRUE
68 | bus_LV_2055-4_0_4_node_174 | 0.4 | n |  | TRUE
69 | bus_LV_2055-4_0_4_node_229 | 0.4 | n |  | TRUE
70 | bus_LV_2055-4_0_4_node_29 | 0.4 | n |  | TRUE
71 | bus_LV_2055-4_0_4_node_14 | 0.4 | n |  | TRUE
72 | bus_LV_2055-4_0_4_node_159 | 0.4 | n |  | TRUE
73 | bus_LV_2055-4_0_4_node_205 | 0.4 | n |  | TRUE
74 | bus_LV_2055-4_0_4_node_225 | 0.4 | n |  | TRUE
75 | bus_LV_2055-4_0_4_node_137 | 0.4 | n |  | TRUE
76 | bus_LV_2055-4_0_4_node_152 | 0.4 | n |  | TRUE
77 | bus_LV_2055-4_0_4_node_236 | 0.4 | n |  | TRUE
78 | bus_LV_2055-4_0_4_node_15 | 0.4 | n |  | TRUE
79 | bus_LV_2055-4_0_4_node_37 | 0.4 | n |  | TRUE
80 | bus_LV_2055-4_0_4_node_176 | 0.4 | n |  | TRUE
81 | bus_LV_2055-4_0_4_node_217 | 0.4 | n |  | TRUE
82 | bus_LV_2055-4_0_4_node_59 | 0.4 | n |  | TRUE
83 | bus_LV_2055-4_0_4_node_101 | 0.4 | n |  | TRUE
84 | bus_LV_2055-4_0_4_node_36 | 0.4 | n |  | TRUE
85 | bus_LV_2055-4_0_4_node_129 | 0.4 | n |  | TRUE
86 | bus_LV_2055-4_0_4_node_73 | 0.4 | n |  | TRUE
87 | bus_LV_2055-4_0_4_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_2055-4_0_4_node_249 | 0.4 | n |  | TRUE
89 | bus_LV_2055-4_0_4_node_17 | 0.4 | n |  | TRUE
90 | bus_LV_2055-4_0_4_node_66 | 0.4 | n |  | TRUE
91 | bus_LV_2055-4_0_4_node_35 | 0.4 | n |  | TRUE
92 | bus_LV_2055-4_0_4_node_72 | 0.4 | n |  | TRUE
93 | bus_LV_2055-4_0_4_node_109 | 0.4 | n |  | TRUE
94 | bus_LV_2055-4_0_4_node_18 | 0.4 | n |  | TRUE
95 | bus_LV_2055-4_0_4_node_39 | 0.4 | n |  | TRUE
96 | bus_LV_2055-4_0_4_node_171 | 0.4 | n |  | TRUE
97 | bus_LV_2055-4_0_4_node_243 | 0.4 | n |  | TRUE
98 | bus_LV_2055-4_0_4_node_19 | 0.4 | n |  | TRUE
99 | bus_LV_2055-4_0_4_node_223 | 0.4 | n |  | TRUE
100 | bus_LV_2055-4_0_4_node_41 | 0.4 | n |  | TRUE
101 | bus_LV_2055-4_0_4_node_20 | 0.4 | n |  | TRUE
102 | bus_LV_2055-4_0_4_node_62 | 0.4 | n |  | TRUE
103 | bus_LV_2055-4_0_4_node_224 | 0.4 | n |  | TRUE
104 | bus_LV_2055-4_0_4_node_21 | 0.4 | n |  | TRUE
105 | bus_LV_2055-4_0_4_node_24 | 0.4 | n |  | TRUE
106 | bus_LV_2055-4_0_4_node_218 | 0.4 | n |  | TRUE
107 | bus_LV_2055-4_0_4_node_98 | 0.4 | n |  | TRUE
108 | bus_LV_2055-4_0_4_node_54 | 0.4 | n |  | TRUE
109 | bus_LV_2055-4_0_4_node_184 | 0.4 | n |  | TRUE
110 | bus_LV_2055-4_0_4_node_22 | 0.4 | n |  | TRUE
111 | bus_LV_2055-4_0_4_node_26 | 0.4 | n |  | TRUE
112 | bus_LV_2055-4_0_4_node_221 | 0.4 | n |  | TRUE
113 | bus_LV_2055-4_0_4_node_136 | 0.4 | n |  | TRUE
114 | bus_LV_2055-4_0_4_node_198 | 0.4 | n |  | TRUE
115 | bus_LV_2055-4_0_4_node_23 | 0.4 | n |  | TRUE
116 | bus_LV_2055-4_0_4_node_158 | 0.4 | n |  | TRUE
117 | bus_LV_2055-4_0_4_node_147 | 0.4 | n |  | TRUE
118 | bus_LV_2055-4_0_4_node_47 | 0.4 | n |  | TRUE
119 | bus_LV_2055-4_0_4_node_25 | 0.4 | n |  | TRUE
120 | bus_LV_2055-4_0_4_node_255 | 0.4 | n |  | TRUE
121 | bus_LV_2055-4_0_4_node_254 | 0.4 | n |  | TRUE
122 | bus_LV_2055-4_0_4_node_49 | 0.4 | n |  | TRUE
123 | bus_LV_2055-4_0_4_node_165 | 0.4 | n |  | TRUE
124 | bus_LV_2055-4_0_4_node_178 | 0.4 | n |  | TRUE
125 | bus_LV_2055-4_0_4_node_28 | 0.4 | n |  | TRUE
126 | bus_LV_2055-4_0_4_node_143 | 0.4 | n |  | TRUE
127 | bus_LV_2055-4_0_4_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_2055-4_0_4_node_93 | 0.4 | n |  | TRUE
129 | bus_LV_2055-4_0_4_node_169 | 0.4 | n |  | TRUE
130 | bus_LV_2055-4_0_4_node_228 | 0.4 | n |  | TRUE
131 | bus_LV_2055-4_0_4_node_30 | 0.4 | n |  | TRUE
132 | bus_LV_2055-4_0_4_node_113 | 0.4 | n |  | TRUE
133 | bus_LV_2055-4_0_4_node_100 | 0.4 | n |  | TRUE
134 | bus_LV_2055-4_0_4_node_31 | 0.4 | n |  | TRUE
135 | bus_LV_2055-4_0_4_node_215 | 0.4 | n |  | TRUE
136 | bus_LV_2055-4_0_4_node_103 | 0.4 | n |  | TRUE
137 | bus_LV_2055-4_0_4_node_34 | 0.4 | n |  | TRUE
138 | bus_LV_2055-4_0_4_node_121 | 0.4 | n |  | TRUE
139 | bus_LV_2055-4_0_4_node_33 | 0.4 | n |  | TRUE
140 | bus_LV_2055-4_0_4_node_55 | 0.4 | n |  | TRUE
141 | bus_LV_2055-4_0_4_node_192 | 0.4 | n |  | TRUE
142 | bus_LV_2055-4_0_4_node_88 | 0.4 | n |  | TRUE
143 | bus_LV_2055-4_0_4_node_234 | 0.4 | n |  | TRUE
144 | bus_LV_2055-4_0_4_node_112 | 0.4 | n |  | TRUE
145 | bus_LV_2055-4_0_4_node_166 | 0.4 | n |  | TRUE
146 | bus_LV_2055-4_0_4_node_82 | 0.4 | n |  | TRUE
147 | bus_LV_2055-4_0_4_node_38 | 0.4 | n |  | TRUE
148 | bus_LV_2055-4_0_4_node_141 | 0.4 | n |  | TRUE
149 | bus_LV_2055-4_0_4_node_40 | 0.4 | n |  | TRUE
150 | bus_LV_2055-4_0_4_node_232 | 0.4 | n |  | TRUE
151 | bus_LV_2055-4_0_4_node_259 | 0.4 | n |  | TRUE
152 | bus_LV_2055-4_0_4_node_231 | 0.4 | n |  | TRUE
153 | bus_LV_2055-4_0_4_node_247 | 0.4 | n |  | TRUE
154 | bus_LV_2055-4_0_4_node_42 | 0.4 | n |  | TRUE
155 | bus_LV_2055-4_0_4_node_110 | 0.4 | n |  | TRUE
156 | bus_LV_2055-4_0_4_node_183 | 0.4 | n |  | TRUE
157 | bus_LV_2055-4_0_4_node_69 | 0.4 | n |  | TRUE
158 | bus_LV_2055-4_0_4_node_43 | 0.4 | n |  | TRUE
159 | bus_LV_2055-4_0_4_node_102 | 0.4 | n |  | TRUE
160 | bus_LV_2055-4_0_4_node_251 | 0.4 | n |  | TRUE
161 | bus_LV_2055-4_0_4_node_44 | 0.4 | n |  | TRUE
162 | bus_LV_2055-4_0_4_node_64 | 0.4 | n |  | TRUE
163 | bus_LV_2055-4_0_4_node_46 | 0.4 | n |  | TRUE
164 | bus_LV_2055-4_0_4_node_131 | 0.4 | n |  | TRUE
165 | bus_LV_2055-4_0_4_node_87 | 0.4 | n |  | TRUE
166 | bus_LV_2055-4_0_4_node_210 | 0.4 | n |  | TRUE
167 | bus_LV_2055-4_0_4_node_194 | 0.4 | n |  | TRUE
168 | bus_LV_2055-4_0_4_node_96 | 0.4 | n |  | TRUE
169 | bus_LV_2055-4_0_4_node_123 | 0.4 | n |  | TRUE
170 | bus_LV_2055-4_0_4_node_127 | 0.4 | n |  | TRUE
171 | bus_LV_2055-4_0_4_node_90 | 0.4 | n |  | TRUE
172 | bus_LV_2055-4_0_4_node_70 | 0.4 | n |  | TRUE
173 | bus_LV_2055-4_0_4_node_197 | 0.4 | n |  | TRUE
174 | bus_LV_2055-4_0_4_node_50 | 0.4 | n |  | TRUE
175 | bus_LV_2055-4_0_4_node_85 | 0.4 | n |  | TRUE
176 | bus_LV_2055-4_0_4_node_256 | 0.4 | n |  | TRUE
177 | bus_LV_2055-4_0_4_node_125 | 0.4 | n |  | TRUE
178 | bus_LV_2055-4_0_4_node_213 | 0.4 | n |  | TRUE
179 | bus_LV_2055-4_0_4_node_51 | 0.4 | n |  | TRUE
180 | bus_LV_2055-4_0_4_node_180 | 0.4 | n |  | TRUE
181 | bus_LV_2055-4_0_4_node_173 | 0.4 | n |  | TRUE
182 | bus_LV_2055-4_0_4_node_74 | 0.4 | n |  | TRUE
183 | bus_LV_2055-4_0_4_node_149 | 0.4 | n |  | TRUE
184 | bus_LV_2055-4_0_4_node_95 | 0.4 | n |  | TRUE
185 | bus_LV_2055-4_0_4_node_116 | 0.4 | n |  | TRUE
186 | bus_LV_2055-4_0_4_node_157 | 0.4 | n |  | TRUE
187 | bus_LV_2055-4_0_4_node_56 | 0.4 | n |  | TRUE
188 | bus_LV_2055-4_0_4_node_188 | 0.4 | n |  | TRUE
189 | bus_LV_2055-4_0_4_node_200 | 0.4 | n |  | TRUE
190 | bus_LV_2055-4_0_4_node_209 | 0.4 | n |  | TRUE
191 | bus_LV_2055-4_0_4_node_242 | 0.4 | n |  | TRUE
192 | bus_LV_2055-4_0_4_node_57 | 0.4 | n |  | TRUE
193 | bus_LV_2055-4_0_4_node_65 | 0.4 | n |  | TRUE
194 | bus_LV_2055-4_0_4_node_199 | 0.4 | n |  | TRUE
195 | bus_LV_2055-4_0_4_node_208 | 0.4 | n |  | TRUE
196 | bus_LV_2055-4_0_4_node_58 | 0.4 | n |  | TRUE
197 | bus_LV_2055-4_0_4_node_189 | 0.4 | n |  | TRUE
198 | bus_LV_2055-4_0_4_node_238 | 0.4 | n |  | TRUE
199 | bus_LV_2055-4_0_4_node_193 | 0.4 | n |  | TRUE
200 | bus_LV_2055-4_0_4_node_154 | 0.4 | n |  | TRUE
201 | bus_LV_2055-4_0_4_node_67 | 0.4 | n |  | TRUE
202 | bus_LV_2055-4_0_4_node_60 | 0.4 | n |  | TRUE
203 | bus_LV_2055-4_0_4_node_61 | 0.4 | n |  | TRUE
204 | bus_LV_2055-4_0_4_node_216 | 0.4 | n |  | TRUE
205 | bus_LV_2055-4_0_4_node_132 | 0.4 | n |  | TRUE
206 | bus_LV_2055-4_0_4_node_63 | 0.4 | n |  | TRUE
207 | bus_LV_2055-4_0_4_node_140 | 0.4 | n |  | TRUE
208 | bus_LV_2055-4_0_4_node_135 | 0.4 | n |  | TRUE
209 | bus_LV_2055-4_0_4_node_195 | 0.4 | n |  | TRUE
210 | bus_LV_2055-4_0_4_node_207 | 0.4 | n |  | TRUE
211 | bus_LV_2055-4_0_4_node_68 | 0.4 | n |  | TRUE
212 | bus_LV_2055-4_0_4_node_167 | 0.4 | n |  | TRUE
213 | bus_LV_2055-4_0_4_node_220 | 0.4 | n |  | TRUE
214 | bus_LV_2055-4_0_4_node_253 | 0.4 | n |  | TRUE
215 | bus_LV_2055-4_0_4_node_230 | 0.4 | n |  | TRUE
216 | bus_LV_2055-4_0_4_node_187 | 0.4 | n |  | TRUE
217 | bus_LV_2055-4_0_4_node_76 | 0.4 | n |  | TRUE
218 | bus_LV_2055-4_0_4_node_124 | 0.4 | n |  | TRUE
219 | bus_LV_2055-4_0_4_node_150 | 0.4 | n |  | TRUE
220 | bus_LV_2055-4_0_4_node_78 | 0.4 | n |  | TRUE
221 | bus_LV_2055-4_0_4_node_235 | 0.4 | n |  | TRUE
222 | bus_LV_2055-4_0_4_node_99 | 0.4 | n |  | TRUE
223 | bus_LV_2055-4_0_4_node_226 | 0.4 | n |  | TRUE
224 | bus_LV_2055-4_0_4_node_79 | 0.4 | n |  | TRUE
225 | bus_LV_2055-4_0_4_node_245 | 0.4 | n |  | TRUE
226 | bus_LV_2055-4_0_4_node_248 | 0.4 | n |  | TRUE
227 | bus_LV_2055-4_0_4_node_107 | 0.4 | n |  | TRUE
228 | bus_LV_2055-4_0_4_node_81 | 0.4 | n |  | TRUE
229 | bus_LV_2055-4_0_4_node_202 | 0.4 | n |  | TRUE
230 | bus_LV_2055-4_0_4_node_83 | 0.4 | n |  | TRUE
231 | bus_LV_2055-4_0_4_node_212 | 0.4 | n |  | TRUE
232 | bus_LV_2055-4_0_4_node_250 | 0.4 | n |  | TRUE
233 | bus_LV_2055-4_0_4_node_89 | 0.4 | n |  | TRUE
234 | bus_LV_2055-4_0_4_node_214 | 0.4 | n |  | TRUE
235 | bus_LV_2055-4_0_4_node_258 | 0.4 | n |  | TRUE
236 | bus_LV_2055-4_0_4_node_134 | 0.4 | n |  | TRUE
237 | bus_LV_2055-4_0_4_node_170 | 0.4 | n |  | TRUE
238 | bus_LV_2055-4_0_4_node_219 | 0.4 | n |  | TRUE
239 | bus_LV_2055-4_0_4_node_160 | 0.4 | n |  | TRUE
240 | bus_LV_2055-4_0_4_node_196 | 0.4 | n |  | TRUE
241 | bus_LV_2055-4_0_4_node_227 | 0.4 | n |  | TRUE
242 | bus_LV_2055-4_0_4_node_104 | 0.4 | n |  | TRUE
243 | bus_LV_2055-4_0_4_node_233 | 0.4 | n |  | TRUE
244 | bus_LV_2055-4_0_4_node_105 | 0.4 | n |  | TRUE
245 | bus_LV_2055-4_0_4_node_146 | 0.4 | n |  | TRUE
246 | bus_LV_2055-4_0_4_node_177 | 0.4 | n |  | TRUE
247 | bus_LV_2055-4_0_4_node_126 | 0.4 | n |  | TRUE
248 | bus_LV_2055-4_0_4_node_117 | 0.4 | n |  | TRUE
249 | bus_LV_2055-4_0_4_node_185 | 0.4 | n |  | TRUE
250 | bus_LV_2055-4_0_4_node_241 | 0.4 | n |  | TRUE
251 | bus_LV_2055-4_0_4_node_239 | 0.4 | n |  | TRUE
252 | bus_LV_2055-4_0_4_node_138 | 0.4 | n |  | TRUE
253 | bus_LV_2055-4_0_4_node_161 | 0.4 | n |  | TRUE
254 | bus_LV_2055-4_0_4_node_172 | 0.4 | n |  | TRUE
255 | bus_MV_454_0_node_194 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2055-4_0_4_load_0 | 0 | 0.0043729 | 0.0010959 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2055-4_0_4_load_153 | 3 | 0.00033513 | 8.3992e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2055-4_0_4_load_204 | 7 | 0.00010662 | 2.6722e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2055-4_0_4_load_128 | 8 | 0.00018197 | 4.5605e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2055-4_0_4_load_111 | 9 | 0.00010576 | 2.6505e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2055-4_0_4_load_162 | 10 | 0.0006798 | 0.00017038 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2055-4_0_4_load_120 | 11 | 0.00027171 | 6.8098e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2055-4_0_4_load_97 | 13 | 0.00018952 | 4.7497e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2055-4_0_4_load_190 | 15 | 0.00044437 | 0.00011137 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2055-4_0_4_load_92 | 17 | 0.00033659 | 8.4358e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2055-4_0_4_load_182 | 19 | 0.00016763 | 4.2013e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2055-4_0_4_load_114 | 20 | 0.0017126 | 0.00042922 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2055-4_0_4_load_168 | 21 | 0.00010428 | 2.6135e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2055-4_0_4_load_4 | 22 | 0.00032437 | 8.1296e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2055-4_0_4_load_32 | 24 | 0.00025241 | 6.3261e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2055-4_0_4_load_163 | 25 | 0.00034527 | 8.6534e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2055-4_0_4_load_240 | 26 | 0.00028287 | 7.0894e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2055-4_0_4_load_5 | 27 | 0.00041736 | 0.0001046 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2055-4_0_4_load_119 | 28 | 0.00026835 | 6.7254e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2055-4_0_4_load_222 | 30 | 0.00039405 | 9.8758e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2055-4_0_4_load_86 | 31 | 0.00029089 | 7.2905e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2055-4_0_4_load_6 | 33 | 0.00019337 | 4.8464e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2055-4_0_4_load_244 | 36 | 0.00015719 | 3.9397e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2055-4_0_4_load_7 | 39 | 0.00028616 | 7.1718e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2055-4_0_4_load_91 | 40 | 9.4064e-05 | 2.3575e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2055-4_0_4_load_181 | 41 | 0.00015207 | 3.8113e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2055-4_0_4_load_252 | 44 | 0.00052756 | 0.00013222 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2055-4_0_4_load_13 | 46 | 0.00022585 | 5.6603e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2055-4_0_4_load_122 | 47 | 0.0016113 | 0.00040382 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2055-4_0_4_load_9 | 48 | 0.00093893 | 0.00023532 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2055-4_0_4_load_155 | 49 | 0.00029889 | 7.491e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2055-4_0_4_load_144 | 50 | 0.00036592 | 9.1709e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2055-4_0_4_load_108 | 51 | 0.00046167 | 0.00011571 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2055-4_0_4_load_186 | 52 | 0.00032359 | 8.11e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2055-4_0_4_load_10 | 53 | 0.00041101 | 0.00010301 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2055-4_0_4_load_27 | 55 | 0.00061831 | 0.00015496 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2055-4_0_4_load_237 | 56 | 0.00048557 | 0.0001217 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2055-4_0_4_load_130 | 57 | 0.00054401 | 0.00013634 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2055-4_0_4_load_11 | 58 | 0.0002918 | 7.3133e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2055-4_0_4_load_16 | 59 | 0.00017108 | 4.2876e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2055-4_0_4_load_203 | 60 | 0.00027392 | 6.8651e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2055-4_0_4_load_201 | 62 | 0.00034681 | 8.6918e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2055-4_0_4_load_52 | 64 | 0.0017437 | 0.00043701 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2055-4_0_4_load_80 | 65 | 0.0016701 | 0.00041858 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2055-4_0_4_load_156 | 66 | 0.0022247 | 0.00055756 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2055-4_0_4_load_174 | 68 | 0.0098894 | 0.0024785 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2055-4_0_4_load_29 | 70 | 0.0025718 | 0.00064455 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2055-4_0_4_load_14 | 71 | 8.3537e-05 | 2.0936e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2055-4_0_4_load_205 | 73 | 0.00010348 | 2.5934e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2055-4_0_4_load_137 | 75 | 0.00011475 | 2.876e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2055-4_0_4_load_152 | 76 | 0.00013921 | 3.489e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2055-4_0_4_load_236 | 77 | 0.00024948 | 6.2525e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2055-4_0_4_load_37 | 79 | 0.0026293 | 0.00065896 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2055-4_0_4_load_217 | 81 | 0.0020943 | 0.00052488 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2055-4_0_4_load_36 | 84 | 0.0016918 | 0.000424 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2055-4_0_4_load_129 | 85 | 0.0020394 | 0.00051112 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2055-4_0_4_load_77 | 87 | 0.0010563 | 0.00026474 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2055-4_0_4_load_249 | 88 | 0.0011382 | 0.00028526 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2055-4_0_4_load_17 | 89 | 0.00035162 | 8.8123e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2055-4_0_4_load_66 | 90 | 0.00047257 | 0.00011844 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2055-4_0_4_load_35 | 91 | 0.00032775 | 8.2143e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2055-4_0_4_load_72 | 92 | 0.0014637 | 0.00036684 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2055-4_0_4_load_109 | 93 | 0.00025961 | 6.5065e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2055-4_0_4_load_18 | 94 | 0.00018066 | 4.5277e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2055-4_0_4_load_39 | 95 | 0.00032292 | 8.093e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2055-4_0_4_load_171 | 96 | 0.00017573 | 4.4043e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2055-4_0_4_load_243 | 97 | 0.00017173 | 4.304e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2055-4_0_4_load_19 | 98 | 0.0002306 | 5.7795e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2055-4_0_4_load_223 | 99 | 0.00017851 | 4.4739e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2055-4_0_4_load_41 | 100 | 0.00017098 | 4.285e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2055-4_0_4_load_20 | 101 | 0.00028514 | 7.1462e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2055-4_0_4_load_62 | 102 | 0.00044107 | 0.00011054 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2055-4_0_4_load_224 | 103 | 0.00026836 | 6.7257e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2055-4_0_4_load_21 | 104 | 0.001148 | 0.00028771 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2055-4_0_4_load_24 | 105 | 0.0015148 | 0.00037965 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2055-4_0_4_load_218 | 106 | 0.0017834 | 0.00044696 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2055-4_0_4_load_98 | 107 | 0.0011862 | 0.0002973 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2055-4_0_4_load_54 | 108 | 0.00074459 | 0.00018661 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2055-4_0_4_load_184 | 109 | 0.0019965 | 0.00050036 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2055-4_0_4_load_22 | 110 | 0.00029528 | 7.4005e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2055-4_0_4_load_26 | 111 | 0.0003982 | 9.9798e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2055-4_0_4_load_221 | 112 | 0.0003162 | 7.9248e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2055-4_0_4_load_136 | 113 | 0.00036945 | 9.2594e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2055-4_0_4_load_198 | 114 | 0.00017496 | 4.385e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2055-4_0_4_load_23 | 115 | 0.00015447 | 3.8713e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2055-4_0_4_load_158 | 116 | 0.00016905 | 4.2369e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2055-4_0_4_load_147 | 117 | 0.00030191 | 7.5665e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2055-4_0_4_load_47 | 118 | 0.0038825 | 0.00097304 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2055-4_0_4_load_255 | 120 | 0.00063028 | 0.00015796 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2055-4_0_4_load_49 | 122 | 0.00036803 | 9.2238e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2055-4_0_4_load_165 | 123 | 0.00030835 | 7.7281e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2055-4_0_4_load_178 | 124 | 0.00041236 | 0.00010335 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2055-4_0_4_load_28 | 125 | 0.00072515 | 0.00018174 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2055-4_0_4_load_143 | 126 | 0.00053871 | 0.00013501 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2055-4_0_4_load_115 | 127 | 0.00029135 | 7.3019e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2055-4_0_4_load_169 | 129 | 0.00032272 | 8.088e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2055-4_0_4_load_228 | 130 | 0.0020959 | 0.00052528 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2055-4_0_4_load_30 | 131 | 0.00026176 | 6.5603e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2055-4_0_4_load_113 | 132 | 0.00021186 | 5.3096e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2055-4_0_4_load_215 | 135 | 0.00081051 | 0.00020313 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2055-4_0_4_load_34 | 137 | 0.00035154 | 8.8103e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2055-4_0_4_load_121 | 138 | 0.00079485 | 0.00019921 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2055-4_0_4_load_33 | 139 | 0.0019818 | 0.00049668 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2055-4_0_4_load_55 | 140 | 0.00022521 | 5.6443e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2055-4_0_4_load_192 | 141 | 0.00060479 | 0.00015157 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2055-4_0_4_load_88 | 142 | 0.0004775 | 0.00011967 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2055-4_0_4_load_234 | 143 | 0.00038618 | 9.6785e-05 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2055-4_0_4_load_112 | 144 | 0.00026274 | 6.585e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2055-4_0_4_load_166 | 145 | 0.00029786 | 7.4651e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2055-4_0_4_load_38 | 147 | 0.00019072 | 4.78e-05 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2055-4_0_4_load_141 | 148 | 0.00038734 | 9.7076e-05 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2055-4_0_4_load_40 | 149 | 0.0001676 | 4.2006e-05 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2055-4_0_4_load_232 | 150 | 0.00019435 | 4.8708e-05 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2055-4_0_4_load_259 | 151 | 0.00020133 | 5.0457e-05 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2055-4_0_4_load_231 | 152 | 0.00031786 | 7.9663e-05 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2055-4_0_4_load_247 | 153 | 0.00018911 | 4.7395e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2055-4_0_4_load_42 | 154 | 0.00032681 | 8.1908e-05 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2055-4_0_4_load_110 | 155 | 0.00050512 | 0.0001266 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2055-4_0_4_load_183 | 156 | 0.00040336 | 0.00010109 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2055-4_0_4_load_69 | 157 | 0.00029535 | 7.4022e-05 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2055-4_0_4_load_43 | 158 | 0.00035897 | 8.9967e-05 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2055-4_0_4_load_102 | 159 | 0.00046664 | 0.00011695 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2055-4_0_4_load_251 | 160 | 0.00028755 | 7.2066e-05 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2055-4_0_4_load_44 | 161 | 0.000847 | 0.00021228 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2055-4_0_4_load_64 | 162 | 0.0017962 | 0.00045017 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2055-4_0_4_load_46 | 163 | 0.00041342 | 0.00010361 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2055-4_0_4_load_131 | 164 | 0.00084098 | 0.00021077 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2055-4_0_4_load_87 | 165 | 0.0006665 | 0.00016704 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2055-4_0_4_load_194 | 167 | 0.0015882 | 0.00039803 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2055-4_0_4_load_96 | 168 | 0.0036115 | 0.00090512 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2055-4_0_4_load_123 | 169 | 0.0035091 | 0.00087945 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2055-4_0_4_load_127 | 170 | 0.034308 | 0.0085983 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2055-4_0_4_load_70 | 172 | 0.00038663 | 9.6898e-05 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2055-4_0_4_load_197 | 173 | 0.0004471 | 0.00011205 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2055-4_0_4_load_50 | 174 | 0.00023139 | 5.7991e-05 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2055-4_0_4_load_85 | 175 | 0.00019969 | 5.0047e-05 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2055-4_0_4_load_256 | 176 | 0.00024692 | 6.1883e-05 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2055-4_0_4_load_125 | 177 | 0.00025027 | 6.2723e-05 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_2055-4_0_4_load_213 | 178 | 0.00027947 | 7.0041e-05 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_2055-4_0_4_load_180 | 180 | 0.0019074 | 0.00047804 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_2055-4_0_4_load_173 | 181 | 0.0033948 | 0.00085083 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_2055-4_0_4_load_74 | 182 | 0.0016707 | 0.00041871 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_2055-4_0_4_load_149 | 183 | 0.0024744 | 0.00062015 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_2055-4_0_4_load_95 | 184 | 0.0023141 | 0.00057997 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_2055-4_0_4_load_116 | 185 | 0.00020096 | 5.0364e-05 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_2055-4_0_4_load_157 | 186 | 0.00028906 | 7.2446e-05 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_2055-4_0_4_load_56 | 187 | 0.00072539 | 0.0001818 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_2055-4_0_4_load_188 | 188 | 0.00069469 | 0.00017411 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_2055-4_0_4_load_200 | 189 | 0.00069464 | 0.00017409 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_2055-4_0_4_load_209 | 190 | 0.00059094 | 0.0001481 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_2055-4_0_4_load_242 | 191 | 0.0017959 | 0.0004501 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_2055-4_0_4_load_199 | 194 | 0.0027478 | 0.00068866 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_2055-4_0_4_load_208 | 195 | 0.0016289 | 0.00040824 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_2055-4_0_4_load_58 | 196 | 0.0017956 | 0.00045002 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_2055-4_0_4_load_189 | 197 | 0.0017153 | 0.00042989 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_2055-4_0_4_load_238 | 198 | 0.001713 | 0.00042932 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_2055-4_0_4_load_193 | 199 | 0.0017951 | 0.0004499 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_2055-4_0_4_load_154 | 200 | 0.001796 | 0.00045011 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_2055-4_0_4_load_67 | 201 | 0.0010219 | 0.00025612 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_2055-4_0_4_load_60 | 202 | 0.00026528 | 6.6485e-05 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_2055-4_0_4_load_216 | 204 | 0.00019255 | 4.8258e-05 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_2055-4_0_4_load_132 | 205 | 0.00027667 | 6.934e-05 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_2055-4_0_4_load_63 | 206 | 0.0012031 | 0.00030153 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_2055-4_0_4_load_135 | 208 | 0.0016185 | 0.00040563 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_2055-4_0_4_load_195 | 209 | 0.0015843 | 0.00039705 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_2055-4_0_4_load_207 | 210 | 0.00029589 | 7.4158e-05 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_2055-4_0_4_load_68 | 211 | 0.0021615 | 0.00054172 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_2055-4_0_4_load_167 | 212 | 0.00087479 | 0.00021924 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_2055-4_0_4_load_220 | 213 | 0.00039428 | 9.8816e-05 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_2055-4_0_4_load_253 | 214 | 0.00026417 | 6.6207e-05 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_2055-4_0_4_load_230 | 215 | 0.00037601 | 9.4237e-05 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_2055-4_0_4_load_187 | 216 | 0.0021431 | 0.0005371 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_2055-4_0_4_load_76 | 217 | 0.0017433 | 0.0004369 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_2055-4_0_4_load_124 | 218 | 0.0017136 | 0.00042947 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_2055-4_0_4_load_78 | 220 | 0.0003398 | 8.5161e-05 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_2055-4_0_4_load_235 | 221 | 0.00037127 | 9.3049e-05 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_2055-4_0_4_load_99 | 222 | 0.00027493 | 6.8904e-05 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_2055-4_0_4_load_226 | 223 | 0.00032548 | 8.1573e-05 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_2055-4_0_4_load_79 | 224 | 0.00020447 | 5.1245e-05 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_2055-4_0_4_load_248 | 226 | 0.0014141 | 0.00035442 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_2055-4_0_4_load_107 | 227 | 8.6289e-05 | 2.1626e-05 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_2055-4_0_4_load_81 | 228 | 0.00012964 | 3.249e-05 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_2055-4_0_4_load_202 | 229 | 0.0011777 | 0.00029515 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_2055-4_0_4_load_83 | 230 | 0.0015271 | 0.00038273 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_2055-4_0_4_load_250 | 232 | 0.00027852 | 6.9804e-05 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_2055-4_0_4_load_89 | 233 | 0.0017962 | 0.00045017 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_2055-4_0_4_load_214 | 234 | 0.001714 | 0.00042957 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_2055-4_0_4_load_258 | 235 | 0.00012228 | 3.0646e-05 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_2055-4_0_4_load_134 | 236 | 0.00018767 | 4.7036e-05 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_2055-4_0_4_load_219 | 238 | 0.00013154 | 3.2967e-05 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_2055-4_0_4_load_160 | 239 | 0.00025877 | 6.4854e-05 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_2055-4_0_4_load_196 | 240 | 0.026827 | 0.0067236 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_2055-4_0_4_load_227 | 241 | 0.00029406 | 7.3698e-05 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_2055-4_0_4_load_104 | 242 | 0.0019715 | 0.00049409 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_2055-4_0_4_load_105 | 244 | 0.00056616 | 0.00014189 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_2055-4_0_4_load_146 | 245 | 0.0039226 | 0.00098311 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_2055-4_0_4_load_177 | 246 | 0.00053928 | 0.00013516 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_2055-4_0_4_load_126 | 247 | 0.00020834 | 5.2215e-05 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_2055-4_0_4_load_117 | 248 | 0.00014502 | 3.6344e-05 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_2055-4_0_4_load_241 | 250 | 0.00012841 | 3.2183e-05 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_2055-4_0_4_load_239 | 251 | 0.00079271 | 0.00019867 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_2055-4_0_4_load_138 | 252 | 0.00030887 | 7.7409e-05 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_2055-4_0_4_load_161 | 253 | 0.00040475 | 0.00010144 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_2055-4_0_4_load_172 | 254 | 0.00026543 | 6.6523e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 162 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2055-4_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.008307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2055-4_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.002613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2055-4_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.018625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2055-4_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.055406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2055-4_0_4_line_4 | NAYY 4x150 SE | 3 | 101 | 0.012139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2055-4_0_4_line_5 | NAYY 4x150 SE | 4 | 51 | 0.0050301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2055-4_0_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.005991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2055-4_0_4_line_7 | NAYY 4x150 SE | 5 | 7 | 0.008925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2055-4_0_4_line_8 | NAYY 4x150 SE | 5 | 8 | 0.014857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2055-4_0_4_line_9 | NAYY 4x150 SE | 6 | 9 | 0.016094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2055-4_0_4_line_10 | NAYY 4x150 SE | 6 | 10 | 0.012716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2055-4_0_4_line_11 | NAYY 4x150 SE | 8 | 11 | 0.017415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2055-4_0_4_line_12 | NAYY 4x150 SE | 9 | 131 | 0.0043384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2055-4_0_4_line_13 | NAYY 4x150 SE | 11 | 46 | 0.014236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2055-4_0_4_line_14 | NAYY 4x150 SE | 12 | 13 | 0.021559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2055-4_0_4_line_15 | NAYY 4x150 SE | 12 | 14 | 0.029097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2055-4_0_4_line_16 | NAYY 4x150 SE | 12 | 15 | 0.0075704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2055-4_0_4_line_17 | NAYY 4x150 SE | 13 | 19 | 0.0035772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2055-4_0_4_line_18 | NAYY 4x150 SE | 14 | 20 | 0.0041699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2055-4_0_4_line_19 | NAYY 4x150 SE | 15 | 21 | 0.00017674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2055-4_0_4_line_20 | NAYY 4x150 SE | 16 | 17 | 0.023619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2055-4_0_4_line_21 | NAYY 4x150 SE | 16 | 18 | 0.040394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2055-4_0_4_line_22 | NAYY 4x150 SE | 17 | 76 | 0.012364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2055-4_0_4_line_23 | NAYY 4x150 SE | 17 | 77 | 0.033375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2055-4_0_4_line_24 | NAYY 4x150 SE | 18 | 169 | 0.00609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2055-4_0_4_line_25 | NAYY 4x150 SE | 18 | 170 | 0.0025587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2055-4_0_4_line_26 | NAYY 4x150 SE | 19 | 39 | 0.013545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2055-4_0_4_line_27 | NAYY 4x150 SE | 20 | 171 | 0.0001369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2055-4_0_4_line_28 | NAYY 4x150 SE | 21 | 248 | 0.0024226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2055-4_0_4_line_29 | NAYY 4x150 SE | 22 | 23 | 0.0091843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2055-4_0_4_line_30 | NAYY 4x150 SE | 22 | 24 | 0.012295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2055-4_0_4_line_31 | NAYY 4x150 SE | 23 | 25 | 0.01968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2055-4_0_4_line_32 | NAYY 4x150 SE | 24 | 26 | 0.00062698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2055-4_0_4_line_33 | NAYY 4x150 SE | 25 | 178 | 0.011799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2055-4_0_4_line_34 | NAYY 4x150 SE | 26 | 140 | 0.002022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2055-4_0_4_line_35 | NAYY 4x150 SE | 27 | 28 | 1.4717e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2055-4_0_4_line_36 | NAYY 4x150 SE | 28 | 32 | 0.0069672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2055-4_0_4_line_37 | NAYY 4x150 SE | 29 | 30 | 0.012606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2055-4_0_4_line_38 | NAYY 4x150 SE | 29 | 31 | 0.008124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2055-4_0_4_line_39 | NAYY 4x150 SE | 31 | 232 | 0.0082486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2055-4_0_4_line_40 | NAYY 4x150 SE | 32 | 239 | 0.0064835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2055-4_0_4_line_41 | NAYY 4x150 SE | 33 | 34 | 0.0045281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2055-4_0_4_line_42 | NAYY 4x150 SE | 33 | 35 | 0.052242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2055-4_0_4_line_43 | NAYY 4x150 SE | 34 | 36 | 0.0067382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2055-4_0_4_line_44 | NAYY 4x150 SE | 35 | 37 | 0.037581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2055-4_0_4_line_45 | NAYY 4x150 SE | 35 | 38 | 0.041904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2055-4_0_4_line_46 | NAYY 4x150 SE | 36 | 204 | 0.010165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2055-4_0_4_line_47 | NAYY 4x150 SE | 37 | 147 | 0.0082504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2055-4_0_4_line_48 | NAYY 4x150 SE | 38 | 150 | 0.077182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2055-4_0_4_line_49 | NAYY 4x150 SE | 39 | 40 | 0.0026308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2055-4_0_4_line_50 | NAYY 4x150 SE | 40 | 41 | 0.0027194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2055-4_0_4_line_51 | NAYY 4x150 SE | 41 | 61 | 0.010199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2055-4_0_4_line_52 | NAYY 4x150 SE | 42 | 43 | 0.12941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2055-4_0_4_line_53 | NAYY 4x150 SE | 42 | 44 | 0.062031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2055-4_0_4_line_54 | NAYY 4x150 SE | 43 | 45 | 0.005733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2055-4_0_4_line_55 | NAYY 4x150 SE | 43 | 46 | 0.0063951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2055-4_0_4_line_56 | NAYY 4x150 SE | 44 | 47 | 0.070395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2055-4_0_4_line_57 | NAYY 4x150 SE | 45 | 239 | 0.0069055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2055-4_0_4_line_58 | NAYY 4x150 SE | 47 | 228 | 0.0054979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2055-4_0_4_line_59 | NAYY 4x150 SE | 48 | 49 | 0.0035928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2055-4_0_4_line_60 | NAYY 4x150 SE | 48 | 50 | 0.0026143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2055-4_0_4_line_61 | NAYY 4x150 SE | 49 | 51 | 0.0036462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2055-4_0_4_line_62 | NAYY 4x150 SE | 50 | 52 | 0.0003855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2055-4_0_4_line_63 | NAYY 4x150 SE | 52 | 215 | 0.00042048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2055-4_0_4_line_64 | NAYY 4x150 SE | 53 | 54 | 0.038504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2055-4_0_4_line_65 | NAYY 4x150 SE | 53 | 55 | 0.0029658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2055-4_0_4_line_66 | NAYY 4x150 SE | 54 | 56 | 0.021379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2055-4_0_4_line_67 | NAYY 4x150 SE | 55 | 57 | 0.020569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2055-4_0_4_line_68 | NAYY 4x150 SE | 57 | 119 | 0.018285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2055-4_0_4_line_69 | NAYY 4x150 SE | 58 | 59 | 5.0607e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_2055-4_0_4_line_70 | NAYY 4x150 SE | 58 | 60 | 0.00048228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
71 | LV_2055-4_0_4_line_71 | NAYY 4x150 SE | 59 | 61 | 0.0014119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_2055-4_0_4_line_72 | NAYY 4x150 SE | 60 | 62 | 0.0011388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_2055-4_0_4_line_73 | NAYY 4x150 SE | 61 | 88 | 0.011455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_2055-4_0_4_line_74 | NAYY 4x150 SE | 62 | 163 | 0.0028792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_2055-4_0_4_line_75 | NAYY 4x150 SE | 63 | 64 | 0.020551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2055-4_0_4_line_76 | NAYY 4x150 SE | 63 | 65 | 0.019044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_2055-4_0_4_line_77 | NAYY 4x150 SE | 63 | 66 | 0.019752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_2055-4_0_4_line_78 | NAYY 4x150 SE | 64 | 67 | 0.020922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2055-4_0_4_line_79 | NAYY 4x150 SE | 65 | 68 | 0.016648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2055-4_0_4_line_80 | NAYY 4x150 SE | 65 | 69 | 0.032526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
81 | LV_2055-4_0_4_line_81 | NAYY 4x150 SE | 66 | 70 | 0.0068531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
82 | LV_2055-4_0_4_line_82 | NAYY 4x150 SE | 67 | 181 | 0.006321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2055-4_0_4_line_83 | NAYY 4x150 SE | 67 | 182 | 0.0050534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2055-4_0_4_line_84 | NAYY 4x150 SE | 69 | 219 | 0.005296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_2055-4_0_4_line_85 | NAYY 4x150 SE | 69 | 207 | 0.027043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2055-4_0_4_line_86 | NAYY 4x150 SE | 70 | 130 | 0.010755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_2055-4_0_4_line_87 | NAYY 4x150 SE | 71 | 72 | 0.0087308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2055-4_0_4_line_88 | NAYY 4x150 SE | 71 | 73 | 0.00049869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2055-4_0_4_line_89 | NAYY 4x150 SE | 72 | 74 | 0.003342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2055-4_0_4_line_90 | NAYY 4x150 SE | 73 | 75 | 0.0018803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2055-4_0_4_line_91 | NAYY 4x150 SE | 74 | 238 | 0.01156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2055-4_0_4_line_92 | NAYY 4x150 SE | 75 | 228 | 0.0013404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2055-4_0_4_line_93 | NAYY 4x150 SE | 76 | 235 | 0.015089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2055-4_0_4_line_94 | NAYY 4x150 SE | 77 | 236 | 0.0076703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2055-4_0_4_line_95 | NAYY 4x150 SE | 78 | 79 | 0.00058427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2055-4_0_4_line_96 | NAYY 4x150 SE | 78 | 80 | 0.018292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2055-4_0_4_line_97 | NAYY 4x150 SE | 79 | 81 | 0.029391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2055-4_0_4_line_98 | NAYY 4x150 SE | 80 | 84 | 0.032958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2055-4_0_4_line_99 | NAYY 4x150 SE | 81 | 82 | 0.0043819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2055-4_0_4_line_100 | NAYY 4x150 SE | 82 | 83 | 0.047277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2055-4_0_4_line_101 | NAYY 4x150 SE | 83 | 201 | 0.0088883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2055-4_0_4_line_102 | NAYY 4x150 SE | 84 | 87 | 0.077302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2055-4_0_4_line_103 | NAYY 4x150 SE | 85 | 86 | 0.063197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_2055-4_0_4_line_104 | NAYY 4x150 SE | 85 | 87 | 0.022318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_2055-4_0_4_line_105 | NAYY 4x150 SE | 86 | 128 | 0.035022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_2055-4_0_4_line_106 | NAYY 4x150 SE | 86 | 137 | 0.016827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_2055-4_0_4_line_107 | NAYY 4x150 SE | 86 | 134 | 0.003358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2055-4_0_4_line_108 | NAYY 4x150 SE | 87 | 146 | 0.031063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
109 | LV_2055-4_0_4_line_109 | NAYY 4x150 SE | 88 | 162 | 0.0109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
110 | LV_2055-4_0_4_line_110 | NAYY 4x150 SE | 89 | 90 | 0.0019594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
111 | LV_2055-4_0_4_line_111 | NAYY 4x150 SE | 89 | 91 | 5.4821e-06 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
112 | LV_2055-4_0_4_line_112 | NAYY 4x150 SE | 90 | 92 | 0.0094575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2055-4_0_4_line_113 | NAYY 4x150 SE | 91 | 93 | 0.01434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
114 | LV_2055-4_0_4_line_114 | NAYY 4x150 SE | 92 | 210 | 0.0030615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2055-4_0_4_line_115 | NAYY 4x150 SE | 93 | 145 | 0.00012219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
116 | LV_2055-4_0_4_line_116 | NAYY 4x150 SE | 94 | 95 | 0.00018687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2055-4_0_4_line_117 | NAYY 4x150 SE | 94 | 96 | 0.00096588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2055-4_0_4_line_118 | NAYY 4x150 SE | 95 | 97 | 0.015536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2055-4_0_4_line_119 | NAYY 4x150 SE | 96 | 98 | 0.010967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2055-4_0_4_line_120 | NAYY 4x150 SE | 97 | 148 | 0.00098054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2055-4_0_4_line_121 | NAYY 4x150 SE | 98 | 99 | 0.0007723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2055-4_0_4_line_122 | NAYY 4x150 SE | 99 | 100 | 0.011433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2055-4_0_4_line_123 | NAYY 4x150 SE | 100 | 152 | 0.0044111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2055-4_0_4_line_124 | NAYY 4x150 SE | 101 | 102 | 0.00239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_2055-4_0_4_line_125 | NAYY 4x150 SE | 102 | 103 | 0.0099025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_2055-4_0_4_line_126 | NAYY 4x150 SE | 103 | 113 | 0.0018548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_2055-4_0_4_line_127 | NAYY 4x150 SE | 104 | 105 | 0.0097055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
128 | LV_2055-4_0_4_line_128 | NAYY 4x150 SE | 104 | 106 | 0.036842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
129 | LV_2055-4_0_4_line_129 | NAYY 4x150 SE | 105 | 107 | 0.0010267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
130 | LV_2055-4_0_4_line_130 | NAYY 4x150 SE | 106 | 108 | 0.054311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_2055-4_0_4_line_131 | NAYY 4x150 SE | 106 | 109 | 0.041602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
132 | LV_2055-4_0_4_line_132 | NAYY 4x150 SE | 107 | 118 | 0.016431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
133 | LV_2055-4_0_4_line_133 | NAYY 4x150 SE | 108 | 183 | 0.0045952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_2055-4_0_4_line_134 | NAYY 4x150 SE | 109 | 130 | 0.0071387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
135 | LV_2055-4_0_4_line_135 | NAYY 4x150 SE | 110 | 111 | 0.0095569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_2055-4_0_4_line_136 | NAYY 4x150 SE | 110 | 112 | 0.00061166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_2055-4_0_4_line_137 | NAYY 4x150 SE | 111 | 113 | 0.00067524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_2055-4_0_4_line_138 | NAYY 4x150 SE | 112 | 114 | 0.016071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_2055-4_0_4_line_139 | NAYY 4x150 SE | 114 | 115 | 0.009081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_2055-4_0_4_line_140 | NAYY 4x150 SE | 115 | 116 | 0.00060824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_2055-4_0_4_line_141 | NAYY 4x150 SE | 116 | 117 | 0.0029185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_2055-4_0_4_line_142 | NAYY 4x150 SE | 117 | 151 | 0.0025336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_2055-4_0_4_line_143 | NAYY 4x150 SE | 118 | 166 | 0.011856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_2055-4_0_4_line_144 | NAYY 4x150 SE | 119 | 120 | 0.0090811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_2055-4_0_4_line_145 | NAYY 4x150 SE | 119 | 121 | 0.004427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_2055-4_0_4_line_146 | NAYY 4x150 SE | 120 | 122 | 0.010084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_2055-4_0_4_line_147 | NAYY 4x150 SE | 121 | 123 | 0.014101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_2055-4_0_4_line_148 | NAYY 4x150 SE | 121 | 124 | 0.006313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_2055-4_0_4_line_149 | NAYY 4x150 SE | 122 | 172 | 0.011522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_2055-4_0_4_line_150 | NAYY 4x150 SE | 125 | 126 | 0.0044112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
151 | LV_2055-4_0_4_line_151 | NAYY 4x150 SE | 125 | 127 | 0.0020589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
152 | LV_2055-4_0_4_line_152 | NAYY 4x150 SE | 126 | 128 | 0.026675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
153 | LV_2055-4_0_4_line_153 | NAYY 4x150 SE | 127 | 129 | 0.00084625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
154 | LV_2055-4_0_4_line_154 | NAYY 4x150 SE | 128 | 216 | 0.01012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_2055-4_0_4_line_155 | NAYY 4x150 SE | 129 | 246 | 0.0059524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
156 | LV_2055-4_0_4_line_156 | NAYY 4x150 SE | 131 | 132 | 0.014289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_2055-4_0_4_line_157 | NAYY 4x150 SE | 132 | 133 | 0.0078797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_2055-4_0_4_line_158 | NAYY 4x150 SE | 133 | 232 | 0.014828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_2055-4_0_4_line_159 | NAYY 4x150 SE | 134 | 135 | 0.021768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_2055-4_0_4_line_160 | NAYY 4x150 SE | 134 | 136 | 0.074201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_2055-4_0_4_line_161 | NAYY 4x150 SE | 136 | 138 | 0.011851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_2055-4_0_4_line_162 | NAYY 4x150 SE | 136 | 139 | 0.0079254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_2055-4_0_4_line_163 | NAYY 4x150 SE | 137 | 143 | 0.019227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
164 | LV_2055-4_0_4_line_164 | NAYY 4x150 SE | 138 | 161 | 0.0012847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
165 | LV_2055-4_0_4_line_165 | NAYY 4x150 SE | 139 | 141 | 0.013343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
166 | LV_2055-4_0_4_line_166 | NAYY 4x150 SE | 140 | 185 | 0.011133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
167 | LV_2055-4_0_4_line_167 | NAYY 4x150 SE | 141 | 142 | 0.015608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
168 | LV_2055-4_0_4_line_168 | NAYY 4x150 SE | 143 | 144 | 0.034234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
169 | LV_2055-4_0_4_line_169 | NAYY 4x150 SE | 144 | 202 | 0.00067065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
170 | LV_2055-4_0_4_line_170 | NAYY 4x150 SE | 145 | 202 | 0.0011817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
171 | LV_2055-4_0_4_line_171 | NAYY 4x150 SE | 146 | 219 | 0.004164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
172 | LV_2055-4_0_4_line_172 | NAYY 4x150 SE | 147 | 148 | 0.0066218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
173 | LV_2055-4_0_4_line_173 | NAYY 4x150 SE | 149 | 150 | 0.01463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
174 | LV_2055-4_0_4_line_174 | NAYY 4x150 SE | 149 | 151 | 0.024168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
175 | LV_2055-4_0_4_line_175 | NAYY 4x150 SE | 152 | 153 | 0.00023452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
176 | LV_2055-4_0_4_line_176 | NAYY 4x150 SE | 153 | 231 | 0.017285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
177 | LV_2055-4_0_4_line_177 | NAYY 4x150 SE | 154 | 155 | 0.0035228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
178 | LV_2055-4_0_4_line_178 | NAYY 4x150 SE | 154 | 156 | 0.0019031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
179 | LV_2055-4_0_4_line_179 | NAYY 4x150 SE | 155 | 157 | 0.0054748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
180 | LV_2055-4_0_4_line_180 | NAYY 4x150 SE | 156 | 158 | 0.0017798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
181 | LV_2055-4_0_4_line_181 | NAYY 4x150 SE | 157 | 213 | 0.00031005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
182 | LV_2055-4_0_4_line_182 | NAYY 4x150 SE | 158 | 159 | 0.0017154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
183 | LV_2055-4_0_4_line_183 | NAYY 4x150 SE | 159 | 160 | 0.0087201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
184 | LV_2055-4_0_4_line_184 | NAYY 4x150 SE | 160 | 241 | 0.00023095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
185 | LV_2055-4_0_4_line_185 | NAYY 4x150 SE | 162 | 179 | 0.0089303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
186 | LV_2055-4_0_4_line_186 | NAYY 4x150 SE | 163 | 164 | 0.00078027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
187 | LV_2055-4_0_4_line_187 | NAYY 4x150 SE | 164 | 165 | 0.006738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
188 | LV_2055-4_0_4_line_188 | NAYY 4x150 SE | 165 | 221 | 0.0010403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
189 | LV_2055-4_0_4_line_189 | NAYY 4x150 SE | 166 | 167 | 0.011786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
190 | LV_2055-4_0_4_line_190 | NAYY 4x150 SE | 166 | 168 | 0.022772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
191 | LV_2055-4_0_4_line_191 | NAYY 4x150 SE | 167 | 192 | 0.014679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
192 | LV_2055-4_0_4_line_192 | NAYY 4x150 SE | 168 | 240 | 0.067536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
193 | LV_2055-4_0_4_line_193 | NAYY 4x150 SE | 170 | 243 | 0.011244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
194 | LV_2055-4_0_4_line_194 | NAYY 4x150 SE | 171 | 233 | 0.0078161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
195 | LV_2055-4_0_4_line_195 | NAYY 4x150 SE | 172 | 173 | 0.0085852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
196 | LV_2055-4_0_4_line_196 | NAYY 4x150 SE | 173 | 205 | 0.020059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
197 | LV_2055-4_0_4_line_197 | NAYY 4x150 SE | 174 | 175 | 0.013041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
198 | LV_2055-4_0_4_line_198 | NAYY 4x150 SE | 174 | 176 | 0.023517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
199 | LV_2055-4_0_4_line_199 | NAYY 4x150 SE | 175 | 177 | 0.0063545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
200 | LV_2055-4_0_4_line_200 | NAYY 4x150 SE | 176 | 178 | 0.0028201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
201 | LV_2055-4_0_4_line_201 | NAYY 4x150 SE | 177 | 231 | 0.0088196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
202 | LV_2055-4_0_4_line_202 | NAYY 4x150 SE | 179 | 180 | 0.004104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
203 | LV_2055-4_0_4_line_203 | NAYY 4x150 SE | 183 | 184 | 0.020472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
204 | LV_2055-4_0_4_line_204 | NAYY 4x150 SE | 185 | 186 | 2.7054e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
205 | LV_2055-4_0_4_line_205 | NAYY 4x150 SE | 186 | 247 | 0.0013062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
206 | LV_2055-4_0_4_line_206 | NAYY 4x150 SE | 187 | 188 | 0.013331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
207 | LV_2055-4_0_4_line_207 | NAYY 4x150 SE | 187 | 189 | 0.010872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
208 | LV_2055-4_0_4_line_208 | NAYY 4x150 SE | 188 | 190 | 0.0079994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
209 | LV_2055-4_0_4_line_209 | NAYY 4x150 SE | 189 | 191 | 0.010105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
210 | LV_2055-4_0_4_line_210 | NAYY 4x150 SE | 190 | 214 | 0.016235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
211 | LV_2055-4_0_4_line_211 | NAYY 4x150 SE | 191 | 217 | 0.0029473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
212 | LV_2055-4_0_4_line_212 | NAYY 4x150 SE | 192 | 193 | 0.029465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
213 | LV_2055-4_0_4_line_213 | NAYY 4x150 SE | 192 | 194 | 0.016974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
214 | LV_2055-4_0_4_line_214 | NAYY 4x150 SE | 193 | 195 | 0.028144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
215 | LV_2055-4_0_4_line_215 | NAYY 4x150 SE | 195 | 209 | 0.0062663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
216 | LV_2055-4_0_4_line_216 | NAYY 4x150 SE | 196 | 197 | 0.012855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
217 | LV_2055-4_0_4_line_217 | NAYY 4x150 SE | 196 | 198 | 0.011116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
218 | LV_2055-4_0_4_line_218 | NAYY 4x150 SE | 197 | 199 | 0.011117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
219 | LV_2055-4_0_4_line_219 | NAYY 4x150 SE | 198 | 200 | 0.019254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
220 | LV_2055-4_0_4_line_220 | NAYY 4x150 SE | 199 | 218 | 0.012712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
221 | LV_2055-4_0_4_line_221 | NAYY 4x150 SE | 201 | 211 | 0.0050661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
222 | LV_2055-4_0_4_line_222 | NAYY 4x150 SE | 203 | 204 | 0.0094436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
223 | LV_2055-4_0_4_line_223 | NAYY 4x150 SE | 203 | 205 | 0.0013256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
224 | LV_2055-4_0_4_line_224 | NAYY 4x150 SE | 206 | 207 | 0.014363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
225 | LV_2055-4_0_4_line_225 | NAYY 4x150 SE | 206 | 208 | 0.00040323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
226 | LV_2055-4_0_4_line_226 | NAYY 4x150 SE | 209 | 230 | 0.015815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
227 | LV_2055-4_0_4_line_227 | NAYY 4x150 SE | 210 | 215 | 0.00075646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
228 | LV_2055-4_0_4_line_228 | NAYY 4x150 SE | 211 | 212 | 0.0056611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
229 | LV_2055-4_0_4_line_229 | NAYY 4x150 SE | 213 | 214 | 0.00039224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
230 | LV_2055-4_0_4_line_230 | NAYY 4x150 SE | 214 | 246 | 0.0061137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
231 | LV_2055-4_0_4_line_231 | NAYY 4x150 SE | 217 | 218 | 0.029457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
232 | LV_2055-4_0_4_line_232 | NAYY 4x150 SE | 219 | 229 | 0.007015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
233 | LV_2055-4_0_4_line_233 | NAYY 4x150 SE | 220 | 221 | 0.010654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
234 | LV_2055-4_0_4_line_234 | NAYY 4x150 SE | 220 | 222 | 0.0009255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
235 | LV_2055-4_0_4_line_235 | NAYY 4x150 SE | 222 | 223 | 0.00069836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
236 | LV_2055-4_0_4_line_236 | NAYY 4x150 SE | 223 | 241 | 0.00035968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
237 | LV_2055-4_0_4_line_237 | NAYY 4x150 SE | 224 | 225 | 0.007767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
238 | LV_2055-4_0_4_line_238 | NAYY 4x150 SE | 225 | 226 | 0.00074591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
239 | LV_2055-4_0_4_line_239 | NAYY 4x150 SE | 225 | 227 | 0.01012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
240 | LV_2055-4_0_4_line_240 | NAYY 4x150 SE | 226 | 254 | 0.0034892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
241 | LV_2055-4_0_4_line_241 | NAYY 4x150 SE | 227 | 245 | 0.002491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
242 | LV_2055-4_0_4_line_242 | NAYY 4x150 SE | 227 | 244 | 0.006167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
243 | LV_2055-4_0_4_line_243 | NAYY 4x150 SE | 231 | 251 | 0.001498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
244 | LV_2055-4_0_4_line_244 | NAYY 4x150 SE | 233 | 234 | 0.01281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
245 | LV_2055-4_0_4_line_245 | NAYY 4x150 SE | 235 | 249 | 0.0061518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
246 | LV_2055-4_0_4_line_246 | NAYY 4x150 SE | 236 | 237 | 0.0035189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
247 | LV_2055-4_0_4_line_247 | NAYY 4x150 SE | 237 | 238 | 0.0043069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
248 | LV_2055-4_0_4_line_248 | NAYY 4x150 SE | 242 | 243 | 0.005567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
249 | LV_2055-4_0_4_line_249 | NAYY 4x150 SE | 247 | 252 | 0.015698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
250 | LV_2055-4_0_4_line_250 | NAYY 4x150 SE | 248 | 249 | 0.0065547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
251 | LV_2055-4_0_4_line_251 | NAYY 4x150 SE | 249 | 250 | 0.010938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
252 | LV_2055-4_0_4_line_252 | NAYY 4x150 SE | 252 | 253 | 0.0024633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
253 | LV_2055-4_0_4_line_253 | NAYY 4x150 SE | 253 | 254 | 0.0088636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2055-4_0_4_trafo_64 | 0.25 MVA 20/0.4 kV | 255 | 162 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31
0 | 2550380.394 | 1185496.0232 | 2550385.6598 | 1185489.587
1 | 2550387.3143 | 1185487.5611 | 2550385.6598 | 1185489.587
2 | 2550387.3143 | 1185487.5611 | 2550384.4553 | 1185485.1501 | 2550373.0817 | 1185475.5473
3 | 2550387.3143 | 1185487.5611 | 2550395.9911 | 1185477.4168 | 2550401.523 | 1185480.9617 | 2550404.4024 | 1185483.0723 | 2550406.818 | 1185486.3207 | 2550409.0465 | 1185490.9159 | 2550410.1157 | 1185494.6869 | 2550410.8803 | 1185499.4609 | 2550410.7126 | 1185504.076 | 2550410.5353 | 1185507.546 | 2550410.6181 | 1185511.0806 | 2550411.0344 | 1185513.4229
4 | 2550363.8068 | 1185467.7164 | 2550373.0817 | 1185475.5473
5 | 2550411.0344 | 1185513.4229 | 2550411.1624 | 1185514.1334 | 2550411.8652 | 1185516.9846 | 2550412.3536 | 1185518.2663
6 | 2550166.5773 | 1185644.9839 | 2550169.717 | 1185639.8771
7 | 2550166.5773 | 1185644.9839 | 2550169.1681 | 1185645.4292 | 2550171.3252 | 1185646.0338 | 2550174.9504 | 1185647.9046
8 | 2550166.5773 | 1185644.9839 | 2550163.4054 | 1185648.0676 | 2550159.6047 | 1185650.7786 | 2550154.6149 | 1185653.6662
9 | 2550169.717 | 1185639.8771 | 2550171.4455 | 1185636.6721 | 2550172.7055 | 1185632.1924 | 2550173.2623 | 1185627.5852 | 2550172.8924 | 1185624.4485
10 | 2550169.717 | 1185639.8771 | 2550175.0262 | 1185642.3453 | 2550181.0072 | 1185645.764
11 | 2550137.5003 | 1185654.3686 | 2550139.5228 | 1185654.915 | 2550146.9146 | 1185655.4647 | 2550154.6149 | 1185653.6662
12 | 2550172.8924 | 1185624.4485 | 2550172.6546 | 1185622.4319 | 2550171.9753 | 1185620.2263
13 | 2550137.5003 | 1185654.3686 | 2550132.9755 | 1185653.1464 | 2550127.6362 | 1185649.8113 | 2550125.2921 | 1185647.5547
14 | 2550378.4453 | 1185739.1954 | 2550391.8845 | 1185722.3382
15 | 2550401.7434 | 1185756.6228 | 2550391.5857 | 1185749.2141 | 2550383.3216 | 1185742.857 | 2550382.4462 | 1185742.1972 | 2550378.4453 | 1185739.1954
16 | 2550378.4453 | 1185739.1954 | 2550372.3714 | 1185734.6767 | 2550372.3714 | 1185734.6767
17 | 2550391.8845 | 1185722.3382 | 2550394.1144 | 1185719.5411
18 | 2550401.7434 | 1185756.6228 | 2550405.5553 | 1185758.3134
19 | 2550372.265 | 1185734.8178 | 2550372.3714 | 1185734.6767
20 | 2550367.3783 | 1185781.2549 | 2550360.0412 | 1185779.9151 | 2550347.8952 | 1185769.2546
21 | 2550367.3783 | 1185781.2549 | 2550376.9522 | 1185788.2015 | 2550382.9634 | 1185780.5807 | 2550397.7054 | 1185792.3426
22 | 2550347.8952 | 1185769.2546 | 2550348.1772 | 1185766.4618 | 2550353.972 | 1185758.8622
23 | 2550347.8952 | 1185769.2546 | 2550316.7663 | 1185757.2177
24 | 2550397.7054 | 1185792.3426 | 2550401.4199 | 1185787.5092
25 | 2550397.7054 | 1185792.3426 | 2550399.7062 | 1185793.9376
26 | 2550394.1144 | 1185719.5411 | 2550402.558 | 1185708.95
27 | 2550405.6804 | 1185758.3689 | 2550405.5553 | 1185758.3134
28 | 2550372.265 | 1185734.8178 | 2550370.806 | 1185736.7518
29 | 2550151.0707 | 1185543.524 | 2550158.1449 | 1185549.3812
30 | 2550158.1449 | 1185549.3812 | 2550167.6152 | 1185557.2223
31 | 2550151.0707 | 1185543.524 | 2550164.1739 | 1185528.8397
32 | 2550168.0981 | 1185557.6221 | 2550167.6152 | 1185557.2223
33 | 2550172.0295 | 1185520.0363 | 2550164.1739 | 1185528.8397
34 | 2550169.6556 | 1185558.9117 | 2550168.0981 | 1185557.6221
35 | 2550117.8872 | 1185617.896 | 2550117.8916 | 1185617.882
36 | 2550116.498 | 1185624.6571 | 2550116.5458 | 1185622.1664 | 2550117.8872 | 1185617.896
37 | 2550129.6478 | 1185602.8131 | 2550123.5748 | 1185591.766
38 | 2550129.6478 | 1185602.8131 | 2550132.6884 | 1185601.3758 | 2550136.6154 | 1185600.0757 | 2550137.2273 | 1185599.9528
39 | 2550145.3805 | 1185599.3319 | 2550141.5828 | 1185599.0781 | 2550137.2273 | 1185599.9528
40 | 2550116.498 | 1185624.6571 | 2550116.3766 | 1185631.1394
41 | 2550175.6623 | 1185434.0253 | 2550178.6678 | 1185430.6385
42 | 2550214.4148 | 1185392.6574 | 2550202.8622 | 1185402.9593 | 2550189.279 | 1185418.6811 | 2550178.6678 | 1185430.6385
43 | 2550175.6623 | 1185434.0253 | 2550171.1505 | 1185439.03
44 | 2550214.4148 | 1185392.6574 | 2550217.5435 | 1185389.8743 | 2550222.28 | 1185393.2033 | 2550227.2996 | 1185397.5306 | 2550230.1867 | 1185400.5527 | 2550232.139 | 1185403.1267 | 2550234.3435 | 1185404.8315 | 2550237.5027 | 1185408.4517 | 2550238.2518 | 1185410.4354 | 2550238.668 | 1185412.7554 | 2550238.9169 | 1185414.2319
45 | 2550232.5425 | 1185356.2864 | 2550226.6987 | 1185363.8726 | 2550226.3144 | 1185364.465 | 2550225.7892 | 1185367.3821 | 2550223.3533 | 1185380.9543 | 2550218.6785 | 1185388.7086 | 2550217.5435 | 1185389.8743 | 2550214.4148 | 1185392.6574
46 | 2550171.1505 | 1185439.03 | 2550164.344 | 1185446.5801
47 | 2550238.9169 | 1185414.2319 | 2550239.2303 | 1185416.1304 | 2550238.9177 | 1185418.9123 | 2550237.4179 | 1185422.1043 | 2550237.4179 | 1185422.1043
48 | 2550232.5425 | 1185356.2864 | 2550234.9252 | 1185358.3122 | 2550291.2821 | 1185406.3529
49 | 2550402.558 | 1185708.95 | 2550404.198 | 1185706.8929
50 | 2550405.8931 | 1185704.7666 | 2550404.198 | 1185706.8929
51 | 2550412.2511 | 1185696.7915 | 2550405.8931 | 1185704.7666
52 | 2550121.1133 | 1185642.7396 | 2550118.0957 | 1185646.0111 | 2550103.1606 | 1185661.4998 | 2550101.242 | 1185663.8616 | 2550101.1628 | 1185664.4403 | 2550101.1051 | 1185664.841 | 2550101.3361 | 1185666.9069 | 2550099.9652 | 1185669.064 | 2550100.9143 | 1185671.235 | 2550102.2991 | 1185672.5686 | 2550107.6956 | 1185674.5247 | 2550111.5371 | 1185675.7822 | 2550115.7943 | 1185678.3926 | 2550120.6174 | 1185682.0543 | 2550124.5361 | 1185685.2567 | 2550127.1733 | 1185686.6911 | 2550129.1352 | 1185686.7636 | 2550131.7131 | 1185687.4981 | 2550135.4112 | 1185688.9569 | 2550138.5266 | 1185690.9987 | 2550141.5833 | 1185693.3301 | 2550143.7368 | 1185695.3243 | 2550145.4124 | 1185696.7667 | 2550146.2118 | 1185697.4493 | 2550154.0775 | 1185703.5871 | 2550156.2982 | 1185707.2372 | 2550158.2187 | 1185710.5897 | 2550161.9024 | 1185716.7179 | 2550163.0751 | 1185720.0767 | 2550165.0077 | 1185724.8743 | 2550165.6261 | 1185727.6485 | 2550166.522 | 1185729.8422
53 | 2550216.718 | 1185694.6935 | 2550214.1099 | 1185696.7497 | 2550206.1494 | 1185703.0417 | 2550199.7292 | 1185708.2647 | 2550193.2991 | 1185712.3094 | 2550188.6742 | 1185715.0161 | 2550181.6637 | 1185719.9105 | 2550176.2318 | 1185721.9347 | 2550169.3166 | 1185725.4498 | 2550167.1456 | 1185727.7581 | 2550166.522 | 1185729.8422
54 | 2550121.1133 | 1185642.7396 | 2550118.8173 | 1185639.2013 | 2550118.3778 | 1185637.7486
55 | 2550121.1133 | 1185642.7396 | 2550123.2972 | 1185645.6341 | 2550125.2921 | 1185647.5547
56 | 2550216.718 | 1185694.6935 | 2550278.7255 | 1185728.0179
57 | 2550118.3778 | 1185637.7486 | 2550116.3766 | 1185631.1394
58 | 2550278.7255 | 1185728.0179 | 2550282.9601 | 1185731.5244
59 | 2550413.7226 | 1185521.6421 | 2550415.3646 | 1185524.8377 | 2550415.3646 | 1185524.8377
60 | 2550416.9742 | 1185526.8977 | 2550415.3646 | 1185524.8377
61 | 2550413.7226 | 1185521.6421 | 2550413.4021 | 1185521.0186 | 2550412.3536 | 1185518.2663
62 | 2550417.2115 | 1185527.2015 | 2550416.9742 | 1185526.8977
63 | 2550417.4704 | 1185527.5328 | 2550417.4704 | 1185527.5328 | 2550417.2115 | 1185527.2015
64 | 2550066.9552 | 1185559.9128 | 2550069.4692 | 1185559.3915 | 2550071.691 | 1185558.5948 | 2550074.6488 | 1185556.3799 | 2550075.5178 | 1185555.3499 | 2550085.8855 | 1185543.0454 | 2550088.7338 | 1185539.5975 | 2550089.8441 | 1185538.2208 | 2550093.7657 | 1185533.4149
65 | 2550093.7657 | 1185533.4149 | 2550095.6408 | 1185531.117
66 | 2550066.9552 | 1185559.9128 | 2550082.0727 | 1185575.0302
67 | 2550108.3434 | 1185514.9414 | 2550099.7751 | 1185525.6977 | 2550096.2653 | 1185530.3518 | 2550095.6408 | 1185531.117
68 | 2550119.7361 | 1185500.6395 | 2550108.3434 | 1185514.9414
69 | 2550413.1414 | 1185695.6312 | 2550413.1106 | 1185695.6713
70 | 2550413.435 | 1185695.2486 | 2550413.1414 | 1185695.6312
71 | 2550412.2511 | 1185696.7915 | 2550413.1106 | 1185695.6713
72 | 2550413.435 | 1185695.2486 | 2550414.1282 | 1185694.3451
73 | 2550412.2511 | 1185696.7915 | 2550421.0807 | 1185704.0887
74 | 2550415.8808 | 1185692.0608 | 2550414.1282 | 1185694.3451
75 | 2550551.8882 | 1185716.8792 | 2550535.3938 | 1185704.6208
76 | 2550551.8882 | 1185716.8792 | 2550556.3751 | 1185711.3056 | 2550563.8535 | 1185702.0387
77 | 2550551.8882 | 1185716.8792 | 2550547.1007 | 1185723.011 | 2550539.7869 | 1185732.4903
78 | 2550518.6015 | 1185692.141 | 2550535.3938 | 1185704.6208
79 | 2550563.8535 | 1185702.0387 | 2550569.7111 | 1185708.1047 | 2550575.6043 | 1185713.8591
80 | 2550584.2866 | 1185676.6891 | 2550563.8535 | 1185702.0387
81 | 2550539.7869 | 1185732.4903 | 2550537.4061 | 1185735.5759 | 2550535.6008 | 1185737.9163
82 | 2550518.6015 | 1185692.141 | 2550522.5748 | 1185687.2165
83 | 2550518.6015 | 1185692.141 | 2550515.4238 | 1185696.0703
84 | 2550580.161 | 1185673.3547 | 2550584.2866 | 1185676.6891
85 | 2550584.2866 | 1185676.6891 | 2550586.7794 | 1185673.6001 | 2550590.7195 | 1185676.647 | 2550594.2181 | 1185678.9082 | 2550597.2007 | 1185680.5956 | 2550600.8001 | 1185682.1223 | 2550603.9903 | 1185684.0081 | 2550606.1656 | 1185685.9022
86 | 2550535.6008 | 1185737.9163 | 2550529.0317 | 1185746.4321
87 | 2550292.5495 | 1185739.4648 | 2550285.8248 | 1185733.8965
88 | 2550285.4407 | 1185733.5785 | 2550285.8248 | 1185733.8965
89 | 2550292.5495 | 1185739.4648 | 2550295.1465 | 1185741.5777
90 | 2550283.9925 | 1185732.3793 | 2550285.4407 | 1185733.5785
91 | 2550295.1465 | 1185741.5777 | 2550303.8938 | 1185749.1347
92 | 2550282.9601 | 1185731.5244 | 2550283.9925 | 1185732.3793
93 | 2550353.972 | 1185758.8622 | 2550363.1211 | 1185746.8636
94 | 2550316.7663 | 1185757.2177 | 2550310.6004 | 1185752.6554
95 | 2550617.1867 | 1185560.5088 | 2550616.7906 | 1185560.0794
96 | 2550617.1867 | 1185560.5088 | 2550622.8697 | 1185566.6653 | 2550627.4234 | 1185568.2285 | 2550632.4835 | 1185567.3529
97 | 2550596.8634 | 1185538.4751 | 2550616.7906 | 1185560.0794
98 | 2550609.6292 | 1185590.6879 | 2550630.3162 | 1185571.9845 | 2550632.4835 | 1185567.3529
99 | 2550593.8925 | 1185535.2541 | 2550596.8634 | 1185538.4751
100 | 2550561.9635 | 1185500.3878 | 2550583.435 | 1185523.9121 | 2550593.8925 | 1185535.2541
101 | 2550561.9635 | 1185500.3878 | 2550555.8629 | 1185493.9236
102 | 2550559.52 | 1185649.5495 | 2550609.6292 | 1185590.6879
103 | 2550494.9363 | 1185593.5605 | 2550518.4838 | 1185612.5204 | 2550536.5769 | 1185628.9686 | 2550542.4872 | 1185634.0113 | 2550543.053 | 1185634.4945
104 | 2550543.053 | 1185634.4945 | 2550548.7281 | 1185639.3404 | 2550559.52 | 1185649.5495
105 | 2550494.9363 | 1185593.5605 | 2550491.8537 | 1185597.3103 | 2550490.1236 | 1185599.4258 | 2550482.155 | 1185609.3973 | 2550481.8305 | 1185609.8335 | 2550474.6543 | 1185618.7201 | 2550472.9546 | 1185620.8242
106 | 2550494.9363 | 1185593.5605 | 2550488.9572 | 1185588.5183 | 2550482.0755 | 1185582.7092
107 | 2550494.9363 | 1185593.5605 | 2550496.9286 | 1185590.8536
108 | 2550582.7899 | 1185670.1201 | 2550574.3656 | 1185662.8302 | 2550565.6715 | 1185655.2201 | 2550563.4653 | 1185653.2817 | 2550559.52 | 1185649.5495
109 | 2550421.0807 | 1185704.0887 | 2550426.1285 | 1185708.2605 | 2550429.4818 | 1185711.0336
110 | 2550427.0886 | 1185536.6355 | 2550428.5873 | 1185537.8976
111 | 2550428.5915 | 1185537.9012 | 2550428.5873 | 1185537.8976
112 | 2550427.0886 | 1185536.6355 | 2550426.2785 | 1185535.9533 | 2550419.9367 | 1185530.4473
113 | 2550439.5019 | 1185547.2075 | 2550432.6188 | 1185541.2926 | 2550428.5915 | 1185537.9012
114 | 2550417.9591 | 1185528.1103 | 2550419.9367 | 1185530.4473 | 2550419.9367 | 1185530.4473
115 | 2550439.5945 | 1185547.2871 | 2550439.5019 | 1185547.2075
116 | 2550222.4306 | 1185439.9769 | 2550222.5507 | 1185439.8337
117 | 2550221.81 | 1185440.717 | 2550222.4306 | 1185439.9769
118 | 2550232.5331 | 1185427.9296 | 2550222.5507 | 1185439.8337
119 | 2550221.81 | 1185440.717 | 2550214.763 | 1185449.1207
120 | 2550232.5331 | 1185427.9296 | 2550233.1631 | 1185427.1783
121 | 2550214.2668 | 1185449.7124 | 2550214.763 | 1185449.1207
122 | 2550214.2668 | 1185449.7124 | 2550206.9208 | 1185458.4727
123 | 2550204.0864 | 1185461.8527 | 2550206.9208 | 1185458.4727
124 | 2550363.8068 | 1185467.7164 | 2550361.9807 | 1185466.1746
125 | 2550354.4144 | 1185459.7863 | 2550361.9807 | 1185466.1746
126 | 2550354.4144 | 1185459.7863 | 2550352.9971 | 1185458.5897
127 | 2550476.7588 | 1185814.1965 | 2550470.8309 | 1185821.8813
128 | 2550476.7588 | 1185814.1965 | 2550499.2615 | 1185785.025
129 | 2550470.2038 | 1185822.6942 | 2550470.8309 | 1185821.8813
130 | 2550499.2615 | 1185785.025 | 2550540.1511 | 1185820.7702
131 | 2550524.6715 | 1185752.0845 | 2550499.2615 | 1185785.025
132 | 2550460.1681 | 1185835.7041 | 2550460.1681 | 1185835.7041 | 2550470.2038 | 1185822.6942
133 | 2550537.5323 | 1185824.5461 | 2550538.1129 | 1185823.7075 | 2550540.1511 | 1185820.7702
134 | 2550529.0317 | 1185746.4321 | 2550524.6715 | 1185752.0845
135 | 2550352.4812 | 1185458.1541 | 2550345.1789 | 1185451.9887
136 | 2550344.7116 | 1185451.5941 | 2550345.1789 | 1185451.9887
137 | 2550352.4812 | 1185458.1541 | 2550352.9971 | 1185458.5897
138 | 2550344.7116 | 1185451.5941 | 2550332.4317 | 1185441.2261
139 | 2550325.4931 | 1185435.3677 | 2550332.4317 | 1185441.2261
140 | 2550325.0283 | 1185434.9753 | 2550325.4931 | 1185435.3677
141 | 2550325.0283 | 1185434.9753 | 2550322.7984 | 1185433.0926
142 | 2550320.8625 | 1185431.4581 | 2550322.7984 | 1185433.0926
143 | 2550450.76 | 1185828.4892 | 2550460.1681 | 1185835.7041
144 | 2550119.7361 | 1185500.6395 | 2550125.471 | 1185493.5984
145 | 2550119.7361 | 1185500.6395 | 2550123.1029 | 1185503.5241
146 | 2550131.8191 | 1185485.7638 | 2550128.771 | 1185489.5469 | 2550125.471 | 1185493.5984
147 | 2550114.4271 | 1185514.6582 | 2550123.1029 | 1185503.5241
148 | 2550127.8918 | 1185507.6531 | 2550123.1029 | 1185503.5241
149 | 2550131.8191 | 1185485.7638 | 2550139.0479 | 1185476.7918
150 | 2550456.0566 | 1185641.4618 | 2550453.1885 | 1185644.8132
151 | 2550451.8498 | 1185646.3775 | 2550453.1885 | 1185644.8132
152 | 2550472.9546 | 1185620.8242 | 2550461.3293 | 1185635.2285 | 2550460.8156 | 1185635.8664 | 2550460.2415 | 1185636.5716 | 2550456.0566 | 1185641.4618
153 | 2550451.8498 | 1185646.3775 | 2550451.3304 | 1185646.9845 | 2550451.2996 | 1185647.0204
154 | 2550465.0795 | 1185614.4415 | 2550472.9546 | 1185620.8242
155 | 2550447.4296 | 1185651.543 | 2550451.2996 | 1185647.0204
156 | 2550171.9753 | 1185620.2263 | 2550171.227 | 1185617.7968 | 2550169.8027 | 1185613.5508 | 2550168.7154 | 1185611.2919 | 2550167.1169 | 1185609.0374 | 2550165.6302 | 1185607.7029
157 | 2550159.7662 | 1185602.4395 | 2550165.6302 | 1185607.7029
158 | 2550159.7662 | 1185602.4395 | 2550155.3106 | 1185600.7535 | 2550150.7533 | 1185599.6909 | 2550145.3805 | 1185599.3319
159 | 2550496.9286 | 1185590.8536 | 2550501.3537 | 1185594.4078 | 2550513.8436 | 1185604.5552
160 | 2550455.9014 | 1185542.0555 | 2550448.5113 | 1185550.01 | 2550496.9286 | 1185590.8536
161 | 2550455.9014 | 1185542.0555 | 2550457.7849 | 1185540.0388 | 2550452.1287 | 1185532.9214
162 | 2550455.9014 | 1185542.0555 | 2550457.655 | 1185543.6974 | 2550461.7038 | 1185547.4541
163 | 2550482.0755 | 1185582.7092 | 2550467.383 | 1185570.3067
164 | 2550451.3294 | 1185531.9157 | 2550452.1287 | 1185532.9214
165 | 2550461.7038 | 1185547.4541 | 2550471.4849 | 1185556.5293
166 | 2550169.6556 | 1185558.9117 | 2550178.2309 | 1185566.0118
167 | 2550482.9267 | 1185567.1454 | 2550471.4849 | 1185556.5293
168 | 2550467.383 | 1185570.3067 | 2550463.0039 | 1185566.6102 | 2550445.0092 | 1185551.9401 | 2550440.9994 | 1185548.4944
169 | 2550440.9994 | 1185548.4944 | 2550440.4908 | 1185548.0573
170 | 2550439.5945 | 1185547.2871 | 2550440.4908 | 1185548.0573
171 | 2550580.161 | 1185673.3547 | 2550582.7899 | 1185670.1201
172 | 2550233.1631 | 1185427.1783 | 2550237.4179 | 1185422.1043
173 | 2550302.4158 | 1185415.8438 | 2550291.2821 | 1185406.3529
174 | 2550302.4158 | 1185415.8438 | 2550305.7929 | 1185418.7225 | 2550307.5454 | 1185420.2199 | 2550310.3814 | 1185422.6088 | 2550320.8625 | 1185431.4581
175 | 2550203.9357 | 1185462.0324 | 2550204.0864 | 1185461.8527
176 | 2550194.1264 | 1185475.5832 | 2550193.7626 | 1185474.9748 | 2550194.0355 | 1185473.8386 | 2550203.9357 | 1185462.0324
177 | 2550439.6629 | 1185661.0644 | 2550437.5185 | 1185663.8593
178 | 2550437.5185 | 1185663.8593 | 2550436.36 | 1185665.3692
179 | 2550439.6629 | 1185661.0644 | 2550440.9401 | 1185659.3997 | 2550443.0218 | 1185656.7411
180 | 2550435.2766 | 1185666.7813 | 2550436.36 | 1185665.3692
181 | 2550443.2129 | 1185656.497 | 2550443.0218 | 1185656.7411
182 | 2550434.2324 | 1185668.1423 | 2550435.2766 | 1185666.7813
183 | 2550434.2324 | 1185668.1423 | 2550428.9242 | 1185675.0606
184 | 2550428.9242 | 1185675.0606 | 2550428.7836 | 1185675.2439
185 | 2550436.3637 | 1185716.7248 | 2550429.4818 | 1185711.0336
186 | 2550416.3558 | 1185691.4417 | 2550415.8808 | 1185692.0608
187 | 2550416.3558 | 1185691.4417 | 2550420.4574 | 1185686.0959
188 | 2550421.0906 | 1185685.2705 | 2550420.4574 | 1185686.0959
189 | 2550450.76 | 1185828.4892 | 2550443.6261 | 1185837.8712
190 | 2550450.76 | 1185828.4892 | 2550439.3117 | 1185819.1011 | 2550444.1815 | 1185812.7965
191 | 2550434.7414 | 1185849.5558 | 2550443.6261 | 1185837.8712
192 | 2550485.5705 | 1185759.4298 | 2550473.8386 | 1185774.4015 | 2550444.1815 | 1185812.7965
193 | 2550408.4988 | 1185800.9467 | 2550399.7062 | 1185793.9376
194 | 2550405.6804 | 1185758.3689 | 2550411.9719 | 1185763.0066
195 | 2550144.4343 | 1185470.1066 | 2550139.0479 | 1185476.7918
196 | 2550157.1637 | 1185454.6056 | 2550152.2999 | 1185460.3457 | 2550150.7741 | 1185462.2372 | 2550150.3058 | 1185462.8192 | 2550144.4343 | 1185470.1066
197 | 2550184.4021 | 1185487.2318 | 2550176.045 | 1185497.2426
198 | 2550176.045 | 1185497.2426 | 2550168.5563 | 1185506.2132 | 2550168.0634 | 1185507.5069 | 2550168.4455 | 1185509.3936 | 2550170.1717 | 1185513.2258 | 2550171.8 | 1185517.2255 | 2550171.8 | 1185517.2255
199 | 2550184.4021 | 1185487.2318 | 2550188.4744 | 1185482.3537
200 | 2550171.8 | 1185517.2255 | 2550172.0295 | 1185520.0363 | 2550172.0295 | 1185520.0363
201 | 2550194.1264 | 1185475.5832 | 2550188.4744 | 1185482.3537
202 | 2550436.3637 | 1185716.7248 | 2550439.5294 | 1185719.3364
203 | 2550537.5323 | 1185824.5461 | 2550537.5323 | 1185824.5461 | 2550538.1129 | 1185823.7075 | 2550544.5682 | 1185814.4045 | 2550549.2061 | 1185807.7291
204 | 2550178.2518 | 1185566.0291 | 2550178.2309 | 1185566.0118
205 | 2550179.2579 | 1185566.8621 | 2550178.2518 | 1185566.0291
206 | 2550472.6089 | 1185679.8788 | 2550462.2628 | 1185671.4717
207 | 2550481.0464 | 1185686.7352 | 2550472.6089 | 1185679.8788
208 | 2550456.0547 | 1185666.4269 | 2550462.2628 | 1185671.4717
209 | 2550481.0464 | 1185686.7352 | 2550488.8888 | 1185693.1079
210 | 2550443.4548 | 1185656.1882 | 2550456.0547 | 1185666.4269
211 | 2550491.1762 | 1185694.9666 | 2550488.8888 | 1185693.1079
212 | 2550434.7414 | 1185849.5558 | 2550423.8861 | 1185863.8092 | 2550421.584 | 1185866.8745 | 2550417.1419 | 1185873.2148
213 | 2550420.0527 | 1185842.3514 | 2550426.4375 | 1185842.9766 | 2550434.7414 | 1185849.5558
214 | 2550417.1419 | 1185873.2148 | 2550434.1231 | 1185885.4029 | 2550439.8576 | 1185889.8256
215 | 2550444.8196 | 1185893.6526 | 2550439.8576 | 1185889.8256
216 | 2550471.5192 | 1185736.6744 | 2550463.6675 | 1185746.8533
217 | 2550463.6675 | 1185746.8533 | 2550456.8783 | 1185755.6548
218 | 2550478.3094 | 1185727.8715 | 2550471.5192 | 1185736.6744
219 | 2550456.8783 | 1185755.6548 | 2550445.1186 | 1185770.9001
220 | 2550486.0737 | 1185717.8059 | 2550478.3094 | 1185727.8715
221 | 2550552.3857 | 1185490.2392 | 2550555.8629 | 1185493.9236
222 | 2550158.0207 | 1185453.5943 | 2550164.344 | 1185446.5801
223 | 2550158.0207 | 1185453.5943 | 2550157.1637 | 1185454.6056
224 | 2550606.1656 | 1185685.9022 | 2550596.6418 | 1185696.6541
225 | 2550596.6418 | 1185696.6541 | 2550596.3744 | 1185696.9559
226 | 2550444.8196 | 1185893.6526 | 2550457.3426 | 1185903.3109
227 | 2550417.9591 | 1185528.1103 | 2550417.4704 | 1185527.5328
228 | 2550552.3857 | 1185490.2392 | 2550548.5473 | 1185486.0781
229 | 2550443.4548 | 1185656.1882 | 2550443.2129 | 1185656.497
230 | 2550443.4548 | 1185656.1882 | 2550447.4296 | 1185651.543
231 | 2550491.1762 | 1185694.9666 | 2550496.3533 | 1185699.1735 | 2550497.365 | 1185700.6326 | 2550497.5585 | 1185701.8761 | 2550497.1065 | 1185703.503 | 2550486.0737 | 1185717.8059
232 | 2550575.7341 | 1185678.8054 | 2550580.161 | 1185673.3547
233 | 2550427.5762 | 1185676.8176 | 2550421.0906 | 1185685.2705
234 | 2550428.1396 | 1185676.0833 | 2550427.5762 | 1185676.8176
235 | 2550428.5647 | 1185675.5292 | 2550428.1396 | 1185676.0833
236 | 2550428.7836 | 1185675.2439 | 2550428.5647 | 1185675.5292
237 | 2550203.5075 | 1185586.5884 | 2550198.4938 | 1185592.5204
238 | 2550203.5075 | 1185586.5884 | 2550202.928 | 1185586.1188
239 | 2550211.383 | 1185592.9708 | 2550203.5075 | 1185586.5884
240 | 2550202.928 | 1185586.1188 | 2550200.2171 | 1185583.9221
241 | 2550213.3192 | 1185594.5444 | 2550211.383 | 1185592.9708
242 | 2550207.5311 | 1185597.7944 | 2550211.383 | 1185592.9708
243 | 2550194.9002 | 1185476.8663 | 2550194.1264 | 1185475.5832
244 | 2550411.9719 | 1185763.0066 | 2550422.2831 | 1185770.6074
245 | 2550366.8997 | 1185742.0151 | 2550366.6044 | 1185742.2955 | 2550363.1211 | 1185746.8636
246 | 2550307.1529 | 1185751.9503 | 2550310.6004 | 1185752.6554
247 | 2550307.1529 | 1185751.9503 | 2550303.8938 | 1185749.1347
248 | 2550408.4988 | 1185800.9467 | 2550411.7887 | 1185796.4503
249 | 2550191.4169 | 1185576.7908 | 2550183.5459 | 1185570.4125 | 2550179.2579 | 1185566.8621
250 | 2550366.8997 | 1185742.0151 | 2550369.1559 | 1185738.9391 | 2550370.806 | 1185736.7518
251 | 2550366.8997 | 1185742.0151 | 2550375.4462 | 1185748.8412
252 | 2550191.4169 | 1185576.7908 | 2550193.3308 | 1185578.3416
253 | 2550200.2171 | 1185583.9221 | 2550193.3308 | 1185578.3416

## bus_geodata
| x | y | coords
0 | 2550380.394 | 1185496.0232
1 | 2550385.6598 | 1185489.587
2 | 2550387.3143 | 1185487.5611
3 | 2550373.0817 | 1185475.5473
4 | 2550411.0344 | 1185513.4229
5 | 2550166.5773 | 1185644.9839
6 | 2550169.717 | 1185639.8771
7 | 2550174.9504 | 1185647.9046
8 | 2550154.6149 | 1185653.6662
9 | 2550172.8924 | 1185624.4485
10 | 2550181.0072 | 1185645.764
11 | 2550137.5003 | 1185654.3686
12 | 2550378.4453 | 1185739.1954
13 | 2550391.8845 | 1185722.3382
14 | 2550401.7434 | 1185756.6228
15 | 2550372.3714 | 1185734.6767
16 | 2550367.3783 | 1185781.2549
17 | 2550347.8952 | 1185769.2546
18 | 2550397.7054 | 1185792.3426
19 | 2550394.1144 | 1185719.5411
20 | 2550405.5553 | 1185758.3134
21 | 2550372.265 | 1185734.8178
22 | 2550158.1449 | 1185549.3812
23 | 2550151.0707 | 1185543.524
24 | 2550167.6152 | 1185557.2223
25 | 2550164.1739 | 1185528.8397
26 | 2550168.0981 | 1185557.6221
27 | 2550117.8916 | 1185617.882
28 | 2550117.8872 | 1185617.896
29 | 2550129.6478 | 1185602.8131
30 | 2550123.5748 | 1185591.766
31 | 2550137.2273 | 1185599.9528
32 | 2550116.498 | 1185624.6571
33 | 2550178.6678 | 1185430.6385
34 | 2550175.6623 | 1185434.0253
35 | 2550214.4148 | 1185392.6574
36 | 2550171.1505 | 1185439.03
37 | 2550238.9169 | 1185414.2319
38 | 2550232.5425 | 1185356.2864
39 | 2550402.558 | 1185708.95
40 | 2550404.198 | 1185706.8929
41 | 2550405.8931 | 1185704.7666
42 | 2550166.522 | 1185729.8422
43 | 2550121.1133 | 1185642.7396
44 | 2550216.718 | 1185694.6935
45 | 2550118.3778 | 1185637.7486
46 | 2550125.2921 | 1185647.5547
47 | 2550278.7255 | 1185728.0179
48 | 2550415.3646 | 1185524.8377
49 | 2550413.7226 | 1185521.6421
50 | 2550416.9742 | 1185526.8977
51 | 2550412.3536 | 1185518.2663
52 | 2550417.2115 | 1185527.2015
53 | 2550093.7657 | 1185533.4149
54 | 2550066.9552 | 1185559.9128
55 | 2550095.6408 | 1185531.117
56 | 2550082.0727 | 1185575.0302
57 | 2550108.3434 | 1185514.9414
58 | 2550413.1414 | 1185695.6312
59 | 2550413.1106 | 1185695.6713
60 | 2550413.435 | 1185695.2486
61 | 2550412.2511 | 1185696.7915
62 | 2550414.1282 | 1185694.3451
63 | 2550551.8882 | 1185716.8792
64 | 2550535.3938 | 1185704.6208
65 | 2550563.8535 | 1185702.0387
66 | 2550539.7869 | 1185732.4903
67 | 2550518.6015 | 1185692.141
68 | 2550575.6043 | 1185713.8591
69 | 2550584.2866 | 1185676.6891
70 | 2550535.6008 | 1185737.9163
71 | 2550285.8248 | 1185733.8965
72 | 2550292.5495 | 1185739.4648
73 | 2550285.4407 | 1185733.5785
74 | 2550295.1465 | 1185741.5777
75 | 2550283.9925 | 1185732.3793
76 | 2550353.9721 | 1185758.8622
77 | 2550316.7663 | 1185757.2177
78 | 2550617.1867 | 1185560.5088
79 | 2550616.7906 | 1185560.0794
80 | 2550632.4835 | 1185567.3529
81 | 2550596.8634 | 1185538.4751
82 | 2550593.8925 | 1185535.2541
83 | 2550561.9635 | 1185500.3878
84 | 2550609.6292 | 1185590.6879
85 | 2550543.053 | 1185634.4945
86 | 2550494.9363 | 1185593.5605
87 | 2550559.52 | 1185649.5495
88 | 2550421.0807 | 1185704.0887
89 | 2550428.5873 | 1185537.8976
90 | 2550427.0886 | 1185536.6355
91 | 2550428.5915 | 1185537.9012
92 | 2550419.9367 | 1185530.4473
93 | 2550439.5019 | 1185547.2075
94 | 2550222.4306 | 1185439.9769
95 | 2550222.5507 | 1185439.8337
96 | 2550221.81 | 1185440.717
97 | 2550232.5331 | 1185427.9296
98 | 2550214.763 | 1185449.1207
99 | 2550214.2668 | 1185449.7124
100 | 2550206.9208 | 1185458.4727
101 | 2550363.8068 | 1185467.7164
102 | 2550361.9807 | 1185466.1746
103 | 2550354.4144 | 1185459.7863
104 | 2550476.7588 | 1185814.1965
105 | 2550470.8309 | 1185821.8813
106 | 2550499.2615 | 1185785.025
107 | 2550470.2038 | 1185822.6942
108 | 2550540.1511 | 1185820.7702
109 | 2550524.6715 | 1185752.0845
110 | 2550345.1789 | 1185451.9887
111 | 2550352.4812 | 1185458.1541
112 | 2550344.7116 | 1185451.5941
113 | 2550352.9971 | 1185458.5897
114 | 2550332.4317 | 1185441.2261
115 | 2550325.4931 | 1185435.3677
116 | 2550325.0283 | 1185434.9753
117 | 2550322.7984 | 1185433.0926
118 | 2550460.1681 | 1185835.7041
119 | 2550119.7362 | 1185500.6395
120 | 2550125.471 | 1185493.5984
121 | 2550123.1029 | 1185503.5241
122 | 2550131.8191 | 1185485.7638
123 | 2550114.4271 | 1185514.6582
124 | 2550127.8918 | 1185507.6531
125 | 2550453.1885 | 1185644.8132
126 | 2550456.0566 | 1185641.4618
127 | 2550451.8498 | 1185646.3775
128 | 2550472.9546 | 1185620.8242
129 | 2550451.2996 | 1185647.0204
130 | 2550529.0317 | 1185746.4321
131 | 2550171.9753 | 1185620.2263
132 | 2550165.6302 | 1185607.7029
133 | 2550159.7662 | 1185602.4395
134 | 2550496.9286 | 1185590.8536
135 | 2550513.8436 | 1185604.5553
136 | 2550455.9014 | 1185542.0555
137 | 2550482.0755 | 1185582.7092
138 | 2550452.1287 | 1185532.9214
139 | 2550461.7038 | 1185547.4541
140 | 2550169.6556 | 1185558.9117
141 | 2550471.4849 | 1185556.5293
142 | 2550482.9267 | 1185567.1454
143 | 2550467.383 | 1185570.3067
144 | 2550440.9994 | 1185548.4944
145 | 2550439.5945 | 1185547.2871
146 | 2550582.7899 | 1185670.1201
147 | 2550237.4179 | 1185422.1043
148 | 2550233.1631 | 1185427.1783
149 | 2550302.4158 | 1185415.8438
150 | 2550291.2821 | 1185406.3529
151 | 2550320.8625 | 1185431.458
152 | 2550204.0864 | 1185461.8527
153 | 2550203.9357 | 1185462.0324
154 | 2550437.5185 | 1185663.8593
155 | 2550439.6629 | 1185661.0644
156 | 2550436.36 | 1185665.3692
157 | 2550443.0218 | 1185656.7411
158 | 2550435.2766 | 1185666.7813
159 | 2550434.2324 | 1185668.1423
160 | 2550428.9242 | 1185675.0606
161 | 2550451.3294 | 1185531.9157
162 | 2550429.4818 | 1185711.0336
163 | 2550415.8808 | 1185692.0608
164 | 2550416.3558 | 1185691.4417
165 | 2550420.4574 | 1185686.0959
166 | 2550450.76 | 1185828.4892
167 | 2550443.6261 | 1185837.8712
168 | 2550444.1815 | 1185812.7965
169 | 2550401.4199 | 1185787.5092
170 | 2550399.7062 | 1185793.9376
171 | 2550405.6804 | 1185758.3689
172 | 2550139.0479 | 1185476.7918
173 | 2550144.4343 | 1185470.1066
174 | 2550176.045 | 1185497.2426
175 | 2550184.4021 | 1185487.2318
176 | 2550171.8 | 1185517.2255
177 | 2550188.4744 | 1185482.3537
178 | 2550172.0295 | 1185520.0363
179 | 2550436.3637 | 1185716.7248
180 | 2550439.5294 | 1185719.3364
181 | 2550522.5748 | 1185687.2165
182 | 2550515.4238 | 1185696.0703
183 | 2550537.5323 | 1185824.5461
184 | 2550549.2061 | 1185807.7291
185 | 2550178.2309 | 1185566.0118
186 | 2550178.2518 | 1185566.0291
187 | 2550472.6089 | 1185679.8788
188 | 2550462.2628 | 1185671.4717
189 | 2550481.0464 | 1185686.7352
190 | 2550456.0547 | 1185666.4269
191 | 2550488.8888 | 1185693.1079
192 | 2550434.7414 | 1185849.5558
193 | 2550417.1419 | 1185873.2148
194 | 2550420.0527 | 1185842.3514
195 | 2550439.8576 | 1185889.8256
196 | 2550463.6675 | 1185746.8533
197 | 2550471.5192 | 1185736.6744
198 | 2550456.8783 | 1185755.6548
199 | 2550478.3094 | 1185727.8715
200 | 2550445.1186 | 1185770.9001
201 | 2550555.8629 | 1185493.9236
202 | 2550440.4908 | 1185548.0573
203 | 2550158.0207 | 1185453.5943
204 | 2550164.344 | 1185446.5801
205 | 2550157.1637 | 1185454.6056
206 | 2550596.6418 | 1185696.6541
207 | 2550606.1656 | 1185685.9022
208 | 2550596.3744 | 1185696.9559
209 | 2550444.8196 | 1185893.6526
210 | 2550417.9591 | 1185528.1103
211 | 2550552.3857 | 1185490.2392
212 | 2550548.5473 | 1185486.0781
213 | 2550443.2129 | 1185656.497
214 | 2550443.4547 | 1185656.1882
215 | 2550417.4704 | 1185527.5328
216 | 2550465.0795 | 1185614.4415
217 | 2550491.1762 | 1185694.9666
218 | 2550486.0737 | 1185717.8059
219 | 2550580.161 | 1185673.3547
220 | 2550427.5762 | 1185676.8176
221 | 2550421.0906 | 1185685.2705
222 | 2550428.1396 | 1185676.0833
223 | 2550428.5647 | 1185675.5292
224 | 2550198.4938 | 1185592.5204
225 | 2550203.5075 | 1185586.5884
226 | 2550202.928 | 1185586.1188
227 | 2550211.383 | 1185592.9708
228 | 2550282.9601 | 1185731.5244
229 | 2550575.7341 | 1185678.8054
230 | 2550457.3426 | 1185903.3109
231 | 2550194.1264 | 1185475.5832
232 | 2550145.3805 | 1185599.3319
233 | 2550411.9719 | 1185763.0066
234 | 2550422.2831 | 1185770.6074
235 | 2550363.1211 | 1185746.8636
236 | 2550310.6004 | 1185752.6554
237 | 2550307.1529 | 1185751.9503
238 | 2550303.8938 | 1185749.1347
239 | 2550116.3766 | 1185631.1394
240 | 2550485.5705 | 1185759.4298
241 | 2550428.7836 | 1185675.2439
242 | 2550411.7887 | 1185796.4503
243 | 2550408.4988 | 1185800.9467
244 | 2550207.5311 | 1185597.7944
245 | 2550213.3192 | 1185594.5444
246 | 2550447.4296 | 1185651.543
247 | 2550179.2579 | 1185566.8621
248 | 2550370.806 | 1185736.7518
249 | 2550366.8997 | 1185742.0151
250 | 2550375.4462 | 1185748.8412
251 | 2550194.9002 | 1185476.8663
252 | 2550191.4169 | 1185576.7908
253 | 2550193.3308 | 1185578.3416
254 | 2550200.2171 | 1185583.9221
255 | 2550436.3637 | 1185716.7248

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98281 | -0.12009 | 0.0043729 | 0.0010959
1 | 0.98286 | -0.11971 | 0 | 0
2 | 0.98288 | -0.1196 | 0 | 0
3 | 0.98224 | -0.1241 | 0.00033513 | 8.3992e-05
4 | 0.98512 | -0.10373 | 0 | 0
5 | 0.98736 | -0.088643 | 0 | 0
6 | 0.98734 | -0.08878 | 0 | 0
7 | 0.98736 | -0.088653 | 0.00010662 | 2.6722e-05
8 | 0.98741 | -0.088287 | 0.00018197 | 4.5605e-05
9 | 0.9873 | -0.089036 | 0.00010576 | 2.6505e-05
10 | 0.98733 | -0.088869 | 0.0006798 | 0.00017038
11 | 0.98747 | -0.087837 | 0.00027171 | 6.8098e-05
12 | 0.99336 | -0.046211 | 0 | 0
13 | 0.99502 | -0.034544 | 0.00018952 | 4.7497e-05
14 | 0.99314 | -0.047749 | 0 | 0
15 | 0.99283 | -0.049916 | 0.00044437 | 0.00011137
16 | 0.98854 | -0.08011 | 0 | 0
17 | 0.9899 | -0.070523 | 0.00033659 | 8.4358e-05
18 | 0.98622 | -0.096564 | 0 | 0
19 | 0.9953 | -0.032605 | 0.00016763 | 4.2013e-05
20 | 0.99311 | -0.04797 | 0.0017126 | 0.00042922
21 | 0.99282 | -0.050002 | 0.00010428 | 2.6135e-05
22 | 0.97211 | -0.19657 | 0.00032437 | 8.1296e-05
23 | 0.97223 | -0.1957 | 0 | 0
24 | 0.97196 | -0.19769 | 0.00025241 | 6.3261e-05
25 | 0.97249 | -0.19384 | 0.00034527 | 8.6534e-05
26 | 0.97195 | -0.19775 | 0.00028287 | 7.0894e-05
27 | 0.98753 | -0.087449 | 0.00041736 | 0.0001046
28 | 0.98753 | -0.087449 | 0.00026835 | 6.7254e-05
29 | 0.98723 | -0.089588 | 0 | 0
30 | 0.98722 | -0.089639 | 0.00039405 | 9.8758e-05
31 | 0.98723 | -0.089555 | 0.00029089 | 7.2905e-05
32 | 0.98753 | -0.0874 | 0 | 0
33 | 0.97522 | -0.17424 | 0.00019337 | 4.8464e-05
34 | 0.97518 | -0.17449 | 0 | 0
35 | 0.97563 | -0.17126 | 0 | 0
36 | 0.97513 | -0.17487 | 0.00015719 | 3.9397e-05
37 | 0.97487 | -0.17672 | 0 | 0
38 | 0.97682 | -0.16278 | 0 | 0
39 | 0.99635 | -0.02525 | 0.00028616 | 7.1718e-05
40 | 0.99656 | -0.023816 | 9.4064e-05 | 2.3575e-05
41 | 0.99677 | -0.022331 | 0.00015207 | 3.8113e-05
42 | 0.98829 | -0.081968 | 0 | 0
43 | 0.98756 | -0.087232 | 0 | 0
44 | 0.98865 | -0.079441 | 0.00052756 | 0.00013222
45 | 0.98755 | -0.087287 | 0 | 0
46 | 0.98753 | -0.08743 | 0.00022585 | 5.6603e-05
47 | 0.9891 | -0.076193 | 0.0016113 | 0.00040382
48 | 0.98562 | -0.10019 | 0.00093893 | 0.00023532
49 | 0.98547 | -0.10124 | 0.00029889 | 7.491e-05
50 | 0.98574 | -0.099393 | 0.00036592 | 9.1709e-05
51 | 0.98532 | -0.1023 | 0.00046167 | 0.00011571
52 | 0.98575 | -0.099275 | 0.00032359 | 8.11e-05
53 | 0.97454 | -0.17916 | 0.00041101 | 0.00010301
54 | 0.97451 | -0.17936 | 0 | 0
55 | 0.97454 | -0.17913 | 0.00061831 | 0.00015496
56 | 0.9745 | -0.17947 | 0.00048557 | 0.0001217
57 | 0.97459 | -0.1788 | 0.00054401 | 0.00013634
58 | 0.99745 | -0.017583 | 0.0002918 | 7.3133e-05
59 | 0.99746 | -0.017554 | 0.00017108 | 4.2876e-05
60 | 0.99741 | -0.017856 | 0.00027392 | 6.8651e-05
61 | 0.99757 | -0.016753 | 0 | 0
62 | 0.99732 | -0.018499 | 0.00034681 | 8.6918e-05
63 | 0.98014 | -0.13903 | 0 | 0
64 | 0.97993 | -0.14048 | 0.0017437 | 0.00043701
65 | 0.98079 | -0.13439 | 0.0016701 | 0.00041858
66 | 0.97953 | -0.14338 | 0.0022247 | 0.00055756
67 | 0.97978 | -0.14159 | 0 | 0
68 | 0.98055 | -0.1361 | 0.0098894 | 0.0024785
69 | 0.98208 | -0.12519 | 0 | 0
70 | 0.97932 | -0.14483 | 0.0025718 | 0.00064455
71 | 0.98919 | -0.075608 | 8.3537e-05 | 2.0936e-05
72 | 0.98927 | -0.075023 | 0 | 0
73 | 0.98918 | -0.075641 | 0.00010348 | 2.5934e-05
74 | 0.9893 | -0.074799 | 0 | 0
75 | 0.98916 | -0.075763 | 0.00011475 | 2.876e-05
76 | 0.99074 | -0.064575 | 0.00013921 | 3.489e-05
77 | 0.98956 | -0.072952 | 0.00024948 | 6.2525e-05
78 | 0.98195 | -0.12626 | 0 | 0
79 | 0.98194 | -0.12631 | 0.0026293 | 0.00065896
80 | 0.98218 | -0.1246 | 0 | 0
81 | 0.98168 | -0.12819 | 0.0020943 | 0.00052488
82 | 0.98165 | -0.12837 | 0 | 0
83 | 0.98137 | -0.13036 | 0 | 0
84 | 0.9826 | -0.1216 | 0.0016918 | 0.000424
85 | 0.98483 | -0.10575 | 0.0020394 | 0.00051112
86 | 0.98789 | -0.084245 | 0 | 0
87 | 0.98377 | -0.11322 | 0.0010563 | 0.00026474
88 | 0.99881 | -0.0081798 | 0.0011382 | 0.00028526
89 | 0.98643 | -0.094474 | 0.00035162 | 8.8123e-05
90 | 0.98639 | -0.094803 | 0.00047257 | 0.00011844
91 | 0.98643 | -0.094473 | 0.00032775 | 8.2143e-05
92 | 0.98594 | -0.097938 | 0.0014637 | 0.00036684
93 | 0.98667 | -0.092833 | 0.00025961 | 6.5065e-05
94 | 0.97425 | -0.18116 | 0.00018066 | 4.5277e-05
95 | 0.97426 | -0.18114 | 0.00032292 | 8.093e-05
96 | 0.97424 | -0.18129 | 0.00017573 | 4.4043e-05
97 | 0.97455 | -0.179 | 0.00017173 | 4.304e-05
98 | 0.97404 | -0.18272 | 0.0002306 | 5.7795e-05
99 | 0.97402 | -0.18282 | 0.00017851 | 4.4739e-05
100 | 0.97382 | -0.18427 | 0.00017098 | 4.285e-05
101 | 0.98184 | -0.127 | 0.00028514 | 7.1462e-05
102 | 0.98176 | -0.12756 | 0.00044107 | 0.00011054
103 | 0.98143 | -0.12985 | 0.00026836 | 6.7257e-05
104 | 0.97686 | -0.16239 | 0.001148 | 0.00028771
105 | 0.97664 | -0.16395 | 0.0015148 | 0.00037965
106 | 0.97771 | -0.15633 | 0.0017834 | 0.00044696
107 | 0.97662 | -0.16411 | 0.0011862 | 0.0002973
108 | 0.97727 | -0.15947 | 0.00074459 | 0.00018661
109 | 0.97882 | -0.14843 | 0.0019965 | 0.00050036
110 | 0.98106 | -0.13254 | 0.00029528 | 7.4005e-05
111 | 0.98135 | -0.13043 | 0.0003982 | 9.9798e-05
112 | 0.98104 | -0.13267 | 0.0003162 | 7.9248e-05
113 | 0.98137 | -0.13028 | 0.00036945 | 9.2594e-05
114 | 0.98055 | -0.13612 | 0.00017496 | 4.385e-05
115 | 0.98028 | -0.13805 | 0.00015447 | 3.8713e-05
116 | 0.98026 | -0.13818 | 0.00016905 | 4.2369e-05
117 | 0.98018 | -0.13879 | 0.00030191 | 7.5665e-05
118 | 0.9761 | -0.16785 | 0.0038825 | 0.00097304
119 | 0.97464 | -0.1784 | 0 | 0
120 | 0.97468 | -0.17814 | 0.00063028 | 0.00015796
121 | 0.97464 | -0.17844 | 0 | 0
122 | 0.97473 | -0.17778 | 0.00036803 | 9.2238e-05
123 | 0.97463 | -0.17848 | 0.00030835 | 7.7281e-05
124 | 0.97463 | -0.17847 | 0.00041236 | 0.00010335
125 | 0.99242 | -0.052519 | 0.00072515 | 0.00018174
126 | 0.99211 | -0.054651 | 0.00053871 | 0.00013501
127 | 0.99256 | -0.051519 | 0.00029135 | 7.3019e-05
128 | 0.99027 | -0.067526 | 0 | 0
129 | 0.99262 | -0.051107 | 0.00032272 | 8.088e-05
130 | 0.97901 | -0.14702 | 0.0020959 | 0.00052528
131 | 0.98729 | -0.0891 | 0.00026176 | 6.5603e-05
132 | 0.98727 | -0.089272 | 0.00021186 | 5.3096e-05
133 | 0.98726 | -0.089351 | 0 | 0
134 | 0.98786 | -0.084435 | 0 | 0
135 | 0.98783 | -0.084616 | 0.00081051 | 0.00020313
136 | 0.98735 | -0.088015 | 0 | 0
137 | 0.9876 | -0.086271 | 0.00035154 | 8.8103e-05
138 | 0.98733 | -0.088214 | 0.00079485 | 0.00019921
139 | 0.98732 | -0.088263 | 0.0019818 | 0.00049668
140 | 0.97192 | -0.19792 | 0.00022521 | 5.6443e-05
141 | 0.9873 | -0.088412 | 0.00060479 | 0.00015157
142 | 0.98729 | -0.088488 | 0.0004775 | 0.00011967
143 | 0.98727 | -0.088563 | 0.00038618 | 9.6785e-05
144 | 0.9867 | -0.092603 | 0.00026274 | 6.585e-05
145 | 0.98667 | -0.092819 | 0.00029786 | 7.4651e-05
146 | 0.98248 | -0.12241 | 0 | 0
147 | 0.97471 | -0.17791 | 0.00019072 | 4.78e-05
148 | 0.97457 | -0.17886 | 0.00038734 | 9.7076e-05
149 | 0.97941 | -0.14426 | 0.0001676 | 4.2006e-05
150 | 0.97899 | -0.14723 | 0.00019435 | 4.8708e-05
151 | 0.9801 | -0.13932 | 0.00020133 | 5.0457e-05
152 | 0.97375 | -0.18481 | 0.00031786 | 7.9663e-05
153 | 0.97374 | -0.18484 | 0.00018911 | 4.7395e-05
154 | 0.99423 | -0.039897 | 0.00032681 | 8.1908e-05
155 | 0.99396 | -0.041833 | 0.00050512 | 0.0001266
156 | 0.99438 | -0.03885 | 0.00040336 | 0.00010109
157 | 0.99352 | -0.044834 | 0.00029535 | 7.4022e-05
158 | 0.99453 | -0.037868 | 0.00035897 | 8.9967e-05
159 | 0.99466 | -0.03692 | 0.00046664 | 0.00011695
160 | 0.99536 | -0.032092 | 0.00028755 | 7.2066e-05
161 | 0.98732 | -0.088225 | 0.000847 | 0.00021228
162 | 1 | 0 | -0.2316 | -0.058323
163 | 0.99709 | -0.020123 | 0.00041342 | 0.00010361
164 | 0.99702 | -0.020562 | 0.00084098 | 0.00021077
165 | 0.99648 | -0.024338 | 0.0006665 | 0.00016704
166 | 0.97541 | -0.17276 | 0 | 0
167 | 0.97525 | -0.17389 | 0.0015882 | 0.00039803
168 | 0.97439 | -0.18004 | 0.0036115 | 0.00090512
169 | 0.98619 | -0.096784 | 0.0035091 | 0.00087945
170 | 0.98608 | -0.097517 | 0.034308 | 0.0085983
171 | 0.99311 | -0.047975 | 0 | 0
172 | 0.97479 | -0.17732 | 0.00038663 | 9.6898e-05
173 | 0.97485 | -0.17694 | 0.0004471 | 0.00011205
174 | 0.97303 | -0.18995 | 0.00023139 | 5.7991e-05
175 | 0.97322 | -0.18857 | 0.00019969 | 5.0047e-05
176 | 0.97269 | -0.19239 | 0.00024692 | 6.1883e-05
177 | 0.97332 | -0.18788 | 0.00025027 | 6.2723e-05
178 | 0.97265 | -0.19268 | 0.00027947 | 7.0041e-05
179 | 0.99998 | -0.00017008 | 0 | 0
180 | 0.99996 | -0.00024822 | 0.0019074 | 0.00047804
181 | 0.97975 | -0.14181 | 0.0033948 | 0.00085083
182 | 0.97977 | -0.14167 | 0.0016707 | 0.00041871
183 | 0.97724 | -0.1597 | 0.0024744 | 0.00062015
184 | 0.97717 | -0.16019 | 0.0023141 | 0.00057997
185 | 0.9718 | -0.19885 | 0.00020096 | 5.0364e-05
186 | 0.9718 | -0.19885 | 0.00028906 | 7.2446e-05
187 | 0.99259 | -0.051379 | 0.00072539 | 0.0001818
188 | 0.99289 | -0.049286 | 0.00069469 | 0.00017411
189 | 0.99236 | -0.053006 | 0.00069464 | 0.00017409
190 | 0.99308 | -0.047975 | 0.00059094 | 0.0001481
191 | 0.99216 | -0.054448 | 0.0017959 | 0.0004501
192 | 0.97509 | -0.17504 | 0 | 0
193 | 0.97489 | -0.17651 | 0 | 0
194 | 0.97502 | -0.17553 | 0.0027478 | 0.00068866
195 | 0.97469 | -0.17791 | 0.0016289 | 0.00040824
196 | 0.99129 | -0.060588 | 0.0017956 | 0.00045002
197 | 0.99139 | -0.059895 | 0.0017153 | 0.00042989
198 | 0.99123 | -0.060984 | 0.001713 | 0.00042932
199 | 0.9915 | -0.059102 | 0.0017951 | 0.0004499
200 | 0.99118 | -0.061336 | 0.001796 | 0.00045011
201 | 0.98132 | -0.13074 | 0.0010219 | 0.00025612
202 | 0.98669 | -0.092681 | 0.00026528 | 6.6485e-05
203 | 0.97499 | -0.1759 | 0 | 0
204 | 0.97506 | -0.17541 | 0.00019255 | 4.8258e-05
205 | 0.97498 | -0.17597 | 0.00027667 | 6.934e-05
206 | 0.98191 | -0.1264 | 0.0012031 | 0.00030153
207 | 0.98197 | -0.12598 | 0 | 0
208 | 0.98191 | -0.12641 | 0.0016185 | 0.00040563
209 | 0.97466 | -0.17812 | 0.0015843 | 0.00039705
210 | 0.9858 | -0.098908 | 0.00029589 | 7.4158e-05
211 | 0.9813 | -0.1309 | 0.0021615 | 0.00054172
212 | 0.98129 | -0.13095 | 0.00087479 | 0.00021924
213 | 0.9935 | -0.045003 | 0.00039428 | 9.8816e-05
214 | 0.99347 | -0.045218 | 0.00026417 | 6.6207e-05
215 | 0.98577 | -0.099145 | 0.00037601 | 9.4237e-05
216 | 0.99024 | -0.067747 | 0.0021431 | 0.0005371
217 | 0.99211 | -0.054815 | 0.0017433 | 0.0004369
218 | 0.99166 | -0.057964 | 0.0017136 | 0.00042947
219 | 0.9823 | -0.12364 | 0 | 0
220 | 0.99554 | -0.030861 | 0.0003398 | 8.5161e-05
221 | 0.99639 | -0.024919 | 0.00037127 | 9.3049e-05
222 | 0.99546 | -0.031376 | 0.00027493 | 6.8904e-05
223 | 0.99541 | -0.031765 | 0.00032548 | 8.1573e-05
224 | 0.97147 | -0.20121 | 0.00020447 | 5.1245e-05
225 | 0.97147 | -0.20119 | 0 | 0
226 | 0.97148 | -0.20116 | 0.0014141 | 0.00035442
227 | 0.9714 | -0.20168 | 8.6289e-05 | 2.1626e-05
228 | 0.98915 | -0.075849 | 0.00012964 | 3.249e-05
229 | 0.98229 | -0.12373 | 0.0011777 | 0.00029515
230 | 0.97463 | -0.17837 | 0.0015271 | 0.00038273
231 | 0.97346 | -0.1869 | 0 | 0
232 | 0.98724 | -0.089497 | 0.00027852 | 6.9804e-05
233 | 0.99307 | -0.048252 | 0.0017962 | 0.00045017
234 | 0.99304 | -0.048475 | 0.001714 | 0.00042957
235 | 0.99178 | -0.057308 | 0.00012228 | 3.0646e-05
236 | 0.98948 | -0.07349 | 0.00018767 | 4.7036e-05
237 | 0.98945 | -0.073731 | 0 | 0
238 | 0.98941 | -0.074025 | 0.00013154 | 3.2967e-05
239 | 0.98754 | -0.087354 | 0.00025877 | 6.4854e-05
240 | 0.97174 | -0.19914 | 0.026827 | 0.0067236
241 | 0.99538 | -0.031964 | 0.00029406 | 7.3698e-05
242 | 0.98604 | -0.097857 | 0.0019715 | 0.00049409
243 | 0.98605 | -0.097745 | 0 | 0
244 | 0.9714 | -0.20172 | 0.00056616 | 0.00014189
245 | 0.97139 | -0.20179 | 0.0039226 | 0.00098311
246 | 0.99304 | -0.048206 | 0.00053928 | 0.00013516
247 | 0.97178 | -0.19895 | 0.00020834 | 5.2215e-05
248 | 0.99265 | -0.051175 | 0.00014502 | 3.6344e-05
249 | 0.9922 | -0.054341 | 0 | 0
250 | 0.9922 | -0.054356 | 0.00012841 | 3.2183e-05
251 | 0.97345 | -0.18692 | 0.00079271 | 0.00019867
252 | 0.97162 | -0.20014 | 0.00030887 | 7.7409e-05
253 | 0.97159 | -0.20032 | 0.00040475 | 0.00010144
254 | 0.97151 | -0.20093 | 0.00026543 | 6.6523e-05
255 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0043729 | -0.0010959 | 0.0043731 | 0.0010959 | 2.2722e-07 | -1.7882e-08 | 0.0066207 | 0.0066207 | 0.0066207 | 0.98281 | -0.12009 | 0.98286 | -0.11971 | 2.4521
1 | -0.0043731 | -0.0010959 | 0.0043732 | 0.0010959 | 7.1471e-08 | -5.6274e-09 | 0.0066207 | 0.0066207 | 0.0066207 | 0.98286 | -0.11971 | 0.98288 | -0.1196 | 2.4521
2 | 0.02352 | 0.0059109 | -0.023505 | -0.0059055 | 1.474e-05 | 5.4334e-06 | 0.035613 | 0.035613 | 0.035613 | 0.98288 | -0.1196 | 0.98224 | -0.1241 | 13.19
3 | -0.027893 | -0.0070069 | 0.027954 | 0.0070299 | 6.1668e-05 | 2.3015e-05 | 0.042234 | 0.042233 | 0.042234 | 0.98288 | -0.1196 | 0.98512 | -0.10373 | 15.6421
4 | 0.02317 | 0.0058215 | -0.02316 | -0.0058181 | 9.3347e-06 | 3.4367e-06 | 0.035105 | 0.035105 | 0.035105 | 0.98224 | -0.1241 | 0.98184 | -0.127 | 13.002
5 | -0.027954 | -0.0070299 | 0.02796 | 0.007032 | 5.5985e-06 | 2.0892e-06 | 0.042233 | 0.042233 | 0.042233 | 0.98512 | -0.10373 | 0.98532 | -0.1023 | 15.642
6 | 0.0022228 | 0.00055577 | -0.0022228 | -0.00055583 | 4.1941e-08 | -6.049e-08 | 0.0033495 | 0.0033495 | 0.0033495 | 0.98736 | -0.088643 | 0.98734 | -0.08878 | 1.2406
7 | 0.00010662 | 2.6608e-05 | -0.00010662 | -2.6722e-05 | 1.4377e-10 | -1.1409e-07 | 0.00016065 | 0.00016069 | 0.00016069 | 0.98736 | -0.088643 | 0.98736 | -0.088653 | 0.059515
8 | -0.0023294 | -0.00058238 | 0.0023296 | 0.00058224 | 1.1423e-07 | -1.461e-07 | 0.0035101 | 0.0035101 | 0.0035101 | 0.98736 | -0.088643 | 0.98741 | -0.088287 | 1.3
9 | 0.001543 | 0.00038562 | -0.0015429 | -0.0003858 | 5.429e-08 | -1.8494e-07 | 0.002325 | 0.0023251 | 0.0023251 | 0.98734 | -0.08878 | 0.9873 | -0.089036 | 0.86115
10 | 0.00067981 | 0.00017022 | -0.0006798 | -0.00017038 | 8.3286e-09 | -1.5942e-07 | 0.0010245 | 0.0010245 | 0.0010245 | 0.98734 | -0.08878 | 0.98733 | -0.088869 | 0.37946
11 | -0.0025115 | -0.00062784 | 0.0025117 | 0.00062768 | 1.5562e-07 | -1.6291e-07 | 0.0037843 | 0.0037842 | 0.0037843 | 0.98741 | -0.088287 | 0.98747 | -0.087837 | 1.4016
12 | 0.0014372 | 0.0003593 | -0.0014371 | -0.00035935 | 1.2697e-08 | -5.0596e-08 | 0.0021657 | 0.0021657 | 0.0021657 | 0.9873 | -0.089036 | 0.98729 | -0.0891 | 0.80212
13 | -0.0027834 | -0.00069578 | 0.0027836 | 0.00069565 | 1.5623e-07 | -1.2204e-07 | 0.0041936 | 0.0041936 | 0.0041936 | 0.98747 | -0.087837 | 0.98753 | -0.08743 | 1.5532
14 | -0.053847 | -0.013529 | 0.053935 | 0.013563 | 8.7553e-05 | 3.3395e-05 | 0.080674 | 0.080674 | 0.080674 | 0.99336 | -0.046211 | 0.99502 | -0.034544 | 29.8791
15 | 0.0052243 | 0.0013088 | -0.0052232 | -0.0013088 | 1.1119e-06 | 5.107e-08 | 0.0078256 | 0.0078257 | 0.0078257 | 0.99336 | -0.046211 | 0.99314 | -0.047749 | 2.8984
16 | 0.048623 | 0.012221 | -0.048598 | -0.012211 | 2.5069e-05 | 9.5441e-06 | 0.072848 | 0.072848 | 0.072848 | 0.99336 | -0.046211 | 0.99283 | -0.049916 | 26.9808
17 | -0.054124 | -0.01361 | 0.054139 | 0.013616 | 1.463e-05 | 5.5804e-06 | 0.080957 | 0.080957 | 0.080957 | 0.99502 | -0.034544 | 0.9953 | -0.032605 | 29.9841
18 | 0.0052232 | 0.0013088 | -0.005223 | -0.0013088 | 1.5935e-07 | 7.3336e-09 | 0.0078257 | 0.0078258 | 0.0078258 | 0.99314 | -0.047749 | 0.99311 | -0.04797 | 2.8984
19 | 0.048154 | 0.0121 | -0.048153 | -0.012099 | 5.746e-07 | 2.1872e-07 | 0.072182 | 0.072182 | 0.072182 | 0.99283 | -0.049916 | 0.99282 | -0.050002 | 26.7341
20 | -0.039884 | -0.010008 | 0.039937 | 0.010028 | 5.3129e-05 | 2.0131e-05 | 0.06004 | 0.06004 | 0.06004 | 0.98854 | -0.08011 | 0.9899 | -0.070523 | 22.2371
21 | 0.039884 | 0.010008 | -0.039793 | -0.0099734 | 9.0863e-05 | 3.4431e-05 | 0.06004 | 0.06004 | 0.06004 | 0.98854 | -0.08011 | 0.98622 | -0.096564 | 22.2372
22 | -0.047378 | -0.011888 | 0.047417 | 0.011903 | 3.9137e-05 | 1.4894e-05 | 0.071224 | 0.071223 | 0.071224 | 0.9899 | -0.070523 | 0.99074 | -0.064575 | 26.3791
23 | 0.0071045 | 0.0017753 | -0.0071021 | -0.0017748 | 2.3744e-06 | 4.8433e-07 | 0.010678 | 0.010678 | 0.010678 | 0.9899 | -0.070523 | 0.98956 | -0.072952 | 3.9547
24 | 0.0035092 | 0.00087942 | -0.0035091 | -0.00087945 | 1.0653e-07 | -3.6733e-08 | 0.0052946 | 0.0052947 | 0.0052947 | 0.98622 | -0.096564 | 0.98619 | -0.096784 | 1.961
25 | 0.036284 | 0.009094 | -0.036279 | -0.0090922 | 4.7852e-06 | 1.8078e-06 | 0.054746 | 0.054746 | 0.054746 | 0.98622 | -0.096564 | 0.98608 | -0.097517 | 20.2762
26 | -0.054307 | -0.013658 | 0.054362 | 0.013679 | 5.5738e-05 | 2.1262e-05 | 0.081208 | 0.081208 | 0.081208 | 0.9953 | -0.032605 | 0.99635 | -0.02525 | 30.0769
27 | 0.0035104 | 0.00087954 | -0.0035104 | -0.00087954 | 2.3636e-09 | -8.6271e-10 | 0.0052597 | 0.0052597 | 0.0052597 | 0.99311 | -0.04797 | 0.99311 | -0.047975 | 1.948
28 | 0.048049 | 0.012073 | -0.048041 | -0.01207 | 7.8422e-06 | 2.9849e-06 | 0.072026 | 0.072026 | 0.072026 | 0.99282 | -0.050002 | 0.99265 | -0.051175 | 26.6762
29 | -0.0089612 | -0.0022455 | 0.0089622 | 0.0022458 | 1.0783e-06 | 3.0084e-07 | 0.013717 | 0.013717 | 0.013717 | 0.97211 | -0.19657 | 0.97223 | -0.1957 | 5.0803
30 | 0.0086368 | 0.0021642 | -0.0086354 | -0.0021639 | 1.3409e-06 | 3.6332e-07 | 0.01322 | 0.01322 | 0.01322 | 0.97211 | -0.19657 | 0.97196 | -0.19769 | 4.8964
31 | -0.0089622 | -0.0022458 | 0.0089645 | 0.0022465 | 2.3106e-06 | 6.4456e-07 | 0.013717 | 0.013717 | 0.013717 | 0.97223 | -0.1957 | 0.97249 | -0.19384 | 5.0803
32 | 0.008383 | 0.0021006 | -0.008383 | -0.0021006 | 6.444e-08 | 1.7014e-08 | 0.012834 | 0.012834 | 0.012834 | 0.97196 | -0.19769 | 0.97195 | -0.19775 | 4.7533
33 | -0.0093098 | -0.002333 | 0.0093113 | 0.0023334 | 1.494e-06 | 4.2819e-07 | 0.014245 | 0.014245 | 0.014245 | 0.97249 | -0.19384 | 0.97265 | -0.19268 | 5.2759
34 | 0.0081001 | 0.0020297 | -0.0080999 | -0.0020296 | 1.9403e-07 | 4.9568e-08 | 0.012401 | 0.012401 | 0.012401 | 0.97195 | -0.19775 | 0.97192 | -0.19792 | 4.5929
35 | -0.00041736 | -0.0001046 | 0.00041736 | 0.0001046 | 3.336e-12 | -1.926e-10 | 0.00062889 | 0.00062889 | 0.00062889 | 0.98753 | -0.087449 | 0.98753 | -0.087449 | 0.23292
36 | -0.00068571 | -0.00017186 | 0.00068571 | 0.00017177 | 4.6412e-09 | -8.7354e-08 | 0.0010332 | 0.0010332 | 0.0010332 | 0.98753 | -0.087449 | 0.98753 | -0.0874 | 0.38268
37 | 0.00039405 | 9.8598e-05 | -0.00039405 | -9.8758e-05 | 2.7747e-09 | -1.6012e-07 | 0.00059388 | 0.00059394 | 0.00059394 | 0.98723 | -0.089588 | 0.98722 | -0.089639 | 0.21998
38 | -0.00039405 | -9.8598e-05 | 0.00039405 | 9.8494e-05 | 1.7878e-09 | -1.0319e-07 | 0.00059388 | 0.00059385 | 0.00059388 | 0.98723 | -0.089588 | 0.98723 | -0.089555 | 0.21996
39 | -0.00068495 | -0.0001714 | 0.00068495 | 0.0001713 | 5.4848e-09 | -1.0336e-07 | 0.0010323 | 0.0010323 | 0.0010323 | 0.98723 | -0.089555 | 0.98724 | -0.089497 | 0.38233
40 | -0.00068571 | -0.00017177 | 0.00068572 | 0.00017169 | 4.3187e-09 | -8.1291e-08 | 0.0010332 | 0.0010332 | 0.0010332 | 0.98753 | -0.0874 | 0.98754 | -0.087354 | 0.38267
41 | 0.0052408 | 0.0013111 | -0.0052407 | -0.0013111 | 1.8064e-07 | 1.2983e-08 | 0.0079958 | 0.0079958 | 0.0079958 | 0.97522 | -0.17424 | 0.97518 | -0.17449 | 2.9614
42 | -0.0054342 | -0.0013596 | 0.0054365 | 0.0013598 | 2.2407e-06 | 2.0971e-07 | 0.0082908 | 0.0082906 | 0.0082908 | 0.97522 | -0.17424 | 0.97563 | -0.17126 | 3.0707
43 | 0.0052407 | 0.0013111 | -0.0052404 | -0.0013111 | 2.6881e-07 | 1.9327e-08 | 0.0079958 | 0.0079958 | 0.0079958 | 0.97518 | -0.17449 | 0.97513 | -0.17487 | 2.9614
44 | 0.013864 | 0.0034772 | -0.013854 | -0.0034736 | 1.0486e-05 | 3.5642e-06 | 0.021146 | 0.021146 | 0.021146 | 0.97563 | -0.17126 | 0.97487 | -0.17672 | 7.832
45 | -0.019301 | -0.004837 | 0.019323 | 0.0048452 | 2.2658e-05 | 8.1906e-06 | 0.029437 | 0.029437 | 0.029437 | 0.97563 | -0.17126 | 0.97682 | -0.16278 | 10.9025
46 | 0.0050832 | 0.0012717 | -0.0050828 | -0.0012717 | 3.8157e-07 | 1.9957e-08 | 0.007756 | 0.007756 | 0.007756 | 0.97513 | -0.17487 | 0.97506 | -0.17541 | 2.8726
47 | 0.013854 | 0.0034736 | -0.013851 | -0.0034728 | 2.3021e-06 | 7.8258e-07 | 0.021146 | 0.021146 | 0.021146 | 0.97487 | -0.17672 | 0.97471 | -0.17791 | 7.832
48 | -0.019323 | -0.0048452 | 0.019365 | 0.0048603 | 4.1732e-05 | 1.5082e-05 | 0.029437 | 0.029436 | 0.029437 | 0.97682 | -0.16278 | 0.97899 | -0.14723 | 10.9024
49 | -0.054649 | -0.013751 | 0.05466 | 0.013755 | 1.094e-05 | 4.1734e-06 | 0.081635 | 0.081635 | 0.081635 | 0.99635 | -0.02525 | 0.99656 | -0.023816 | 30.2351
50 | -0.054754 | -0.013779 | 0.054765 | 0.013783 | 1.1347e-05 | 4.329e-06 | 0.081775 | 0.081775 | 0.081775 | 0.99656 | -0.023816 | 0.99677 | -0.022331 | 30.2872
51 | -0.054917 | -0.013821 | 0.05496 | 0.013837 | 4.2796e-05 | 1.6327e-05 | 0.082002 | 0.082002 | 0.082002 | 0.99677 | -0.022331 | 0.99757 | -0.016753 | 30.3712
52 | 0.0039569 | 0.00098804 | -0.003954 | -0.00098859 | 2.8652e-06 | -5.5503e-07 | 0.0059563 | 0.0059569 | 0.0059569 | 0.98829 | -0.081968 | 0.98756 | -0.087232 | 2.2063
53 | -0.0039569 | -0.00098804 | 0.0039582 | 0.00098777 | 1.3732e-06 | -2.67e-07 | 0.0059563 | 0.005956 | 0.0059563 | 0.98829 | -0.081968 | 0.98865 | -0.079441 | 2.206
54 | 0.0009445 | 0.00023638 | -0.0009445 | -0.00023645 | 7.2444e-09 | -7.0566e-08 | 0.001423 | 0.0014231 | 0.0014231 | 0.98756 | -0.087232 | 0.98755 | -0.087287 | 0.52706
55 | 0.0030095 | 0.00075221 | -0.0030094 | -0.00075226 | 8.203e-08 | -5.0272e-08 | 0.0045339 | 0.0045339 | 0.0045339 | 0.98756 | -0.087232 | 0.98753 | -0.08743 | 1.6792
56 | -0.0044858 | -0.00112 | 0.0044878 | 0.0011199 | 2.0013e-06 | -1.3335e-07 | 0.0067501 | 0.0067497 | 0.0067501 | 0.98865 | -0.079441 | 0.9891 | -0.076193 | 2.5
57 | 0.0009445 | 0.00023645 | -0.00094449 | -0.00023654 | 8.7264e-09 | -8.4996e-08 | 0.0014231 | 0.0014231 | 0.0014231 | 0.98755 | -0.087287 | 0.98754 | -0.087354 | 0.52707
58 | -0.0060991 | -0.0015237 | 0.0060994 | 0.0015237 | 2.8872e-07 | 4.0477e-08 | 0.0091738 | 0.0091737 | 0.0091738 | 0.9891 | -0.076193 | 0.98915 | -0.075849 | 3.3977
59 | 0.028729 | 0.0072257 | -0.028725 | -0.0072241 | 4.2193e-06 | 1.577e-06 | 0.043382 | 0.043382 | 0.043382 | 0.98562 | -0.10019 | 0.98547 | -0.10124 | 16.0674
60 | -0.029668 | -0.007461 | 0.029671 | 0.0074623 | 3.274e-06 | 1.2259e-06 | 0.044799 | 0.044799 | 0.044799 | 0.98562 | -0.10019 | 0.98574 | -0.099393 | 16.5924
61 | 0.028426 | 0.0071492 | -0.028422 | -0.0071477 | 4.1934e-06 | 1.5664e-06 | 0.042931 | 0.042931 | 0.042931 | 0.98547 | -0.10124 | 0.98532 | -0.1023 | 15.9002
62 | -0.030037 | -0.007554 | 0.030038 | 0.0075542 | 4.9476e-07 | 1.8538e-07 | 0.045352 | 0.045352 | 0.045352 | 0.98574 | -0.099393 | 0.98575 | -0.099275 | 16.797
63 | -0.030361 | -0.0076353 | 0.030362 | 0.0076355 | 5.5135e-07 | 2.067e-07 | 0.04584 | 0.04584 | 0.04584 | 0.98575 | -0.099275 | 0.98577 | -0.099145 | 16.9779
64 | 0.0004856 | 0.00012096 | -0.00048558 | -0.00012143 | 1.3202e-08 | -4.7466e-07 | 0.00074119 | 0.00074136 | 0.00074136 | 0.97454 | -0.17916 | 0.97451 | -0.17936 | 0.27458
65 | -0.00089661 | -0.00022397 | 0.00089661 | 0.00022393 | 3.4672e-09 | -3.562e-08 | 0.0013688 | 0.0013687 | 0.0013688 | 0.97454 | -0.17916 | 0.97454 | -0.17913 | 0.50695
66 | 0.00048558 | 0.00012143 | -0.00048557 | -0.0001217 | 7.3331e-09 | -2.6354e-07 | 0.00074136 | 0.00074145 | 0.00074145 | 0.97451 | -0.17936 | 0.9745 | -0.17947 | 0.27461
67 | -0.0015149 | -0.0003789 | 0.001515 | 0.00037867 | 6.8654e-08 | -2.2989e-07 | 0.0023128 | 0.0023127 | 0.0023128 | 0.97454 | -0.17913 | 0.97459 | -0.1788 | 0.85661
68 | -0.002059 | -0.00051501 | 0.0020591 | 0.00051482 | 1.1273e-07 | -1.845e-07 | 0.0031433 | 0.0031433 | 0.0031433 | 0.97459 | -0.1788 | 0.97464 | -0.1784 | 1.1642
69 | -0.17206 | -0.043466 | 0.17206 | 0.043466 | 6.9422e-07 | 2.6503e-07 | 0.25681 | 0.25681 | 0.25681 | 0.99745 | -0.017583 | 0.99746 | -0.017554 | 31.7048
70 | 0.17177 | 0.043393 | -0.17177 | -0.043391 | 6.5934e-06 | 2.517e-06 | 0.25637 | 0.25637 | 0.25637 | 0.99745 | -0.017583 | 0.99741 | -0.017856 | 31.6511
71 | -0.17224 | -0.043509 | 0.17226 | 0.043517 | 1.9407e-05 | 7.409e-06 | 0.25706 | 0.25706 | 0.25706 | 0.99746 | -0.017554 | 0.99757 | -0.016753 | 31.7363
72 | 0.17149 | 0.043322 | -0.17148 | -0.043316 | 1.5519e-05 | 5.9243e-06 | 0.25597 | 0.25597 | 0.25597 | 0.99741 | -0.017856 | 0.99732 | -0.018499 | 31.6006
73 | -0.22722 | -0.057354 | 0.22749 | 0.057459 | 0.00027392 | 0.0001049 | 0.33907 | 0.33907 | 0.33907 | 0.99757 | -0.016753 | 0.99881 | -0.0081798 | 41.8601
74 | 0.17113 | 0.043229 | -0.17109 | -0.043214 | 3.9078e-05 | 1.4917e-05 | 0.25545 | 0.25545 | 0.25545 | 0.99732 | -0.018499 | 0.99709 | -0.020123 | 31.5367
75 | 0.0068115 | 0.0017068 | -0.0068101 | -0.0017065 | 1.3713e-06 | 2.6847e-07 | 0.010341 | 0.010341 | 0.010341 | 0.98014 | -0.13903 | 0.97993 | -0.14048 | 3.83
76 | -0.070614 | -0.017735 | 0.070659 | 0.017752 | 4.5535e-05 | 1.6793e-05 | 0.10722 | 0.10722 | 0.10722 | 0.98014 | -0.13903 | 0.98079 | -0.13439 | 13.2367
77 | 0.063802 | 0.016028 | -0.063764 | -0.016014 | 3.8558e-05 | 1.4084e-05 | 0.096876 | 0.096877 | 0.096877 | 0.98014 | -0.13903 | 0.97953 | -0.14338 | 11.9601
78 | 0.0050664 | 0.0012695 | -0.0050656 | -0.0012694 | 7.7268e-07 | 3.3652e-08 | 0.0076932 | 0.0076933 | 0.0076933 | 0.97993 | -0.14048 | 0.97978 | -0.14159 | 2.8494
79 | 0.0098917 | 0.0024792 | -0.0098894 | -0.0024785 | 2.3397e-06 | 6.8983e-07 | 0.015007 | 0.015007 | 0.015007 | 0.98079 | -0.13439 | 0.98055 | -0.1361 | 5.5583
80 | -0.082221 | -0.020649 | 0.082326 | 0.020689 | 0.0001053 | 3.9267e-05 | 0.12476 | 0.12476 | 0.12476 | 0.98079 | -0.13439 | 0.98208 | -0.12519 | 15.4023
81 | 0.061539 | 0.015456 | -0.061527 | -0.015452 | 1.2461e-05 | 4.5339e-06 | 0.093497 | 0.093497 | 0.093497 | 0.97953 | -0.14338 | 0.97932 | -0.14483 | 11.5429
82 | 0.0033949 | 0.00085079 | -0.0033948 | -0.00085083 | 1.0486e-07 | -3.9275e-08 | 0.005156 | 0.005156 | 0.005156 | 0.97978 | -0.14159 | 0.97975 | -0.14181 | 1.9096
83 | 0.0016707 | 0.00041865 | -0.0016707 | -0.00041871 | 2.0301e-08 | -5.5834e-08 | 0.0025373 | 0.0025373 | 0.0025373 | 0.97978 | -0.14159 | 0.97977 | -0.14167 | 0.93975
84 | -0.085149 | -0.021395 | 0.085167 | 0.021402 | 1.8341e-05 | 6.853e-06 | 0.12903 | 0.12903 | 0.12903 | 0.98208 | -0.12519 | 0.9823 | -0.12364 | 15.9301
85 | 0.0028221 | 0.00070681 | -0.0028218 | -0.00070704 | 3.0851e-07 | -2.2349e-07 | 0.0042757 | 0.0042758 | 0.0042758 | 0.98208 | -0.12519 | 0.98197 | -0.12598 | 1.5836
86 | 0.058955 | 0.014807 | -0.058937 | -0.014801 | 1.7955e-05 | 6.5e-06 | 0.08959 | 0.08959 | 0.08959 | 0.97932 | -0.14483 | 0.97901 | -0.14702 | 11.0605
87 | -0.006531 | -0.0016319 | 0.0065315 | 0.001632 | 5.2565e-07 | 9.0086e-08 | 0.0098227 | 0.0098226 | 0.0098227 | 0.98919 | -0.075608 | 0.98927 | -0.075023 | 3.638
88 | 0.0064474 | 0.0016109 | -0.0064474 | -0.0016109 | 2.9261e-08 | 4.8525e-09 | 0.009697 | 0.009697 | 0.009697 | 0.98919 | -0.075608 | 0.98918 | -0.075641 | 3.5915
89 | -0.0065315 | -0.001632 | 0.0065317 | 0.001632 | 2.0121e-07 | 3.4478e-08 | 0.0098226 | 0.0098226 | 0.0098226 | 0.98927 | -0.075023 | 0.9893 | -0.074799 | 3.638
90 | 0.0063439 | 0.001585 | -0.0063438 | -0.001585 | 1.0681e-07 | 1.6946e-08 | 0.0095414 | 0.0095414 | 0.0095414 | 0.98918 | -0.075641 | 0.98916 | -0.075763 | 3.5338
91 | -0.0065317 | -0.001632 | 0.0065324 | 0.0016321 | 6.9595e-07 | 1.1923e-07 | 0.0098226 | 0.0098226 | 0.0098226 | 0.9893 | -0.074799 | 0.98941 | -0.074025 | 3.638
92 | 0.0062291 | 0.0015562 | -0.006229 | -0.0015562 | 7.3416e-08 | 1.1031e-08 | 0.0093687 | 0.0093688 | 0.0093688 | 0.98916 | -0.075763 | 0.98915 | -0.075849 | 3.4699
93 | -0.047556 | -0.011937 | 0.047605 | 0.011956 | 4.8043e-05 | 1.8284e-05 | 0.071433 | 0.071433 | 0.071433 | 0.99074 | -0.064575 | 0.99178 | -0.057308 | 26.4565
94 | 0.0068526 | 0.0017123 | -0.0068521 | -0.0017122 | 5.0803e-07 | 9.6865e-08 | 0.010303 | 0.010303 | 0.010303 | 0.98956 | -0.072952 | 0.98948 | -0.07349 | 3.8158
95 | 0.0087849 | 0.0022009 | -0.0087849 | -0.0022008 | 6.4609e-08 | 1.7459e-08 | 0.013312 | 0.013312 | 0.013312 | 0.98195 | -0.12626 | 0.98194 | -0.12631 | 4.9304
96 | -0.0087849 | -0.0022009 | 0.0087869 | 0.0022014 | 2.0227e-06 | 5.4653e-07 | 0.013312 | 0.013312 | 0.013312 | 0.98195 | -0.12626 | 0.98218 | -0.1246 | 4.9304
97 | 0.0061556 | 0.0015419 | -0.006154 | -0.0015416 | 1.5957e-06 | 2.4206e-07 | 0.0093278 | 0.0093279 | 0.0093279 | 0.98194 | -0.12631 | 0.98168 | -0.12819 | 3.4548
98 | -0.0087869 | -0.0022014 | 0.0087906 | 0.0022024 | 3.6444e-06 | 9.8442e-07 | 0.013312 | 0.013312 | 0.013312 | 0.98218 | -0.1246 | 0.9826 | -0.1216 | 4.9304
99 | 0.0040597 | 0.0010168 | -0.0040596 | -0.0010168 | 1.0353e-07 | -1.5578e-08 | 0.0061534 | 0.0061534 | 0.0061534 | 0.98168 | -0.12819 | 0.98165 | -0.12837 | 2.279
100 | 0.0040596 | 0.0010168 | -0.0040585 | -0.0010169 | 1.1171e-06 | -1.6787e-07 | 0.0061534 | 0.0061536 | 0.0061536 | 0.98165 | -0.12837 | 0.98137 | -0.13036 | 2.2791
101 | 0.0040585 | 0.0010169 | -0.0040583 | -0.001017 | 2.1002e-07 | -3.1519e-08 | 0.0061536 | 0.0061537 | 0.0061537 | 0.98137 | -0.13036 | 0.98132 | -0.13074 | 2.2791
102 | -0.010482 | -0.0026264 | 0.010495 | 0.0026301 | 1.2154e-05 | 3.6944e-06 | 0.015874 | 0.015874 | 0.015874 | 0.9826 | -0.1216 | 0.98377 | -0.11322 | 5.8792
103 | -0.10016 | -0.025189 | 0.10046 | 0.025302 | 0.00030119 | 0.00011342 | 0.15137 | 0.15137 | 0.15137 | 0.98483 | -0.10575 | 0.98789 | -0.084245 | 18.6876
104 | 0.098123 | 0.024677 | -0.098021 | -0.024639 | 0.00010208 | 3.841e-05 | 0.14829 | 0.14829 | 0.14829 | 0.98483 | -0.10575 | 0.98377 | -0.11322 | 18.3072
105 | -0.14153 | -0.035624 | 0.14186 | 0.03575 | 0.00033121 | 0.00012604 | 0.21323 | 0.21323 | 0.21323 | 0.98789 | -0.084245 | 0.99027 | -0.067526 | 26.3247
106 | 0.035543 | 0.0089399 | -0.035533 | -0.0089367 | 1.0036e-05 | 3.214e-06 | 0.053549 | 0.053549 | 0.053549 | 0.98789 | -0.084245 | 0.9876 | -0.086271 | 6.611
107 | 0.0055191 | 0.0013817 | -0.0055189 | -0.0013816 | 1.4479e-07 | 1.2697e-08 | 0.0083126 | 0.0083127 | 0.0083127 | 0.98789 | -0.084245 | 0.98786 | -0.084435 | 3.0788
108 | 0.08647 | 0.021744 | -0.086359 | -0.021703 | 0.00011057 | 4.1344e-05 | 0.13082 | 0.13082 | 0.13082 | 0.98377 | -0.11322 | 0.98248 | -0.12241 | 16.1503
109 | -0.22863 | -0.057744 | 0.22889 | 0.057845 | 0.00026326 | 0.00010083 | 0.34076 | 0.34076 | 0.34076 | 0.99881 | -0.0081798 | 1 | 0 | 42.0694
110 | 0.032991 | 0.008297 | -0.032989 | -0.0082964 | 1.5147e-06 | 5.3254e-07 | 0.049776 | 0.049776 | 0.049776 | 0.98643 | -0.094474 | 0.98639 | -0.094803 | 9.2178
111 | -0.033343 | -0.0083851 | 0.033343 | 0.0083851 | 2.8854e-09 | 8.8024e-10 | 0.050307 | 0.050307 | 0.050307 | 0.98643 | -0.094474 | 0.98643 | -0.094473 | 6.2107
112 | 0.032517 | 0.008178 | -0.032503 | -0.0081727 | 1.4206e-05 | 5.3433e-06 | 0.049063 | 0.049064 | 0.049064 | 0.98639 | -0.094803 | 0.98594 | -0.097938 | 18.1717
113 | -0.03367 | -0.0084672 | 0.033678 | 0.0084696 | 7.6979e-06 | 2.4114e-06 | 0.050801 | 0.050801 | 0.050801 | 0.98643 | -0.094473 | 0.98667 | -0.092833 | 6.2718
114 | 0.031039 | 0.0078058 | -0.031035 | -0.0078042 | 4.1939e-06 | 1.574e-06 | 0.046854 | 0.046854 | 0.046854 | 0.98594 | -0.097938 | 0.9858 | -0.098908 | 17.3535
115 | -0.033938 | -0.0085347 | 0.033938 | 0.0085347 | 6.6606e-08 | 2.0935e-08 | 0.051193 | 0.051193 | 0.051193 | 0.98667 | -0.092833 | 0.98667 | -0.092819 | 6.3201
116 | -0.012773 | -0.003202 | 0.012773 | 0.003202 | 4.4379e-08 | 1.4742e-08 | 0.019509 | 0.019509 | 0.019509 | 0.97425 | -0.18116 | 0.97426 | -0.18114 | 7.2254
117 | 0.012592 | 0.0031567 | -0.012592 | -0.0031566 | 2.2294e-07 | 7.3718e-08 | 0.019233 | 0.019233 | 0.019233 | 0.97425 | -0.18116 | 0.97424 | -0.18129 | 7.1232
118 | -0.013096 | -0.0032829 | 0.0131 | 0.0032842 | 3.8784e-06 | 1.2982e-06 | 0.020002 | 0.020002 | 0.020002 | 0.97426 | -0.18114 | 0.97455 | -0.179 | 7.408
119 | 0.012416 | 0.0031126 | -0.012414 | -0.0031118 | 2.4612e-06 | 8.1009e-07 | 0.018964 | 0.018964 | 0.018964 | 0.97424 | -0.18129 | 0.97404 | -0.18272 | 7.0238
120 | -0.013271 | -0.0033273 | 0.013271 | 0.0033274 | 2.5124e-07 | 8.4414e-08 | 0.020264 | 0.020264 | 0.020264 | 0.97455 | -0.179 | 0.97457 | -0.17886 | 7.5051
121 | 0.012183 | 0.003054 | -0.012183 | -0.0030539 | 1.6694e-07 | 5.4594e-08 | 0.018612 | 0.018612 | 0.018612 | 0.97404 | -0.18272 | 0.97402 | -0.18282 | 6.8933
122 | 0.012004 | 0.0030092 | -0.012002 | -0.0030084 | 2.3994e-06 | 7.8056e-07 | 0.018339 | 0.018339 | 0.018339 | 0.97402 | -0.18282 | 0.97382 | -0.18427 | 6.7923
123 | 0.011831 | 0.0029656 | -0.01183 | -0.0029653 | 8.9957e-07 | 2.9111e-07 | 0.018078 | 0.018078 | 0.018078 | 0.97382 | -0.18427 | 0.97375 | -0.18481 | 6.6956
124 | 0.022875 | 0.0057466 | -0.022873 | -0.0057459 | 1.7929e-06 | 6.5937e-07 | 0.034673 | 0.034673 | 0.034673 | 0.98184 | -0.127 | 0.98176 | -0.12756 | 12.842
125 | 0.022432 | 0.0056354 | -0.022425 | -0.0056328 | 7.1451e-06 | 2.6229e-06 | 0.034005 | 0.034005 | 0.034005 | 0.98176 | -0.12756 | 0.98143 | -0.12985 | 12.5944
126 | 0.022157 | 0.0055655 | -0.022156 | -0.005565 | 1.3065e-06 | 4.7907e-07 | 0.033598 | 0.033598 | 0.033598 | 0.98143 | -0.12985 | 0.98137 | -0.13028 | 12.4437
127 | 0.046266 | 0.011614 | -0.046256 | -0.011611 | 1.0029e-05 | 3.4927e-06 | 0.070482 | 0.070482 | 0.070482 | 0.97686 | -0.16239 | 0.97664 | -0.16395 | 8.7015
128 | -0.047414 | -0.011902 | 0.047454 | 0.011916 | 3.9981e-05 | 1.3992e-05 | 0.072231 | 0.07223 | 0.072231 | 0.97686 | -0.16239 | 0.97771 | -0.15633 | 8.9174
129 | 0.044741 | 0.011231 | -0.04474 | -0.011231 | 9.925e-07 | 3.4319e-07 | 0.068174 | 0.068174 | 0.068174 | 0.97664 | -0.16395 | 0.97662 | -0.16411 | 8.4166
130 | 0.0055358 | 0.0013868 | -0.0055334 | -0.0013865 | 2.4056e-06 | 2.4443e-07 | 0.008425 | 0.0084252 | 0.0084252 | 0.97771 | -0.15633 | 0.97727 | -0.15947 | 3.1205
131 | -0.054773 | -0.01375 | 0.054833 | 0.013771 | 6.0144e-05 | 2.1565e-05 | 0.08337 | 0.083369 | 0.08337 | 0.97771 | -0.15633 | 0.97882 | -0.14843 | 10.2926
132 | 0.043554 | 0.010933 | -0.043531 | -0.010925 | 2.258e-05 | 8.2736e-06 | 0.066367 | 0.066367 | 0.066367 | 0.97662 | -0.16411 | 0.9761 | -0.16785 | 12.2902
133 | 0.0047888 | 0.0011999 | -0.0047887 | -0.0011999 | 1.5245e-07 | 1.0596e-09 | 0.0072915 | 0.0072915 | 0.0072915 | 0.97727 | -0.15947 | 0.97724 | -0.1597 | 2.7006
134 | -0.05683 | -0.014272 | 0.056841 | 0.014276 | 1.1085e-05 | 3.9944e-06 | 0.086404 | 0.086404 | 0.086404 | 0.97882 | -0.14843 | 0.97901 | -0.14702 | 10.6672
135 | -0.021381 | -0.0053702 | 0.021387 | 0.0053725 | 6.2734e-06 | 2.2921e-06 | 0.032434 | 0.032434 | 0.032434 | 0.98106 | -0.13254 | 0.98135 | -0.13043 | 12.0126
136 | 0.021086 | 0.0052962 | -0.021086 | -0.005296 | 3.905e-07 | 1.4247e-07 | 0.031986 | 0.031986 | 0.031986 | 0.98106 | -0.13254 | 0.98104 | -0.13267 | 11.8467
137 | -0.021786 | -0.0054723 | 0.021786 | 0.0054724 | 4.599e-07 | 1.6835e-07 | 0.033038 | 0.033038 | 0.033038 | 0.98135 | -0.13043 | 0.98137 | -0.13028 | 12.2362
138 | 0.020769 | 0.0052168 | -0.020759 | -0.0052132 | 9.955e-06 | 3.626e-06 | 0.031507 | 0.031507 | 0.031507 | 0.98104 | -0.13267 | 0.98055 | -0.13612 | 11.6691
139 | 0.020584 | 0.0051693 | -0.020579 | -0.0051673 | 5.5306e-06 | 2.0126e-06 | 0.031241 | 0.031241 | 0.031241 | 0.98055 | -0.13612 | 0.98028 | -0.13805 | 11.5708
140 | 0.020424 | 0.0051286 | -0.020424 | -0.0051285 | 3.649e-07 | 1.3268e-07 | 0.031007 | 0.031007 | 0.031007 | 0.98028 | -0.13805 | 0.98026 | -0.13818 | 11.484
141 | 0.020255 | 0.0050861 | -0.020253 | -0.0050855 | 1.722e-06 | 6.2552e-07 | 0.03075 | 0.03075 | 0.03075 | 0.98026 | -0.13818 | 0.98018 | -0.13879 | 11.3889
142 | 0.019951 | 0.0050098 | -0.01995 | -0.0050093 | 1.4507e-06 | 5.2603e-07 | 0.030292 | 0.030292 | 0.030292 | 0.98018 | -0.13879 | 0.9801 | -0.13932 | 11.2192
143 | 0.039649 | 0.0099521 | -0.039622 | -0.0099418 | 2.7033e-05 | 1.0249e-05 | 0.060449 | 0.060449 | 0.060449 | 0.9761 | -0.16785 | 0.97541 | -0.17276 | 22.3884
144 | -0.0027798 | -0.00069514 | 0.0027799 | 0.00069507 | 1.0204e-07 | -7.393e-08 | 0.0042435 | 0.0042435 | 0.0042435 | 0.97464 | -0.1784 | 0.97468 | -0.17814 | 1.5717
145 | 0.00072072 | 0.00018032 | -0.00072071 | -0.00018037 | 3.344e-09 | -5.3885e-08 | 0.0011002 | 0.0011002 | 0.0011002 | 0.97464 | -0.1784 | 0.97464 | -0.17844 | 0.4075
146 | -0.0034102 | -0.00085303 | 0.0034104 | 0.00085297 | 1.7051e-07 | -6.0101e-08 | 0.0052057 | 0.0052056 | 0.0052057 | 0.97468 | -0.17814 | 0.97473 | -0.17778 | 1.928
147 | 0.00030836 | 7.7106e-05 | -0.00030835 | -7.7281e-05 | 1.9499e-09 | -1.7498e-07 | 0.00047072 | 0.00047078 | 0.00047078 | 0.97464 | -0.17844 | 0.97463 | -0.17848 | 0.17436
148 | 0.00041236 | 0.00010327 | -0.00041236 | -0.00010335 | 1.5613e-09 | -7.8073e-08 | 0.00062953 | 0.00062956 | 0.00062956 | 0.97464 | -0.17844 | 0.97463 | -0.17847 | 0.23317
149 | -0.0037784 | -0.00094521 | 0.0037787 | 0.00094516 | 2.3915e-07 | -5.1642e-08 | 0.0057675 | 0.0057674 | 0.0057675 | 0.97473 | -0.17778 | 0.97479 | -0.17732 | 2.1361
150 | 0.14484 | 0.036537 | -0.1448 | -0.036521 | 4.3308e-05 | 1.6486e-05 | 0.21726 | 0.21726 | 0.21726 | 0.99242 | -0.052519 | 0.99211 | -0.054651 | 26.8219
151 | -0.14557 | -0.036719 | 0.14559 | 0.036727 | 2.0416e-05 | 7.7726e-06 | 0.21834 | 0.21834 | 0.21834 | 0.99242 | -0.052519 | 0.99256 | -0.051519 | 26.9561
152 | 0.14426 | 0.036386 | -0.144 | -0.036287 | 0.00025995 | 9.8947e-05 | 0.21645 | 0.21645 | 0.21645 | 0.99211 | -0.054651 | 0.99027 | -0.067526 | 26.7222
153 | -0.14588 | -0.0368 | 0.14589 | 0.036803 | 8.4253e-06 | 3.2077e-06 | 0.21878 | 0.21878 | 0.21878 | 0.99256 | -0.051519 | 0.99262 | -0.051107 | 27.01
154 | 0.0021431 | 0.000537 | -0.0021431 | -0.0005371 | 6.5489e-08 | -1.05e-07 | 0.0032203 | 0.0032204 | 0.0032204 | 0.99027 | -0.067526 | 0.99024 | -0.067747 | 1.1927
155 | -0.14621 | -0.036884 | 0.14627 | 0.036906 | 5.9524e-05 | 2.2663e-05 | 0.21926 | 0.21926 | 0.21926 | 0.99262 | -0.051107 | 0.99304 | -0.048206 | 27.0697
156 | 0.0011754 | 0.00029375 | -0.0011754 | -0.00029392 | 2.7973e-08 | -1.7197e-07 | 0.0017712 | 0.0017713 | 0.0017713 | 0.98729 | -0.0891 | 0.98727 | -0.089272 | 0.65603
157 | 0.0009635 | 0.00024082 | -0.00096349 | -0.00024092 | 1.0366e-08 | -9.6773e-08 | 0.001452 | 0.001452 | 0.001452 | 0.98727 | -0.089272 | 0.98726 | -0.089351 | 0.53778
158 | 0.00096349 | 0.00024092 | -0.00096347 | -0.0002411 | 1.9509e-08 | -1.821e-07 | 0.001452 | 0.0014521 | 0.0014521 | 0.98726 | -0.089351 | 0.98724 | -0.089497 | 0.5378
159 | 0.00081053 | 0.00020286 | -0.00081051 | -0.00020313 | 2.0246e-08 | -2.709e-07 | 0.0012208 | 0.0012209 | 0.0012209 | 0.98786 | -0.084435 | 0.98783 | -0.084616 | 0.45219
160 | 0.0047084 | 0.0011788 | -0.0047061 | -0.0011788 | 2.3288e-06 | -5.3789e-08 | 0.0070918 | 0.0070922 | 0.0070922 | 0.98786 | -0.084435 | 0.98735 | -0.088015 | 2.6267
161 | 0.0016419 | 0.00041134 | -0.0016419 | -0.00041147 | 4.5277e-08 | -1.3415e-07 | 0.0024744 | 0.0024745 | 0.0024745 | 0.98735 | -0.088015 | 0.98733 | -0.088214 | 0.91646
162 | 0.0030642 | 0.0007675 | -0.0030641 | -0.00076756 | 1.0546e-07 | -6.0799e-08 | 0.0046178 | 0.0046178 | 0.0046178 | 0.98735 | -0.088015 | 0.98732 | -0.088263 | 1.7103
163 | 0.035182 | 0.0088486 | -0.03517 | -0.008845 | 1.1242e-05 | 3.5861e-06 | 0.053019 | 0.05302 | 0.05302 | 0.9876 | -0.086271 | 0.98727 | -0.088563 | 6.5456
164 | 0.000847 | 0.00021226 | -0.000847 | -0.00021228 | 1.3064e-09 | -1.5928e-08 | 0.0012765 | 0.0012765 | 0.0012765 | 0.98733 | -0.088214 | 0.98732 | -0.088225 | 0.47279
165 | 0.0010823 | 0.00027089 | -0.0010823 | -0.00027105 | 2.2151e-08 | -1.6211e-07 | 0.0016311 | 0.0016311 | 0.0016311 | 0.98732 | -0.088263 | 0.9873 | -0.088412 | 0.60412
166 | 0.0078747 | 0.0019732 | -0.0078737 | -0.0019729 | 1.0098e-06 | 2.5041e-07 | 0.012056 | 0.012056 | 0.012056 | 0.97192 | -0.19792 | 0.9718 | -0.19885 | 4.4652
167 | 0.00047751 | 0.00011948 | -0.0004775 | -0.00011967 | 5.044e-09 | -1.9766e-07 | 0.00071961 | 0.00071968 | 0.00071968 | 0.9873 | -0.088412 | 0.98729 | -0.088488 | 0.26655
168 | 0.034784 | 0.0087483 | -0.034765 | -0.008742 | 1.958e-05 | 6.2182e-06 | 0.052438 | 0.052438 | 0.052438 | 0.98727 | -0.088563 | 0.9867 | -0.092603 | 6.4738
169 | 0.034502 | 0.0086762 | -0.034501 | -0.0086761 | 3.778e-07 | 1.1961e-07 | 0.052042 | 0.052042 | 0.052042 | 0.9867 | -0.092603 | 0.98669 | -0.092681 | 6.4249
170 | -0.034236 | -0.0086094 | 0.034236 | 0.0086096 | 6.5551e-07 | 2.0684e-07 | 0.051642 | 0.051642 | 0.051642 | 0.98667 | -0.092819 | 0.98669 | -0.092681 | 6.3755
171 | 0.086359 | 0.021703 | -0.086345 | -0.021697 | 1.4822e-05 | 5.5426e-06 | 0.13082 | 0.13082 | 0.13082 | 0.98248 | -0.12241 | 0.9823 | -0.12364 | 16.1503
172 | 0.013661 | 0.003425 | -0.013659 | -0.0034244 | 1.7972e-06 | 6.087e-07 | 0.020855 | 0.020855 | 0.020855 | 0.97471 | -0.17791 | 0.97457 | -0.17886 | 7.7242
173 | 0.019567 | 0.0049119 | -0.019559 | -0.004909 | 8.0698e-06 | 2.9198e-06 | 0.029732 | 0.029732 | 0.029732 | 0.97941 | -0.14426 | 0.97899 | -0.14723 | 11.0117
174 | -0.019735 | -0.0049539 | 0.019749 | 0.0049588 | 1.356e-05 | 4.9111e-06 | 0.029986 | 0.029986 | 0.029986 | 0.97941 | -0.14426 | 0.9801 | -0.13932 | 11.106
175 | 0.011512 | 0.0028856 | -0.011512 | -0.0028856 | 4.5291e-08 | 1.4502e-08 | 0.017592 | 0.017592 | 0.017592 | 0.97375 | -0.18481 | 0.97374 | -0.18484 | 6.5157
176 | 0.011323 | 0.0028382 | -0.01132 | -0.0028372 | 3.2294e-06 | 1.0271e-06 | 0.017303 | 0.017303 | 0.017303 | 0.97374 | -0.18484 | 0.97346 | -0.1869 | 6.4087
177 | 0.16525 | 0.04169 | -0.16521 | -0.041673 | 4.4857e-05 | 1.7116e-05 | 0.24742 | 0.24742 | 0.24742 | 0.99423 | -0.039897 | 0.99396 | -0.041833 | 30.5461
178 | -0.16558 | -0.041772 | 0.16561 | 0.041781 | 2.4329e-05 | 9.2833e-06 | 0.24791 | 0.24791 | 0.24791 | 0.99423 | -0.039897 | 0.99438 | -0.03885 | 30.6065
179 | 0.1647 | 0.041546 | -0.16463 | -0.04152 | 6.9287e-05 | 2.6436e-05 | 0.24667 | 0.24667 | 0.24667 | 0.99396 | -0.041833 | 0.99352 | -0.044834 | 30.4528
180 | -0.16601 | -0.041882 | 0.16603 | 0.041891 | 2.2864e-05 | 8.7244e-06 | 0.24852 | 0.24852 | 0.24852 | 0.99438 | -0.03885 | 0.99453 | -0.037868 | 30.681
181 | 0.16434 | 0.041446 | -0.16434 | -0.041445 | 3.9098e-06 | 1.4917e-06 | 0.24623 | 0.24623 | 0.24623 | 0.99352 | -0.044834 | 0.9935 | -0.045003 | 30.3982
182 | -0.16639 | -0.041981 | 0.16641 | 0.04199 | 2.2132e-05 | 8.4456e-06 | 0.24905 | 0.24905 | 0.24905 | 0.99453 | -0.037868 | 0.99466 | -0.03692 | 30.7473
183 | -0.16688 | -0.042107 | 0.16699 | 0.04215 | 0.00011314 | 4.3174e-05 | 0.24975 | 0.24975 | 0.24975 | 0.99466 | -0.03692 | 0.99536 | -0.032092 | 30.8335
184 | -0.16728 | -0.042222 | 0.16728 | 0.042223 | 3.0067e-06 | 1.1474e-06 | 0.25018 | 0.25018 | 0.25018 | 0.99536 | -0.032092 | 0.99538 | -0.031964 | 30.8866
185 | 0.0019075 | 0.0004779 | -0.0019074 | -0.000478 | 4.4893e-08 | -9.989e-08 | 0.0028383 | 0.0028383 | 0.0028383 | 1 | 0 | 0.99998 | -0.00017008 | 1.0512
186 | 0.17068 | 0.04311 | -0.17067 | -0.043106 | 1.0539e-05 | 4.0231e-06 | 0.25483 | 0.25483 | 0.25483 | 0.99709 | -0.020123 | 0.99702 | -0.020562 | 31.4606
187 | 0.16983 | 0.042896 | -0.16974 | -0.042861 | 9.0118e-05 | 3.4397e-05 | 0.25358 | 0.25358 | 0.25358 | 0.99702 | -0.020562 | 0.99648 | -0.024338 | 31.3056
188 | 0.16907 | 0.042694 | -0.16906 | -0.042689 | 1.3805e-05 | 5.2688e-06 | 0.25258 | 0.25258 | 0.25258 | 0.99648 | -0.024338 | 0.99639 | -0.024919 | 31.1828
189 | 0.009081 | 0.002275 | -0.0090796 | -0.0022746 | 1.4114e-06 | 3.9576e-07 | 0.013853 | 0.013853 | 0.013853 | 0.97541 | -0.17276 | 0.97525 | -0.17389 | 5.1308
190 | 0.030541 | 0.0076668 | -0.03051 | -0.0076552 | 3.0851e-05 | 1.1582e-05 | 0.046596 | 0.046596 | 0.046596 | 0.97541 | -0.17276 | 0.97439 | -0.18004 | 17.2576
191 | 0.0074915 | 0.0018766 | -0.0074903 | -0.0018763 | 1.1966e-06 | 2.7712e-07 | 0.01143 | 0.01143 | 0.01143 | 0.97525 | -0.17389 | 0.97509 | -0.17504 | 4.2333
192 | 0.026899 | 0.0067501 | -0.026827 | -0.0067236 | 7.112e-05 | 2.6515e-05 | 0.04108 | 0.041081 | 0.041081 | 0.97439 | -0.18004 | 0.97174 | -0.19914 | 15.2151
193 | 0.0019715 | 0.00049391 | -0.0019715 | -0.00049403 | 6.2103e-08 | -1.1955e-07 | 0.002975 | 0.0029751 | 0.0029751 | 0.98608 | -0.097517 | 0.98605 | -0.097745 | 1.1019
194 | 0.0035104 | 0.00087954 | -0.0035103 | -0.00087959 | 1.3493e-07 | -4.9234e-08 | 0.0052597 | 0.0052597 | 0.0052597 | 0.99311 | -0.047975 | 0.99307 | -0.048252 | 1.948
195 | -0.0041653 | -0.0010421 | 0.0041655 | 0.001042 | 2.1653e-07 | -2.375e-08 | 0.0063576 | 0.0063576 | 0.0063576 | 0.97479 | -0.17732 | 0.97485 | -0.17694 | 2.3547
196 | -0.0046126 | -0.0011541 | 0.0046132 | 0.0011541 | 6.2036e-07 | -1.1525e-08 | 0.00704 | 0.00704 | 0.00704 | 0.97485 | -0.17694 | 0.97498 | -0.17597 | 2.6074
197 | -0.010073 | -0.0025244 | 0.010075 | 0.002525 | 1.9308e-06 | 5.8061e-07 | 0.015404 | 0.015404 | 0.015404 | 0.97303 | -0.18995 | 0.97322 | -0.18857 | 5.7051
198 | 0.0098414 | 0.0024664 | -0.0098381 | -0.0024655 | 3.3238e-06 | 9.8639e-07 | 0.01505 | 0.01505 | 0.01505 | 0.97303 | -0.18995 | 0.97269 | -0.19239 | 5.5741
199 | -0.010274 | -0.0025751 | 0.010275 | 0.0025754 | 9.7852e-07 | 2.9738e-07 | 0.015709 | 0.015709 | 0.015709 | 0.97322 | -0.18857 | 0.97332 | -0.18788 | 5.8182
200 | 0.0095912 | 0.0024036 | -0.0095908 | -0.0024035 | 3.7884e-07 | 1.107e-07 | 0.014672 | 0.014672 | 0.014672 | 0.97269 | -0.19239 | 0.97265 | -0.19268 | 5.4342
201 | -0.010526 | -0.0026381 | 0.010527 | 0.0026385 | 1.4251e-06 | 4.3847e-07 | 0.016092 | 0.016092 | 0.016092 | 0.97332 | -0.18788 | 0.97346 | -0.1869 | 5.9599
202 | 0.0019074 | 0.000478 | -0.0019074 | -0.00047804 | 2.0631e-08 | -4.5903e-08 | 0.0028383 | 0.0028384 | 0.0028384 | 0.99998 | -0.00017008 | 0.99996 | -0.00024822 | 1.0512
203 | 0.0023143 | 0.00057977 | -0.0023141 | -0.00057997 | 1.5862e-07 | -1.9546e-07 | 0.0035238 | 0.0035239 | 0.0035239 | 0.97724 | -0.1597 | 0.97717 | -0.16019 | 1.3051
204 | 0.0076727 | 0.0019226 | -0.0076727 | -0.0019226 | 2.329e-09 | 5.6034e-10 | 0.011748 | 0.011748 | 0.011748 | 0.9718 | -0.19885 | 0.9718 | -0.19885 | 4.3512
205 | 0.0073837 | 0.0018501 | -0.0073836 | -0.0018501 | 1.0418e-07 | 2.3887e-08 | 0.011306 | 0.011306 | 0.011306 | 0.9718 | -0.19885 | 0.97178 | -0.19895 | 4.1873
206 | -0.015502 | -0.0038856 | 0.015507 | 0.0038871 | 4.4928e-06 | 1.5556e-06 | 0.02324 | 0.02324 | 0.02324 | 0.99259 | -0.051379 | 0.99289 | -0.049286 | 8.6073
207 | 0.014777 | 0.0037038 | -0.014773 | -0.0037026 | 3.3291e-06 | 1.1399e-06 | 0.022152 | 0.022152 | 0.022152 | 0.99259 | -0.051379 | 0.99236 | -0.053006 | 8.2045
208 | -0.016201 | -0.0040612 | 0.016204 | 0.0040623 | 2.9428e-06 | 1.0284e-06 | 0.024281 | 0.024281 | 0.024281 | 0.99289 | -0.049286 | 0.99308 | -0.047975 | 8.9929
209 | 0.014079 | 0.0035285 | -0.014076 | -0.0035276 | 2.8102e-06 | 9.5031e-07 | 0.021111 | 0.021111 | 0.021111 | 0.99236 | -0.053006 | 0.99216 | -0.054448 | 7.8188
210 | -0.016795 | -0.0042104 | 0.016802 | 0.0042126 | 6.4162e-06 | 2.2576e-06 | 0.025166 | 0.025166 | 0.025166 | 0.99308 | -0.047975 | 0.99347 | -0.045218 | 9.3208
211 | 0.01228 | 0.0030775 | -0.012279 | -0.0030773 | 6.2383e-07 | 2.0187e-07 | 0.018417 | 0.018417 | 0.018417 | 0.99216 | -0.054448 | 0.99211 | -0.054815 | 6.8212
212 | 0.0047423 | 0.0011878 | -0.0047413 | -0.0011878 | 9.6288e-07 | 2.8704e-09 | 0.0072366 | 0.0072367 | 0.0072367 | 0.97509 | -0.17504 | 0.97489 | -0.17651 | 2.6803
213 | 0.002748 | 0.00068852 | -0.0027478 | -0.00068866 | 1.8626e-07 | -1.4008e-07 | 0.0041934 | 0.0041935 | 0.0041935 | 0.97509 | -0.17504 | 0.97502 | -0.17553 | 1.5531
214 | 0.0047413 | 0.0011878 | -0.0047404 | -0.0011878 | 9.1975e-07 | 2.8981e-09 | 0.0072367 | 0.0072369 | 0.0072369 | 0.97489 | -0.17651 | 0.97469 | -0.17791 | 2.6803
215 | 0.0031115 | 0.00077957 | -0.0031114 | -0.00077961 | 8.8229e-08 | -4.4165e-08 | 0.0047501 | 0.0047502 | 0.0047502 | 0.97469 | -0.17791 | 0.97466 | -0.17812 | 1.7593
216 | -0.0053049 | -0.0013292 | 0.0053054 | 0.0013292 | 5.0865e-07 | 2.9888e-08 | 0.007963 | 0.0079629 | 0.007963 | 0.99129 | -0.060588 | 0.99139 | -0.059895 | 2.9492
217 | 0.0035093 | 0.00087916 | -0.0035091 | -0.00087922 | 1.9247e-07 | -6.9267e-08 | 0.0052676 | 0.0052677 | 0.0052677 | 0.99129 | -0.060588 | 0.99123 | -0.060984 | 1.951
218 | -0.0070207 | -0.0017591 | 0.0070214 | 0.0017592 | 7.703e-07 | 1.529e-07 | 0.010537 | 0.010537 | 0.010537 | 0.99139 | -0.059895 | 0.9915 | -0.059102 | 3.9028
219 | 0.0017961 | 0.0004499 | -0.001796 | -0.00045011 | 8.7336e-08 | -2.1458e-07 | 0.0026961 | 0.0026962 | 0.0026962 | 0.99123 | -0.060984 | 0.99118 | -0.061336 | 0.9986
220 | -0.0088166 | -0.0022091 | 0.008818 | 0.0022095 | 1.3887e-06 | 3.7015e-07 | 0.013231 | 0.013231 | 0.013231 | 0.9915 | -0.059102 | 0.99166 | -0.057964 | 4.9005
221 | 0.0030363 | 0.00076085 | -0.0030363 | -0.00076089 | 6.7012e-08 | -3.8229e-08 | 0.0046041 | 0.0046041 | 0.0046041 | 0.98132 | -0.13074 | 0.9813 | -0.1309 | 1.7052
222 | -0.0048899 | -0.0012234 | 0.0048903 | 0.0012234 | 3.2814e-07 | 8.4241e-09 | 0.0074622 | 0.0074622 | 0.0074622 | 0.97499 | -0.1759 | 0.97506 | -0.17541 | 2.7638
223 | 0.0048899 | 0.0012234 | -0.0048899 | -0.0012234 | 4.6062e-08 | 1.1839e-09 | 0.0074622 | 0.0074622 | 0.0074622 | 0.97499 | -0.1759 | 0.97498 | -0.17597 | 2.7638
224 | -0.0028216 | -0.00070715 | 0.0028218 | 0.00070704 | 1.6387e-07 | -1.1867e-07 | 0.0042759 | 0.0042758 | 0.0042759 | 0.98191 | -0.1264 | 0.98197 | -0.12598 | 1.5837
225 | 0.0016185 | 0.00040562 | -0.0016185 | -0.00040563 | 1.5135e-09 | -4.5183e-09 | 0.0024527 | 0.0024527 | 0.0024527 | 0.98191 | -0.1264 | 0.98191 | -0.12641 | 0.9084
226 | 0.0015272 | 0.00038256 | -0.0015271 | -0.00038273 | 5.3644e-08 | -1.7646e-07 | 0.0023315 | 0.0023315 | 0.0023315 | 0.97466 | -0.17812 | 0.97463 | -0.17837 | 0.86353
227 | 0.030739 | 0.0077301 | -0.030738 | -0.0077297 | 1.0166e-06 | 3.8136e-07 | 0.046408 | 0.046408 | 0.046408 | 0.9858 | -0.098908 | 0.98577 | -0.099145 | 17.1881
228 | 0.0008748 | 0.00021917 | -0.00087479 | -0.00021924 | 6.2159e-09 | -6.9126e-08 | 0.0013265 | 0.0013265 | 0.0013265 | 0.9813 | -0.1309 | 0.98129 | -0.13095 | 0.4913
229 | 0.16394 | 0.041346 | -0.16394 | -0.041344 | 4.9226e-06 | 1.8781e-06 | 0.24563 | 0.24563 | 0.24563 | 0.9935 | -0.045003 | 0.99347 | -0.045218 | 30.3253
230 | 0.14687 | 0.037065 | -0.14681 | -0.037042 | 6.1588e-05 | 2.345e-05 | 0.22007 | 0.22007 | 0.22007 | 0.99347 | -0.045218 | 0.99304 | -0.048206 | 27.1695
231 | 0.010536 | 0.0026404 | -0.010532 | -0.002639 | 4.5902e-06 | 1.3853e-06 | 0.015803 | 0.015803 | 0.015803 | 0.99211 | -0.054815 | 0.99166 | -0.057964 | 5.8529
232 | 0.0011777 | 0.00029507 | -0.0011777 | -0.00029515 | 1.3931e-08 | -8.3444e-08 | 0.0017839 | 0.001784 | 0.001784 | 0.9823 | -0.12364 | 0.98229 | -0.12373 | 0.66073
233 | -0.16854 | -0.042542 | 0.16868 | 0.042596 | 0.00014076 | 5.3723e-05 | 0.25203 | 0.25203 | 0.25203 | 0.99554 | -0.030861 | 0.99639 | -0.024919 | 31.1143
234 | 0.1682 | 0.042457 | -0.16819 | -0.042452 | 1.2178e-05 | 4.6478e-06 | 0.25152 | 0.25152 | 0.25152 | 0.99554 | -0.030861 | 0.99546 | -0.031376 | 31.0516
235 | 0.16792 | 0.042384 | -0.16791 | -0.04238 | 9.1593e-06 | 3.4956e-06 | 0.25111 | 0.25111 | 0.25111 | 0.99546 | -0.031376 | 0.99541 | -0.031765 | 31.0009
236 | 0.16758 | 0.042298 | -0.16758 | -0.042297 | 4.6991e-06 | 1.7933e-06 | 0.25062 | 0.25062 | 0.25062 | 0.99541 | -0.031765 | 0.99538 | -0.031964 | 30.9408
237 | -0.00020447 | -5.1245e-05 | 0.00020447 | 5.1149e-05 | 4.7533e-10 | -9.5983e-08 | 0.00031319 | 0.00031315 | 0.00031319 | 0.97147 | -0.20121 | 0.97147 | -0.20119 | 0.116
238 | -0.0047799 | -0.0011977 | 0.0047799 | 0.0011977 | 2.4949e-08 | 3.6042e-10 | 0.0073214 | 0.0073214 | 0.0073214 | 0.97147 | -0.20119 | 0.97148 | -0.20116 | 2.7116
239 | 0.0045755 | 0.0011465 | -0.0045751 | -0.0011465 | 3.1016e-07 | -5.9993e-09 | 0.0070082 | 0.0070083 | 0.0070083 | 0.97147 | -0.20119 | 0.9714 | -0.20168 | 2.5957
240 | -0.0061941 | -0.0015521 | 0.0061943 | 0.0015521 | 1.9598e-07 | 3.2173e-08 | 0.0094874 | 0.0094874 | 0.0094874 | 0.97148 | -0.20116 | 0.97151 | -0.20093 | 3.5139
241 | 0.0039227 | 0.0009831 | -0.0039226 | -0.00098311 | 5.6123e-08 | -9.2514e-09 | 0.0060089 | 0.0060089 | 0.0060089 | 0.9714 | -0.20168 | 0.97139 | -0.20179 | 2.2255
242 | 0.00056616 | 0.00014182 | -0.00056616 | -0.00014189 | 2.8943e-09 | -7.5232e-08 | 0.00086723 | 0.00086726 | 0.00086726 | 0.9714 | -0.20168 | 0.9714 | -0.20172 | 0.32121
243 | 0.00079272 | 0.00019865 | -0.00079271 | -0.00019867 | 1.3725e-09 | -1.8095e-08 | 0.0012117 | 0.0012117 | 0.0012117 | 0.97346 | -0.1869 | 0.97345 | -0.18692 | 0.44879
244 | 0.0017141 | 0.00042942 | -0.001714 | -0.00042957 | 5.2727e-08 | -1.4545e-07 | 0.0025683 | 0.0025684 | 0.0025684 | 0.99307 | -0.048252 | 0.99304 | -0.048475 | 0.95124
245 | -0.047727 | -0.011986 | 0.047746 | 0.011994 | 1.9688e-05 | 7.493e-06 | 0.071616 | 0.071616 | 0.071616 | 0.99178 | -0.057308 | 0.9922 | -0.054341 | 26.5244
246 | 0.0066644 | 0.0016652 | -0.0066642 | -0.0016651 | 2.2048e-07 | 3.9601e-08 | 0.01002 | 0.01002 | 0.01002 | 0.98948 | -0.07349 | 0.98945 | -0.073731 | 3.7113
247 | 0.0066642 | 0.0016651 | -0.0066639 | -0.0016651 | 2.6985e-07 | 4.8472e-08 | 0.01002 | 0.01002 | 0.01002 | 0.98945 | -0.073731 | 0.98941 | -0.074025 | 3.7113
248 | -0.0019715 | -0.00049409 | 0.0019715 | 0.00049403 | 3.0747e-08 | -5.9185e-08 | 0.0029751 | 0.0029751 | 0.0029751 | 0.98604 | -0.097857 | 0.98605 | -0.097745 | 1.1019
249 | 0.0071752 | 0.0017979 | -0.007174 | -0.0017976 | 1.1824e-06 | 2.6032e-07 | 0.010987 | 0.010987 | 0.010987 | 0.97178 | -0.19895 | 0.97162 | -0.20014 | 4.0692
250 | 0.047896 | 0.012034 | -0.047875 | -0.012026 | 2.109e-05 | 8.027e-06 | 0.071808 | 0.071808 | 0.071808 | 0.99265 | -0.051175 | 0.9922 | -0.054341 | 26.5957
251 | 0.00012841 | 3.2042e-05 | -0.00012841 | -3.2183e-05 | 2.5307e-10 | -1.4117e-07 | 0.00019253 | 0.00019258 | 0.00019258 | 0.9922 | -0.054341 | 0.9922 | -0.054356 | 0.071326
252 | 0.0068652 | 0.0017202 | -0.006865 | -0.0017202 | 1.6991e-07 | 3.4843e-08 | 0.010514 | 0.010514 | 0.010514 | 0.97162 | -0.20014 | 0.97159 | -0.20032 | 3.894
253 | 0.0064603 | 0.0016188 | -0.0064597 | -0.0016187 | 5.4142e-07 | 9.8476e-08 | 0.0098939 | 0.009894 | 0.009894 | 0.97159 | -0.20032 | 0.97151 | -0.20093 | 3.6644

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23339 | 0.058773

## res_load
| p_mw | q_mvar
0 | 0.0043729 | 0.0010959
1 | 0.00033513 | 8.3992e-05
2 | 0.00010662 | 2.6722e-05
3 | 0.00018197 | 4.5605e-05
4 | 0.00010576 | 2.6505e-05
5 | 0.0006798 | 0.00017038
6 | 0.00027171 | 6.8098e-05
7 | 0.00018952 | 4.7497e-05
8 | 0.00044437 | 0.00011137
9 | 0.00033659 | 8.4358e-05
10 | 0.00016763 | 4.2013e-05
11 | 0.0017126 | 0.00042922
12 | 0.00010428 | 2.6135e-05
13 | 0.00032437 | 8.1296e-05
14 | 0.00025241 | 6.3261e-05
15 | 0.00034527 | 8.6534e-05
16 | 0.00028287 | 7.0894e-05
17 | 0.00041736 | 0.0001046
18 | 0.00026835 | 6.7254e-05
19 | 0.00039405 | 9.8758e-05
20 | 0.00029089 | 7.2905e-05
21 | 0.00019337 | 4.8464e-05
22 | 0.00015719 | 3.9397e-05
23 | 0.00028616 | 7.1718e-05
24 | 9.4064e-05 | 2.3575e-05
25 | 0.00015207 | 3.8113e-05
26 | 0.00052756 | 0.00013222
27 | 0.00022585 | 5.6603e-05
28 | 0.0016113 | 0.00040382
29 | 0.00093893 | 0.00023532
30 | 0.00029889 | 7.491e-05
31 | 0.00036592 | 9.1709e-05
32 | 0.00046167 | 0.00011571
33 | 0.00032359 | 8.11e-05
34 | 0.00041101 | 0.00010301
35 | 0.00061831 | 0.00015496
36 | 0.00048557 | 0.0001217
37 | 0.00054401 | 0.00013634
38 | 0.0002918 | 7.3133e-05
39 | 0.00017108 | 4.2876e-05
40 | 0.00027392 | 6.8651e-05
41 | 0.00034681 | 8.6918e-05
42 | 0.0017437 | 0.00043701
43 | 0.0016701 | 0.00041858
44 | 0.0022247 | 0.00055756
45 | 0.0098894 | 0.0024785
46 | 0.0025718 | 0.00064455
47 | 8.3537e-05 | 2.0936e-05
48 | 0.00010348 | 2.5934e-05
49 | 0.00011475 | 2.876e-05
50 | 0.00013921 | 3.489e-05
51 | 0.00024948 | 6.2525e-05
52 | 0.0026293 | 0.00065896
53 | 0.0020943 | 0.00052488
54 | 0.0016918 | 0.000424
55 | 0.0020394 | 0.00051112
56 | 0.0010563 | 0.00026474
57 | 0.0011382 | 0.00028526
58 | 0.00035162 | 8.8123e-05
59 | 0.00047257 | 0.00011844
60 | 0.00032775 | 8.2143e-05
61 | 0.0014637 | 0.00036684
62 | 0.00025961 | 6.5065e-05
63 | 0.00018066 | 4.5277e-05
64 | 0.00032292 | 8.093e-05
65 | 0.00017573 | 4.4043e-05
66 | 0.00017173 | 4.304e-05
67 | 0.0002306 | 5.7795e-05
68 | 0.00017851 | 4.4739e-05
69 | 0.00017098 | 4.285e-05
70 | 0.00028514 | 7.1462e-05
71 | 0.00044107 | 0.00011054
72 | 0.00026836 | 6.7257e-05
73 | 0.001148 | 0.00028771
74 | 0.0015148 | 0.00037965
75 | 0.0017834 | 0.00044696
76 | 0.0011862 | 0.0002973
77 | 0.00074459 | 0.00018661
78 | 0.0019965 | 0.00050036
79 | 0.00029528 | 7.4005e-05
80 | 0.0003982 | 9.9798e-05
81 | 0.0003162 | 7.9248e-05
82 | 0.00036945 | 9.2594e-05
83 | 0.00017496 | 4.385e-05
84 | 0.00015447 | 3.8713e-05
85 | 0.00016905 | 4.2369e-05
86 | 0.00030191 | 7.5665e-05
87 | 0.0038825 | 0.00097304
88 | 0.00063028 | 0.00015796
89 | 0.00036803 | 9.2238e-05
90 | 0.00030835 | 7.7281e-05
91 | 0.00041236 | 0.00010335
92 | 0.00072515 | 0.00018174
93 | 0.00053871 | 0.00013501
94 | 0.00029135 | 7.3019e-05
95 | 0.00032272 | 8.088e-05
96 | 0.0020959 | 0.00052528
97 | 0.00026176 | 6.5603e-05
98 | 0.00021186 | 5.3096e-05
99 | 0.00081051 | 0.00020313
100 | 0.00035154 | 8.8103e-05
101 | 0.00079485 | 0.00019921
102 | 0.0019818 | 0.00049668
103 | 0.00022521 | 5.6443e-05
104 | 0.00060479 | 0.00015157
105 | 0.0004775 | 0.00011967
106 | 0.00038618 | 9.6785e-05
107 | 0.00026274 | 6.585e-05
108 | 0.00029786 | 7.4651e-05
109 | 0.00019072 | 4.78e-05
110 | 0.00038734 | 9.7076e-05
111 | 0.0001676 | 4.2006e-05
112 | 0.00019435 | 4.8708e-05
113 | 0.00020133 | 5.0457e-05
114 | 0.00031786 | 7.9663e-05
115 | 0.00018911 | 4.7395e-05
116 | 0.00032681 | 8.1908e-05
117 | 0.00050512 | 0.0001266
118 | 0.00040336 | 0.00010109
119 | 0.00029535 | 7.4022e-05
120 | 0.00035897 | 8.9967e-05
121 | 0.00046664 | 0.00011695
122 | 0.00028755 | 7.2066e-05
123 | 0.000847 | 0.00021228
124 | 0.0017962 | 0.00045017
125 | 0.00041342 | 0.00010361
126 | 0.00084098 | 0.00021077
127 | 0.0006665 | 0.00016704
128 | 0.0015882 | 0.00039803
129 | 0.0036115 | 0.00090512
130 | 0.0035091 | 0.00087945
131 | 0.034308 | 0.0085983
132 | 0.00038663 | 9.6898e-05
133 | 0.0004471 | 0.00011205
134 | 0.00023139 | 5.7991e-05
135 | 0.00019969 | 5.0047e-05
136 | 0.00024692 | 6.1883e-05
137 | 0.00025027 | 6.2723e-05
138 | 0.00027947 | 7.0041e-05
139 | 0.0019074 | 0.00047804
140 | 0.0033948 | 0.00085083
141 | 0.0016707 | 0.00041871
142 | 0.0024744 | 0.00062015
143 | 0.0023141 | 0.00057997
144 | 0.00020096 | 5.0364e-05
145 | 0.00028906 | 7.2446e-05
146 | 0.00072539 | 0.0001818
147 | 0.00069469 | 0.00017411
148 | 0.00069464 | 0.00017409
149 | 0.00059094 | 0.0001481
150 | 0.0017959 | 0.0004501
151 | 0.0027478 | 0.00068866
152 | 0.0016289 | 0.00040824
153 | 0.0017956 | 0.00045002
154 | 0.0017153 | 0.00042989
155 | 0.001713 | 0.00042932
156 | 0.0017951 | 0.0004499
157 | 0.001796 | 0.00045011
158 | 0.0010219 | 0.00025612
159 | 0.00026528 | 6.6485e-05
160 | 0.00019255 | 4.8258e-05
161 | 0.00027667 | 6.934e-05
162 | 0.0012031 | 0.00030153
163 | 0.0016185 | 0.00040563
164 | 0.0015843 | 0.00039705
165 | 0.00029589 | 7.4158e-05
166 | 0.0021615 | 0.00054172
167 | 0.00087479 | 0.00021924
168 | 0.00039428 | 9.8816e-05
169 | 0.00026417 | 6.6207e-05
170 | 0.00037601 | 9.4237e-05
171 | 0.0021431 | 0.0005371
172 | 0.0017433 | 0.0004369
173 | 0.0017136 | 0.00042947
174 | 0.0003398 | 8.5161e-05
175 | 0.00037127 | 9.3049e-05
176 | 0.00027493 | 6.8904e-05
177 | 0.00032548 | 8.1573e-05
178 | 0.00020447 | 5.1245e-05
179 | 0.0014141 | 0.00035442
180 | 8.6289e-05 | 2.1626e-05
181 | 0.00012964 | 3.249e-05
182 | 0.0011777 | 0.00029515
183 | 0.0015271 | 0.00038273
184 | 0.00027852 | 6.9804e-05
185 | 0.0017962 | 0.00045017
186 | 0.001714 | 0.00042957
187 | 0.00012228 | 3.0646e-05
188 | 0.00018767 | 4.7036e-05
189 | 0.00013154 | 3.2967e-05
190 | 0.00025877 | 6.4854e-05
191 | 0.026827 | 0.0067236
192 | 0.00029406 | 7.3698e-05
193 | 0.0019715 | 0.00049409
194 | 0.00056616 | 0.00014189
195 | 0.0039226 | 0.00098311
196 | 0.00053928 | 0.00013516
197 | 0.00020834 | 5.2215e-05
198 | 0.00014502 | 3.6344e-05
199 | 0.00012841 | 3.2183e-05
200 | 0.00079271 | 0.00019867
201 | 0.00030887 | 7.7409e-05
202 | 0.00040475 | 0.00010144
203 | 0.00026543 | 6.6523e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1