## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2063-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2063-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2063-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2063-1_0_3_node_29 | 0.4 | n |  | TRUE
4 | bus_LV_2063-1_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2063-1_0_3_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_2063-1_0_3_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_2063-1_0_3_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_2063-1_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2063-1_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2063-1_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2063-1_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2063-1_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2063-1_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2063-1_0_3_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_2063-1_0_3_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_2063-1_0_3_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_2063-1_0_3_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_2063-1_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2063-1_0_3_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2063-1_0_3_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_2063-1_0_3_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_2063-1_0_3_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_2063-1_0_3_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2063-1_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2063-1_0_3_node_20 | 0.4 | n |  | TRUE
26 | bus_MV_33_0_node_1 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2063-1_0_3_load_0 | 0 | 0.0053213 | 0.0013336 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2063-1_0_3_load_1 | 1 | 0.0020955 | 0.00052518 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2063-1_0_3_load_29 | 3 | 0.0016305 | 0.00040863 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2063-1_0_3_load_3 | 4 | 0.00054152 | 0.00013572 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2063-1_0_3_load_6 | 8 | 0.0904 | 0.022656 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2063-1_0_3_load_11 | 13 | 0.0086392 | 0.0021652 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2063-1_0_3_load_19 | 15 | 0.0095781 | 0.0024005 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2063-1_0_3_load_14 | 16 | 0.00035854 | 8.9859e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2063-1_0_3_load_18 | 17 | 0.012096 | 0.0030316 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2063-1_0_3_load_12 | 18 | 0.0007148 | 0.00017915 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2063-1_0_3_load_13 | 19 | 0.0011151 | 0.00027946 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2063-1_0_3_load_22 | 20 | 0.00063392 | 0.00015887 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2063-1_0_3_load_26 | 22 | 0.001585 | 0.00039725 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2063-1_0_3_load_28 | 23 | 0.0029333 | 0.00073515 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2063-1_0_3_load_20 | 25 | 0.09171 | 0.022985 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2063-1_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.02572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2063-1_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.11209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2063-1_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.14906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2063-1_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.030134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2063-1_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.021396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2063-1_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.014382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2063-1_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.017665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2063-1_0_3_line_7 | NAYY 4x150 SE | 6 | 20 | 0.085526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2063-1_0_3_line_8 | NAYY 4x150 SE | 7 | 21 | 0.018352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2063-1_0_3_line_9 | NAYY 4x150 SE | 7 | 22 | 0.01764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2063-1_0_3_line_10 | NAYY 4x150 SE | 8 | 9 | 0.0068073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2063-1_0_3_line_11 | NAYY 4x150 SE | 9 | 13 | 0.044858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2063-1_0_3_line_12 | NAYY 4x150 SE | 10 | 11 | 0.016291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2063-1_0_3_line_13 | NAYY 4x150 SE | 10 | 12 | 0.01975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2063-1_0_3_line_14 | NAYY 4x150 SE | 11 | 13 | 0.028241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2063-1_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.015024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2063-1_0_3_line_16 | NAYY 4x150 SE | 12 | 15 | 0.018241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2063-1_0_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.056362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2063-1_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.023541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_2063-1_0_3_line_19 | NAYY 4x150 SE | 16 | 19 | 0.018552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2063-1_0_3_line_20 | NAYY 4x150 SE | 17 | 25 | 0.061089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_2063-1_0_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.041474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2063-1_0_3_line_22 | NAYY 4x150 SE | 21 | 23 | 0.098963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2063-1_0_3_line_23 | NAYY 4x150 SE | 22 | 24 | 0.11066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2063-1_0_3_line_24 | NAYY 4x150 SE | 24 | 25 | 0.077986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2063-1_0_3_trafo_20 | 0.25 MVA 20/0.4 kV | 26 | 25 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2559293.6423 | 1171519.0024 | 2559306.2489 | 1171520.8676 | 2559315.3301 | 1171522.2066 | 2559319.0863 | 1171522.7628
1 | 2559185.663 | 1171523.8341 | 2559193.0696 | 1171518.5253 | 2559200.6292 | 1171514.3494 | 2559205.9006 | 1171512.2568 | 2559212.811 | 1171510.4644 | 2559221.1893 | 1171509.6847 | 2559227.8675 | 1171509.7392 | 2559236.5703 | 1171510.5582 | 2559293.6423 | 1171519.0024
2 | 2559319.0863 | 1171522.7628 | 2559401.9861 | 1171398.8761
3 | 2559185.663 | 1171523.8341 | 2559165.1935 | 1171501.7191
4 | 2559151.1334 | 1171485.605 | 2559157.5744 | 1171493.4874 | 2559165.1935 | 1171501.7191
5 | 2559151.1334 | 1171485.605 | 2559152.4822 | 1171483.7281 | 2559153.3185 | 1171481.8548 | 2559153.9559 | 1171479.9828 | 2559154.3476 | 1171477.979 | 2559154.2662 | 1171475.0114 | 2559153.6798 | 1171472.036
6 | 2559151.1334 | 1171485.605 | 2559149.6 | 1171487.3274 | 2559147.5592 | 1171488.6754 | 2559144.9208 | 1171489.894 | 2559141.8966 | 1171490.615 | 2559138.6763 | 1171490.6259 | 2559135.0599 | 1171489.7501
7 | 2559153.6798 | 1171472.036 | 2559187.3584 | 1171452.7408 | 2559223.6942 | 1171423.3855
8 | 2559126.0794 | 1171475.1593 | 2559126.129 | 1171477.9382 | 2559126.5592 | 1171480.4588 | 2559127.5569 | 1171483.1756 | 2559129.3254 | 1171485.6427 | 2559131.9424 | 1171488.0149 | 2559135.0599 | 1171489.7501
9 | 2559135.0599 | 1171489.7501 | 2559127.0506 | 1171497.5311 | 2559122.4627 | 1171502.0981
10 | 2558924.9259 | 1171543.3267 | 2558931.0478 | 1171540.3498
11 | 2558924.9259 | 1171543.3267 | 2558910.4557 | 1171550.3408 | 2558887.5566 | 1171532.911
12 | 2558877.9942 | 1171490.4766 | 2558876.6384 | 1171499.1237 | 2558877.9057 | 1171506.5523
13 | 2558890.2852 | 1171475.7956 | 2558882.3685 | 1171481.4084 | 2558877.9942 | 1171490.4766
14 | 2558877.9057 | 1171506.5523 | 2558880.5016 | 1171518.0961 | 2558887.5566 | 1171532.911
15 | 2558890.2852 | 1171475.7956 | 2558881.8543 | 1171463.3469
16 | 2558890.2852 | 1171475.7956 | 2558898.2981 | 1171486.4017 | 2558901.8895 | 1171489.8059
17 | 2558881.8543 | 1171463.3469 | 2558875.5325 | 1171470.6386 | 2558869.6503 | 1171484.0193 | 2558866.5773 | 1171494.3348 | 2558859.3469 | 1171506.3129 | 2558852.4498 | 1171508.8251
18 | 2558919.0789 | 1171505.8802 | 2558917.6621 | 1171504.7563 | 2558901.8895 | 1171489.8059
19 | 2558852.4498 | 1171508.8251 | 2558852.0677 | 1171508.9643 | 2558842.9063 | 1171513.7742 | 2558837.3844 | 1171519.2798
20 | 2558969.1203 | 1171540.4933 | 2558951.2557 | 1171531.2176 | 2558949.2419 | 1171529.8085 | 2558919.0789 | 1171505.8802
21 | 2558808.3778 | 1171548.9161 | 2558819.3626 | 1171537.2484 | 2558837.3844 | 1171519.2798
22 | 2559126.0794 | 1171475.1593 | 2559119.8936 | 1171475.535 | 2559114.486 | 1171475.5942 | 2559108.3393 | 1171474.9692 | 2559100.5652 | 1171473.4993 | 2559095.4678 | 1171471.9555 | 2559088.3448 | 1171469.5028 | 2559079.5435 | 1171465.4831 | 2559069.3205 | 1171459.3831 | 2559058.7738 | 1171451.8067 | 2559046.2693 | 1171440.9532 | 2559039.5226 | 1171434.5755
23 | 2559038.7764 | 1171574.4967 | 2559120.8433 | 1171503.71 | 2559122.4627 | 1171502.0981
24 | 2559038.7764 | 1171574.4967 | 2559027.4562 | 1171568.9935 | 2559007.1596 | 1171555.1251 | 2558976.1278 | 1171544.1318 | 2558969.1203 | 1171540.4933

## bus_geodata
| x | y | coords
0 | 2559293.6423 | 1171519.0024
1 | 2559319.0863 | 1171522.7628
2 | 2559185.663 | 1171523.8341
3 | 2559401.9861 | 1171398.8761
4 | 2559165.1935 | 1171501.7191
5 | 2559151.1334 | 1171485.605
6 | 2559153.6798 | 1171472.036
7 | 2559135.0599 | 1171489.7501
8 | 2558931.0478 | 1171540.3498
9 | 2558924.9259 | 1171543.3267
10 | 2558877.9942 | 1171490.4766
11 | 2558877.9057 | 1171506.5523
12 | 2558890.2852 | 1171475.7956
13 | 2558887.5566 | 1171532.911
14 | 2558881.8543 | 1171463.3469
15 | 2558901.8895 | 1171489.8059
16 | 2558852.4498 | 1171508.8251
17 | 2558919.0789 | 1171505.8802
18 | 2558808.3778 | 1171548.9161
19 | 2558837.3844 | 1171519.2798
20 | 2559223.6942 | 1171423.3855
21 | 2559126.0794 | 1171475.1593
22 | 2559122.4627 | 1171502.0981
23 | 2559039.5226 | 1171434.5755
24 | 2559038.7764 | 1171574.4967
25 | 2558969.1203 | 1171540.4933
26 | 2559038.7764 | 1171574.4967

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99328 | -0.047262 | 0.0053213 | 0.0013336
1 | 0.99314 | -0.048236 | 0.0020955 | 0.00052518
2 | 0.99474 | -0.036994 | 0 | 0
3 | 0.99279 | -0.050707 | 0.0016305 | 0.00040863
4 | 0.99513 | -0.034236 | 0.00054152 | 0.00013572
5 | 0.99542 | -0.032162 | 0 | 0
6 | 0.99541 | -0.032255 | 0 | 0
7 | 0.99568 | -0.030336 | 0 | 0
8 | 0.97377 | -0.18391 | 0.0904 | 0.022656
9 | 0.97467 | -0.17744 | 0 | 0
10 | 0.98706 | -0.089612 | 0 | 0
11 | 0.9847 | -0.10618 | 0 | 0
12 | 0.98992 | -0.069631 | 0 | 0
13 | 0.98061 | -0.13509 | 0.0086392 | 0.0021652
14 | 0.98987 | -0.069967 | 0 | 0
15 | 0.99262 | -0.050871 | 0.0095781 | 0.0024005
16 | 0.9897 | -0.071229 | 0.00035854 | 8.9859e-05
17 | 0.99453 | -0.037683 | 0.012096 | 0.0030316
18 | 0.98961 | -0.071879 | 0.0007148 | 0.00017915
19 | 0.98965 | -0.071576 | 0.0011151 | 0.00027946
20 | 0.99533 | -0.032805 | 0.00063392 | 0.00015887
21 | 0.9956 | -0.03088 | 0 | 0
22 | 0.99601 | -0.027991 | 0.001585 | 0.00039725
23 | 0.99519 | -0.033809 | 0.0029333 | 0.00073515
24 | 0.99835 | -0.011548 | 0 | 0
25 | 1 | 0 | -0.14121 | -0.035545
26 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.003727 | 0.00093196 | -0.0037265 | -0.0009321 | 5.0021e-07 | -1.4048e-07 | 0.0055826 | 0.0055828 | 0.0055828 | 0.99328 | -0.047262 | 0.99314 | -0.048236 | 2.0677
1 | -0.0090483 | -0.0022656 | 0.0090612 | 0.0022691 | 1.2849e-05 | 3.4892e-06 | 0.013554 | 0.013554 | 0.013554 | 0.99328 | -0.047262 | 0.99474 | -0.036994 | 5.0201
2 | 0.001631 | 0.00040692 | -0.0016305 | -0.00040863 | 5.5534e-07 | -1.7146e-06 | 0.0024431 | 0.0024438 | 0.0024438 | 0.99314 | -0.048236 | 0.99279 | -0.050707 | 0.9051
3 | -0.0090612 | -0.0022691 | 0.0090646 | 0.00227 | 3.4544e-06 | 9.3726e-07 | 0.013554 | 0.013554 | 0.013554 | 0.99474 | -0.036994 | 0.99513 | -0.034236 | 5.02
4 | -0.0096061 | -0.0024057 | 0.0096089 | 0.0024065 | 2.7544e-06 | 7.8134e-07 | 0.014363 | 0.014363 | 0.014363 | 0.99513 | -0.034236 | 0.99542 | -0.032162 | 5.3198
5 | 0.00063397 | 0.0001576 | -0.00063397 | -0.00015778 | 8.0531e-09 | -1.8386e-07 | 0.00094725 | 0.00094731 | 0.00094731 | 0.99542 | -0.032162 | 0.99541 | -0.032255 | 0.35086
6 | -0.010243 | -0.0025641 | 0.010245 | 0.0025649 | 2.5839e-06 | 7.6413e-07 | 0.015311 | 0.015311 | 0.015311 | 0.99542 | -0.032162 | 0.99568 | -0.030336 | 5.6706
7 | 0.00063397 | 0.00015778 | -0.00063392 | -0.00015887 | 4.7913e-08 | -1.0933e-06 | 0.00094731 | 0.0009477 | 0.0009477 | 0.99541 | -0.032255 | 0.99533 | -0.032805 | 0.351
8 | 0.0029347 | 0.00073416 | -0.0029345 | -0.00073432 | 2.2023e-07 | -1.5397e-07 | 0.0043853 | 0.0043854 | 0.0043854 | 0.99568 | -0.030336 | 0.9956 | -0.03088 | 1.6242
9 | -0.01318 | -0.0032991 | 0.013184 | 0.0033005 | 4.2701e-06 | 1.4128e-06 | 0.019696 | 0.019696 | 0.019696 | 0.99568 | -0.030336 | 0.99601 | -0.027991 | 7.2948
10 | -0.0904 | -0.022656 | 0.090481 | 0.022687 | 8.1059e-05 | 3.1092e-05 | 0.13814 | 0.13814 | 0.13814 | 0.97377 | -0.18391 | 0.97467 | -0.17744 | 51.163
11 | -0.090481 | -0.022687 | 0.091015 | 0.022892 | 0.00053415 | 0.00020488 | 0.13814 | 0.13814 | 0.13814 | 0.97467 | -0.17744 | 0.98061 | -0.13509 | 51.163
12 | 0.10029 | 0.025301 | -0.10006 | -0.025212 | 0.00023255 | 8.9235e-05 | 0.15125 | 0.15125 | 0.15125 | 0.98706 | -0.089612 | 0.9847 | -0.10618 | 56.0182
13 | -0.10029 | -0.025301 | 0.10057 | 0.02541 | 0.00028193 | 0.00010818 | 0.15125 | 0.15125 | 0.15125 | 0.98706 | -0.089612 | 0.98992 | -0.069631 | 56.0182
14 | 0.10006 | 0.025212 | -0.099654 | -0.025058 | 0.00040314 | 0.00015469 | 0.15125 | 0.15125 | 0.15125 | 0.9847 | -0.10618 | 0.98061 | -0.13509 | 56.0183
15 | 0.002189 | 0.00054701 | -0.0021889 | -0.00054717 | 1.0147e-07 | -1.5411e-07 | 0.0032899 | 0.00329 | 0.00329 | 0.98992 | -0.069631 | 0.98987 | -0.069967 | 1.2185
16 | -0.10276 | -0.025957 | 0.10303 | 0.026061 | 0.00027184 | 0.00010432 | 0.15454 | 0.15454 | 0.15454 | 0.98992 | -0.069631 | 0.99262 | -0.050871 | 57.2366
17 | 0.0021889 | 0.00054717 | -0.0021885 | -0.00054774 | 3.807e-07 | -5.7798e-07 | 0.00329 | 0.0032902 | 0.0032902 | 0.98987 | -0.069967 | 0.9897 | -0.071229 | 1.2186
18 | -0.11261 | -0.028461 | 0.11282 | 0.028541 | 0.00020952 | 7.9973e-05 | 0.1689 | 0.1689 | 0.1689 | 0.99262 | -0.050871 | 0.99453 | -0.037683 | 31.2772
19 | 0.00183 | 0.00045788 | -0.0018299 | -0.00045809 | 8.762e-08 | -2.0468e-07 | 0.0027511 | 0.0027512 | 0.0027512 | 0.9897 | -0.071229 | 0.98965 | -0.071576 | 1.019
20 | -0.12492 | -0.031573 | 0.12558 | 0.031828 | 0.00066646 | 0.00025474 | 0.187 | 0.18699 | 0.187 | 0.99453 | -0.037683 | 1 | 0 | 34.6287
21 | -0.0007148 | -0.00017915 | 0.00071483 | 0.00017863 | 2.9892e-08 | -5.2138e-07 | 0.0010748 | 0.0010746 | 0.0010748 | 0.98961 | -0.071879 | 0.98965 | -0.071576 | 0.39808
22 | 0.0029345 | 0.00073432 | -0.0029333 | -0.00073515 | 1.1877e-06 | -8.2957e-07 | 0.0043854 | 0.0043859 | 0.0043859 | 0.9956 | -0.03088 | 0.99519 | -0.033809 | 1.6244
23 | -0.014769 | -0.0036977 | 0.014803 | 0.0037092 | 3.3615e-05 | 1.1485e-05 | 0.022064 | 0.022063 | 0.022064 | 0.99601 | -0.027991 | 0.99835 | -0.011548 | 8.1718
24 | -0.014803 | -0.0037092 | 0.014827 | 0.0037173 | 2.3688e-05 | 8.0895e-06 | 0.022063 | 0.022063 | 0.022063 | 0.99835 | -0.011548 | 1 | 0 | 8.1716

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23292 | 0.05853

## res_load
| p_mw | q_mvar
0 | 0.0053213 | 0.0013336
1 | 0.0020955 | 0.00052518
2 | 0.0016305 | 0.00040863
3 | 0.00054152 | 0.00013572
4 | 0.0904 | 0.022656
5 | 0.0086392 | 0.0021652
6 | 0.0095781 | 0.0024005
7 | 0.00035854 | 8.9859e-05
8 | 0.012096 | 0.0030316
9 | 0.0007148 | 0.00017915
10 | 0.0011151 | 0.00027946
11 | 0.00063392 | 0.00015887
12 | 0.001585 | 0.00039725
13 | 0.0029333 | 0.00073515
14 | 0.09171 | 0.022985

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1