## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2067-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2067-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2067-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2067-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2067-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2067-1_0_4_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_2067-1_0_4_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_2067-1_0_4_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_2067-1_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2067-1_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2067-1_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2067-1_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2067-1_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2067-1_0_4_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_2067-1_0_4_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_2067-1_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_2067-1_0_4_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_2067-1_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2067-1_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2067-1_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2067-1_0_4_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_2067-1_0_4_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_2067-1_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2067-1_0_4_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_2067-1_0_4_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_2067-1_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_2067-1_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2067-1_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_2067-1_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2067-1_0_4_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_2067-1_0_4_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_2067-1_0_4_node_31 | 0.4 | n |  | TRUE
32 | bus_MV_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2067-1_0_4_load_0 | 0 | 0.0015741 | 0.0003945 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2067-1_0_4_load_1 | 1 | 0.0023505 | 0.00058909 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2067-1_0_4_load_2 | 2 | 0.00075611 | 0.0001895 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2067-1_0_4_load_4 | 4 | 0.0013524 | 0.00033894 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2067-1_0_4_load_26 | 5 | 0.008241 | 0.0020654 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2067-1_0_4_load_30 | 7 | 0.0045068 | 0.0011295 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2067-1_0_4_load_5 | 8 | 0.00041775 | 0.0001047 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2067-1_0_4_load_6 | 9 | 0.0005057 | 0.00012674 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2067-1_0_4_load_7 | 10 | 0.00021797 | 5.4629e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2067-1_0_4_load_8 | 11 | 0.00025256 | 6.3297e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2067-1_0_4_load_9 | 12 | 0.00043003 | 0.00010778 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2067-1_0_4_load_20 | 14 | 0.00048888 | 0.00012253 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2067-1_0_4_load_19 | 15 | 0.0010215 | 0.00025601 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2067-1_0_4_load_25 | 16 | 0.0052098 | 0.0013057 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2067-1_0_4_load_10 | 17 | 0.0002648 | 6.6365e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2067-1_0_4_load_23 | 21 | 0.00022383 | 5.6098e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2067-1_0_4_load_12 | 22 | 0.0083203 | 0.0020853 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2067-1_0_4_load_27 | 23 | 0.00044141 | 0.00011063 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2067-1_0_4_load_29 | 24 | 0.0013905 | 0.00034849 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2067-1_0_4_load_22 | 25 | 0.00089643 | 0.00022467 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2067-1_0_4_load_14 | 26 | 0.00043283 | 0.00010848 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2067-1_0_4_load_21 | 29 | 0.00062926 | 0.00015771 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2067-1_0_4_load_28 | 30 | 0.0012181 | 0.00030529 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2067-1_0_4_load_31 | 31 | 0.0081275 | 0.0020369 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2067-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2067-1_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.03693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2067-1_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.063497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2067-1_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.034091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2067-1_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.063362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2067-1_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.01366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2067-1_0_4_line_6 | NAYY 4x150 SE | 6 | 7 | 0.47704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_2067-1_0_4_line_7 | NAYY 4x150 SE | 7 | 22 | 0.38163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_2067-1_0_4_line_8 | NAYY 4x150 SE | 8 | 9 | 0.012365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2067-1_0_4_line_9 | NAYY 4x150 SE | 8 | 10 | 0.01064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2067-1_0_4_line_10 | NAYY 4x150 SE | 9 | 11 | 0.032896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2067-1_0_4_line_11 | NAYY 4x150 SE | 10 | 12 | 0.1194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2067-1_0_4_line_12 | NAYY 4x150 SE | 11 | 13 | 0.014793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2067-1_0_4_line_13 | NAYY 4x150 SE | 12 | 14 | 0.022708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2067-1_0_4_line_14 | NAYY 4x150 SE | 13 | 15 | 0.136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_2067-1_0_4_line_15 | NAYY 4x150 SE | 14 | 16 | 0.037846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2067-1_0_4_line_16 | NAYY 4x150 SE | 15 | 23 | 0.062747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2067-1_0_4_line_17 | NAYY 4x150 SE | 15 | 22 | 0.26959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_2067-1_0_4_line_18 | NAYY 4x150 SE | 16 | 31 | 0.22507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2067-1_0_4_line_19 | NAYY 4x150 SE | 17 | 18 | 0.022176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2067-1_0_4_line_20 | NAYY 4x150 SE | 18 | 19 | 0.14286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2067-1_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.012733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2067-1_0_4_line_22 | NAYY 4x150 SE | 19 | 21 | 0.10329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2067-1_0_4_line_23 | NAYY 4x150 SE | 20 | 24 | 0.035411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2067-1_0_4_line_24 | NAYY 4x150 SE | 21 | 25 | 0.024425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2067-1_0_4_line_25 | NAYY 4x150 SE | 23 | 30 | 0.0054099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2067-1_0_4_line_26 | NAYY 4x150 SE | 24 | 30 | 0.055993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2067-1_0_4_line_27 | NAYY 4x150 SE | 25 | 29 | 0.056084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2067-1_0_4_line_28 | NAYY 4x150 SE | 26 | 27 | 0.052385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2067-1_0_4_line_29 | NAYY 4x150 SE | 27 | 28 | 0.027758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2067-1_0_4_line_30 | NAYY 4x150 SE | 28 | 29 | 0.0093088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2067-1_0_4_trafo_17 | 0.25 MVA 20/0.4 kV | 32 | 6 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2566370.7987 | 1169655.5872 | 2566370.7987 | 1169655.5872 | 2566397.265 | 1169651.4254 | 2566397.265 | 1169651.4254
1 | 2566370.7987 | 1169655.5872 | 2566334.0168 | 1169658.8858
2 | 2566458.7639 | 1169635.6503 | 2566452.6805 | 1169636.9294 | 2566397.265 | 1169651.4254
3 | 2566300.0036 | 1169657.4845 | 2566323.2882 | 1169659.2894 | 2566333.7687 | 1169658.908 | 2566334.0168 | 1169658.8858
4 | 2566458.7639 | 1169635.6503 | 2566462.4025 | 1169660.9541 | 2566473.7278 | 1169678.8999 | 2566480.0781 | 1169684.2893 | 2566488.3227 | 1169684.5371
5 | 2566286.384 | 1169656.4289 | 2566300.0036 | 1169657.4845
6 | 2566286.384 | 1169656.4289 | 2566266.6812 | 1169179.7941
7 | 2565960.2902 | 1169407.3148 | 2566266.6812 | 1169179.7941
8 | 2566039.9076 | 1169731.8383 | 2566035.0539 | 1169720.466
9 | 2566039.9076 | 1169731.8383 | 2566044.0844 | 1169741.6243
10 | 2566035.0539 | 1169720.466 | 2566031.5912 | 1169712.353 | 2566023.7274 | 1169689.5987
11 | 2566122.2821 | 1169831.2283 | 2566089.8775 | 1169798.3337 | 2566047.1778 | 1169748.8723 | 2566044.0844 | 1169741.6243
12 | 2566018.8955 | 1169675.6171 | 2566023.7274 | 1169689.5987
13 | 2566139.372 | 1169846.1766 | 2566123.0609 | 1169832.0188 | 2566122.2821 | 1169831.2283
14 | 2566018.8955 | 1169675.6171 | 2565990.6041 | 1169681.7031 | 2565960.979 | 1169687.3521 | 2565938.4992 | 1169684.7341 | 2565896.8614 | 1169668.9184 | 2565887.3495 | 1169666.8542
15 | 2566139.372 | 1169846.1766 | 2566144.0059 | 1169850.1987 | 2566166.1617 | 1169864.6698 | 2566170.7714 | 1169867.1755
16 | 2565825.2897 | 1169665.6672 | 2565849.1691 | 1169662.1533 | 2565869.6572 | 1169663.0148 | 2565887.3495 | 1169666.8542
17 | 2565887.3495 | 1169666.8542 | 2565960.2902 | 1169407.3148
18 | 2566170.7714 | 1169867.1755 | 2566343.8593 | 1170011.0441
19 | 2565690.3217 | 1169541.7657 | 2565698.7071 | 1169538.9384 | 2565711.1417 | 1169534.1444
20 | 2565690.3217 | 1169541.7657 | 2565695.7737 | 1169559.8105 | 2565703.856 | 1169592.2476 | 2565707.4843 | 1169612.5262 | 2565712.2592 | 1169639.3015 | 2565716.6224 | 1169670.3482 | 2565718.0951 | 1169681.6678
21 | 2565730.5824 | 1169684.331 | 2565718.0951 | 1169681.6678
22 | 2565718.0951 | 1169681.6678 | 2565692.1719 | 1169676.3468 | 2565665.4929 | 1169668.6735 | 2565619.5562 | 1169657.22 | 2565617.8488 | 1169657.0071
23 | 2565730.5824 | 1169684.331 | 2565734.8454 | 1169684.529 | 2565757.2862 | 1169681.6658 | 2565765.5367 | 1169679.5376
24 | 2565593.5633 | 1169654.6564 | 2565600.0384 | 1169654.7864 | 2565617.8488 | 1169657.0071
25 | 2565825.2897 | 1169665.6672 | 2565819.9374 | 1169666.4548
26 | 2565819.9374 | 1169666.4548 | 2565811.364 | 1169667.7163 | 2565765.5367 | 1169679.5376
27 | 2565593.5633 | 1169654.6564 | 2565584.9708 | 1169654.4839 | 2565566.4154 | 1169655.7579 | 2565543.7172 | 1169661.7582 | 2565538.7586 | 1169663.9285
28 | 2565508.3177 | 1169650.545 | 2565522.7467 | 1169614.3544 | 2565531.5938 | 1169604.2585
29 | 2565508.3177 | 1169650.545 | 2565530.2309 | 1169667.661
30 | 2565530.2309 | 1169667.661 | 2565538.7586 | 1169663.9285

## bus_geodata
| x | y | coords
0 | 2566370.7987 | 1169655.5872
1 | 2566397.265 | 1169651.4254
2 | 2566334.0168 | 1169658.8858
3 | 2566458.7639 | 1169635.6503
4 | 2566300.0036 | 1169657.4845
5 | 2566488.3227 | 1169684.5371
6 | 2566286.384 | 1169656.4289
7 | 2566266.6812 | 1169179.7941
8 | 2566039.9076 | 1169731.8383
9 | 2566035.0539 | 1169720.466
10 | 2566044.0844 | 1169741.6243
11 | 2566023.7274 | 1169689.5987
12 | 2566122.2821 | 1169831.2283
13 | 2566018.8955 | 1169675.6171
14 | 2566139.372 | 1169846.1766
15 | 2565887.3495 | 1169666.8542
16 | 2566170.7714 | 1169867.1755
17 | 2565711.1417 | 1169534.1444
18 | 2565690.3217 | 1169541.7657
19 | 2565718.0951 | 1169681.6678
20 | 2565730.5824 | 1169684.331
21 | 2565617.8488 | 1169657.0071
22 | 2565960.2902 | 1169407.3148
23 | 2565825.2897 | 1169665.6672
24 | 2565765.5367 | 1169679.5376
25 | 2565593.5633 | 1169654.6564
26 | 2565531.5938 | 1169604.2585
27 | 2565508.3177 | 1169650.545
28 | 2565530.2309 | 1169667.661
29 | 2565538.7586 | 1169663.9285
30 | 2565819.9374 | 1169666.4548
31 | 2566343.8593 | 1170011.0441
32 | 2566286.384 | 1169656.4289

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99845 | -0.010859 | 0.0015741 | 0.0003945
1 | 0.99804 | -0.013705 | 0.0023505 | 0.00058909
2 | 0.99909 | -0.0063582 | 0.00075611 | 0.0001895
3 | 0.9973 | -0.018958 | 0 | 0
4 | 0.99972 | -0.0019497 | 0.0013524 | 0.00033894
5 | 0.99655 | -0.024203 | 0.008241 | 0.0020654
6 | 1 | 0 | -0.050745 | -0.012544
7 | 0.99192 | -0.056604 | 0.0045068 | 0.0011295
8 | 0.98048 | -0.13779 | 0.00041775 | 0.0001047
9 | 0.98074 | -0.13587 | 0.0005057 | 0.00012674
10 | 0.98025 | -0.13939 | 0.00021797 | 5.4629e-05
11 | 0.98148 | -0.13061 | 0.00025256 | 6.3297e-05
12 | 0.97776 | -0.15716 | 0.00043003 | 0.00010778
13 | 0.98182 | -0.1282 | 0 | 0
14 | 0.9773 | -0.16044 | 0.00048888 | 0.00012253
15 | 0.98338 | -0.11716 | 0.0010215 | 0.00025601
16 | 0.97657 | -0.16573 | 0.0052098 | 0.0013057
17 | 0.98229 | -0.125 | 0.0002648 | 6.6365e-05
18 | 0.9823 | -0.12494 | 0 | 0
19 | 0.98236 | -0.12453 | 0 | 0
20 | 0.9824 | -0.12421 | 0 | 0
21 | 0.98203 | -0.12689 | 0.00022383 | 5.6098e-05
22 | 0.98628 | -0.096508 | 0.0083203 | 0.0020853
23 | 0.98288 | -0.12076 | 0.00044141 | 0.00011063
24 | 0.98253 | -0.12329 | 0.0013905 | 0.00034849
25 | 0.98196 | -0.12739 | 0.00089643 | 0.00022467
26 | 0.98182 | -0.12841 | 0.00043283 | 0.00010848
27 | 0.98185 | -0.12818 | 0 | 0
28 | 0.98187 | -0.12805 | 0 | 0
29 | 0.98187 | -0.12801 | 0.00062926 | 0.00015771
30 | 0.98284 | -0.12104 | 0.0012181 | 0.00030529
31 | 0.97389 | -0.18495 | 0.0081275 | 0.0020369
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.010608 | 0.0026587 | -0.010603 | -0.0026574 | 4.1782e-06 | 1.2567e-06 | 0.015809 | 0.015809 | 0.015809 | 0.99845 | -0.010859 | 0.99804 | -0.013705 | 5.8552
1 | -0.012182 | -0.0030532 | 0.012189 | 0.0030556 | 7.5952e-06 | 2.4379e-06 | 0.018155 | 0.018155 | 0.018155 | 0.99845 | -0.010859 | 0.99909 | -0.0063582 | 6.724
2 | 0.008253 | 0.0020683 | -0.008247 | -0.0020669 | 5.9991e-06 | 1.4782e-06 | 0.012305 | 0.012305 | 0.012305 | 0.99804 | -0.013705 | 0.9973 | -0.018958 | 4.5574
3 | -0.012945 | -0.0032451 | 0.012953 | 0.0032477 | 7.908e-06 | 2.5948e-06 | 0.019281 | 0.019281 | 0.019281 | 0.99909 | -0.0063582 | 0.99972 | -0.0019497 | 7.141
4 | 0.008247 | 0.0020669 | -0.008241 | -0.0020654 | 5.9866e-06 | 1.4764e-06 | 0.012305 | 0.012305 | 0.012305 | 0.9973 | -0.018958 | 0.99655 | -0.024203 | 4.5575
5 | -0.014306 | -0.0035867 | 0.01431 | 0.003588 | 3.8649e-06 | 1.3074e-06 | 0.021294 | 0.021293 | 0.021294 | 0.99972 | -0.0019497 | 1 | 0 | 7.8865
6 | 0.035635 | 0.008956 | -0.035356 | -0.0088673 | 0.00027912 | 8.8731e-05 | 0.053035 | 0.053041 | 0.053041 | 1 | 0 | 0.99192 | -0.056604 | 6.5483
7 | 0.030849 | 0.0077378 | -0.030679 | -0.0076871 | 0.00017004 | 5.0706e-05 | 0.046281 | 0.046286 | 0.046286 | 0.99192 | -0.056604 | 0.98628 | -0.096508 | 5.7143
8 | -0.014968 | -0.0037564 | 0.014972 | 0.0037578 | 3.9821e-06 | 1.3756e-06 | 0.022718 | 0.022718 | 0.022718 | 0.98048 | -0.13779 | 0.98074 | -0.13587 | 8.4141
9 | 0.01455 | 0.0036517 | -0.014547 | -0.0036506 | 3.2381e-06 | 1.1113e-06 | 0.022084 | 0.022084 | 0.022084 | 0.98048 | -0.13779 | 0.98025 | -0.13939 | 8.1793
10 | -0.015478 | -0.0038845 | 0.015489 | 0.0038884 | 1.1322e-05 | 3.9391e-06 | 0.023485 | 0.023485 | 0.023485 | 0.98074 | -0.13587 | 0.98148 | -0.13061 | 8.6983
11 | 0.014329 | 0.0035959 | -0.014294 | -0.0035839 | 3.5257e-05 | 1.2059e-05 | 0.021753 | 0.021754 | 0.021754 | 0.98025 | -0.13939 | 0.97776 | -0.15716 | 8.057
12 | -0.015742 | -0.0039517 | 0.015747 | 0.0039536 | 5.2587e-06 | 1.8355e-06 | 0.023868 | 0.023868 | 0.023868 | 0.98148 | -0.13061 | 0.98182 | -0.1282 | 8.8401
13 | 0.013864 | 0.0034761 | -0.013858 | -0.003474 | 6.3083e-06 | 2.1416e-06 | 0.021099 | 0.0211 | 0.0211 | 0.97776 | -0.15716 | 0.9773 | -0.16044 | 7.8146
14 | -0.015747 | -0.0039536 | 0.015771 | 0.0039594 | 2.4172e-05 | 5.8515e-06 | 0.023868 | 0.023867 | 0.023868 | 0.98182 | -0.1282 | 0.98338 | -0.11716 | 4.42
15 | 0.013369 | 0.0033514 | -0.013359 | -0.0033482 | 9.7849e-06 | 3.2895e-06 | 0.020355 | 0.020355 | 0.020355 | 0.9773 | -0.16044 | 0.97657 | -0.16573 | 7.539
16 | 0.0055026 | 0.0013721 | -0.0054999 | -0.0013718 | 2.713e-06 | 2.4781e-07 | 0.0083239 | 0.0083242 | 0.0083242 | 0.98338 | -0.11716 | 0.98288 | -0.12076 | 3.083
17 | -0.022295 | -0.0055875 | 0.022359 | 0.0056018 | 6.3815e-05 | 1.4253e-05 | 0.033736 | 0.033733 | 0.033736 | 0.98338 | -0.11716 | 0.98628 | -0.096508 | 4.165
18 | 0.0081492 | 0.0020425 | -0.0081275 | -0.0020369 | 2.1656e-05 | 5.521e-06 | 0.012417 | 0.012418 | 0.012418 | 0.97657 | -0.16573 | 0.97389 | -0.18495 | 4.5993
19 | -0.0002648 | -6.6365e-05 | 0.0002648 | 6.6086e-05 | 2.226e-09 | -2.7987e-07 | 0.00040113 | 0.00040103 | 0.00040113 | 0.98229 | -0.125 | 0.9823 | -0.12494 | 0.14857
20 | -0.0002648 | -6.6086e-05 | 0.00026482 | 6.4282e-05 | 1.4314e-08 | -1.8031e-06 | 0.00040103 | 0.0004004 | 0.00040103 | 0.9823 | -0.12494 | 0.98236 | -0.12453 | 0.14853
21 | -0.0024481 | -0.00060814 | 0.0024482 | 0.00060802 | 1.0914e-07 | -1.1923e-07 | 0.0037063 | 0.0037063 | 0.0037063 | 0.98236 | -0.12453 | 0.9824 | -0.12421 | 1.3727
22 | 0.0021833 | 0.00054386 | -0.0021826 | -0.00054489 | 7.0451e-07 | -1.0363e-06 | 0.003306 | 0.0033064 | 0.0033064 | 0.98236 | -0.12453 | 0.98203 | -0.12689 | 1.2246
23 | -0.0024482 | -0.00060802 | 0.0024485 | 0.00060769 | 3.0352e-07 | -3.3168e-07 | 0.0037063 | 0.0037061 | 0.0037063 | 0.9824 | -0.12421 | 0.98253 | -0.12329 | 1.3727
24 | 0.0019588 | 0.0004888 | -0.0019586 | -0.00048905 | 1.342e-07 | -2.5739e-07 | 0.0029673 | 0.0029674 | 0.0029674 | 0.98203 | -0.12689 | 0.98196 | -0.12739 | 1.099
25 | 0.0050585 | 0.0012612 | -0.0050583 | -0.0012612 | 1.9787e-07 | 7.5412e-09 | 0.007656 | 0.007656 | 0.007656 | 0.98288 | -0.12076 | 0.98284 | -0.12104 | 2.8355
26 | -0.003839 | -0.00095618 | 0.0038402 | 0.00095592 | 1.1802e-06 | -2.5545e-07 | 0.005812 | 0.0058117 | 0.005812 | 0.98253 | -0.12329 | 0.98284 | -0.12104 | 2.1526
27 | 0.0010622 | 0.00026439 | -0.0010621 | -0.00026506 | 9.0611e-08 | -6.7456e-07 | 0.001609 | 0.0016092 | 0.0016092 | 0.98196 | -0.12739 | 0.98187 | -0.12801 | 0.596
28 | -0.00043283 | -0.00010848 | 0.00043284 | 0.00010782 | 1.4061e-08 | -6.571e-07 | 0.00065598 | 0.00065574 | 0.00065598 | 0.98182 | -0.12841 | 0.98185 | -0.12818 | 0.24296
29 | -0.00043284 | -0.00010782 | 0.00043285 | 0.00010747 | 7.4466e-09 | -3.4821e-07 | 0.00065574 | 0.00065562 | 0.00065574 | 0.98185 | -0.12818 | 0.98187 | -0.12805 | 0.24287
30 | -0.00043285 | -0.00010747 | 0.00043285 | 0.00010735 | 2.4966e-09 | -1.1678e-07 | 0.00065562 | 0.00065558 | 0.00065562 | 0.98187 | -0.12805 | 0.98187 | -0.12801 | 0.24282

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.050745 | 0.012544

## res_load
| p_mw | q_mvar
0 | 0.0015741 | 0.0003945
1 | 0.0023505 | 0.00058909
2 | 0.00075611 | 0.0001895
3 | 0.0013524 | 0.00033894
4 | 0.008241 | 0.0020654
5 | 0.0045068 | 0.0011295
6 | 0.00041775 | 0.0001047
7 | 0.0005057 | 0.00012674
8 | 0.00021797 | 5.4629e-05
9 | 0.00025256 | 6.3297e-05
10 | 0.00043003 | 0.00010778
11 | 0.00048888 | 0.00012253
12 | 0.0010215 | 0.00025601
13 | 0.0052098 | 0.0013057
14 | 0.0002648 | 6.6365e-05
15 | 0.00022383 | 5.6098e-05
16 | 0.0083203 | 0.0020853
17 | 0.00044141 | 0.00011063
18 | 0.0013905 | 0.00034849
19 | 0.00089643 | 0.00022467
20 | 0.00043283 | 0.00010848
21 | 0.00062926 | 0.00015771
22 | 0.0012181 | 0.00030529
23 | 0.0081275 | 0.0020369

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1