## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2087-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2087-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2087-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2087-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2087-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2087-3_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2087-3_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2087-3_0_3_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_2087-3_0_3_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_2087-3_0_3_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_2087-3_0_3_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_2087-3_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2087-3_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2087-3_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2087-3_0_3_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_2087-3_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2087-3_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2087-3_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2087-3_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2087-3_0_3_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_2087-3_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_2087-3_0_3_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_2087-3_0_3_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_2087-3_0_3_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_2087-3_0_3_node_24 | 0.4 | n |  | TRUE
25 | bus_MV_33_0_node_21 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2087-3_0_3_load_0 | 0 | 0.042162 | 0.010567 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2087-3_0_3_load_1 | 1 | 0.012583 | 0.0031536 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2087-3_0_3_load_3 | 3 | 0.0047067 | 0.0011796 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2087-3_0_3_load_4 | 4 | 0.038996 | 0.0097734 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2087-3_0_3_load_5 | 5 | 0.033946 | 0.0085077 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2087-3_0_3_load_6 | 6 | 0.0062395 | 0.0015638 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2087-3_0_3_load_21 | 8 | 0.0084924 | 0.0021284 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2087-3_0_3_load_9 | 11 | 0.0055994 | 0.0014034 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2087-3_0_3_load_10 | 12 | 0.011133 | 0.0027903 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2087-3_0_3_load_11 | 13 | 0.000377 | 9.4485e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2087-3_0_3_load_12 | 15 | 0.0013925 | 0.000349 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2087-3_0_3_load_14 | 17 | 0.0012414 | 0.00031112 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2087-3_0_3_load_18 | 19 | 0.0019833 | 0.00049705 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2087-3_0_3_load_16 | 20 | 0.00017315 | 4.3394e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2087-3_0_3_load_27 | 21 | 0.0014275 | 0.00035776 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2087-3_0_3_load_20 | 22 | 0.0012359 | 0.00030975 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2087-3_0_3_load_25 | 23 | 0.0027489 | 0.00068894 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2087-3_0_3_load_24 | 24 | 0.0087378 | 0.0021899 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2087-3_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0025659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2087-3_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.026368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2087-3_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.046274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2087-3_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.025665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2087-3_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.019614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_2087-3_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0024943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2087-3_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.015156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2087-3_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.060997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2087-3_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.041333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2087-3_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.014552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2087-3_0_3_line_10 | NAYY 4x150 SE | 9 | 24 | 0.096166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2087-3_0_3_line_11 | NAYY 4x150 SE | 10 | 14 | 0.032029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2087-3_0_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.023012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2087-3_0_3_line_13 | NAYY 4x150 SE | 11 | 12 | 0.048304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2087-3_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.0097706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2087-3_0_3_line_15 | NAYY 4x150 SE | 14 | 22 | 0.027372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2087-3_0_3_line_16 | NAYY 4x150 SE | 14 | 20 | 0.021498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2087-3_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.06591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2087-3_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.039226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2087-3_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.031226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2087-3_0_3_line_20 | NAYY 4x150 SE | 18 | 19 | 0.11918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2087-3_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.04002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2087-3_0_3_line_22 | NAYY 4x150 SE | 19 | 21 | 0.057448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2087-3_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.26564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2087-3_0_3_trafo_5 | 0.25 MVA 20/0.4 kV | 25 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2560755.7702 | 1169790.0821 | 2560756.449 | 1169792.5565
1 | 2560743.5895 | 1169767.0027 | 2560750.204 | 1169775.7306 | 2560753.0839 | 1169782.0039 | 2560755.5807 | 1169789.3914 | 2560755.7702 | 1169790.0821
2 | 2560756.449 | 1169792.5565 | 2560758.0891 | 1169798.5353 | 2560765.6772 | 1169837.8848
3 | 2560743.5895 | 1169767.0027 | 2560749.3199 | 1169757.5714 | 2560756.4592 | 1169744.8025
4 | 2560743.5895 | 1169767.0027 | 2560731.2675 | 1169782.263
5 | 2560766.1495 | 1169840.334 | 2560765.6772 | 1169837.8848
6 | 2560763.8557 | 1169731.5737 | 2560756.4592 | 1169744.8025
7 | 2560731.2675 | 1169782.263 | 2560728.3567 | 1169785.868 | 2560719.8477 | 1169796.2847 | 2560710.6014 | 1169806.2617 | 2560699.1111 | 1169817.0871 | 2560688.8086 | 1169825.8482
8 | 2560763.8557 | 1169731.5737 | 2560773.8338 | 1169707.129 | 2560777.7565 | 1169692.718
9 | 2560677.1052 | 1169834.4962 | 2560688.8086 | 1169825.8482
10 | 2560777.7565 | 1169692.718 | 2560800.732 | 1169701.739 | 2560830.2457 | 1169711.3287 | 2560842.0585 | 1169721.6791 | 2560856.8026 | 1169741.5513
11 | 2560677.1052 | 1169834.4962 | 2560662.1212 | 1169844.5887 | 2560650.0793 | 1169851.7826
12 | 2560677.1052 | 1169834.4962 | 2560667.726 | 1169813.4823
13 | 2560672.8065 | 1169764.0948 | 2560657.3707 | 1169781.865 | 2560656.235 | 1169783.6956 | 2560655.7763 | 1169784.9103 | 2560655.776 | 1169786.0332 | 2560656.1533 | 1169787.5537 | 2560663.7438 | 1169804.5601
14 | 2560667.726 | 1169813.4823 | 2560663.7438 | 1169804.5601
15 | 2560650.0793 | 1169851.7826 | 2560654.8082 | 1169857.6658 | 2560667.3358 | 1169873.0296
16 | 2560650.0793 | 1169851.7826 | 2560631.5062 | 1169862.6091
17 | 2560565.3229 | 1169881.6778 | 2560572.5443 | 1169876.8055 | 2560585.1352 | 1169870.5082 | 2560623.5516 | 1169854.0581 | 2560624.7512 | 1169853.4819
18 | 2560635.0442 | 1169822.6773 | 2560638.0797 | 1169846.7922 | 2560635.2137 | 1169848.4563 | 2560624.7512 | 1169853.4819
19 | 2560596.6204 | 1169882.2166 | 2560585.3742 | 1169882.4018 | 2560577.5922 | 1169882.3196 | 2560565.3229 | 1169881.6778
20 | 2560596.6204 | 1169882.2166 | 2560578.4788 | 1169894.9648 | 2560566.8649 | 1169905.5356 | 2560554.1527 | 1169921.2831 | 2560547.2564 | 1169934.8467 | 2560541.642 | 1169947.8571 | 2560538.5054 | 1169961.8629 | 2560535.0279 | 1169978.8325
21 | 2560596.6204 | 1169882.2166 | 2560623.9429 | 1169867.0179 | 2560631.5062 | 1169862.6091
22 | 2560535.0279 | 1169978.8325 | 2560477.8825 | 1169984.7189
23 | 2560477.8825 | 1169984.7189 | 2560468.7164 | 1170250.2012

## bus_geodata
| x | y | coords
0 | 2560755.7702 | 1169790.0821
1 | 2560756.449 | 1169792.5565
2 | 2560743.5895 | 1169767.0027
3 | 2560765.6772 | 1169837.8848
4 | 2560756.4592 | 1169744.8025
5 | 2560731.2675 | 1169782.263
6 | 2560766.1495 | 1169840.334
7 | 2560763.8557 | 1169731.5737
8 | 2560688.8086 | 1169825.8482
9 | 2560777.7565 | 1169692.718
10 | 2560677.1052 | 1169834.4962
11 | 2560672.8065 | 1169764.0948
12 | 2560663.7438 | 1169804.5601
13 | 2560667.726 | 1169813.4823
14 | 2560650.0793 | 1169851.7826
15 | 2560624.7512 | 1169853.4819
16 | 2560565.3229 | 1169881.6778
17 | 2560635.0442 | 1169822.6773
18 | 2560596.6204 | 1169882.2166
19 | 2560535.0279 | 1169978.8325
20 | 2560631.5062 | 1169862.6091
21 | 2560477.8825 | 1169984.7189
22 | 2560667.3358 | 1169873.0296
23 | 2560468.7164 | 1170250.2012
24 | 2560856.8026 | 1169741.5513
25 | 2560743.5895 | 1169767.0027

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99593 | -0.028509 | 0.042162 | 0.010567
1 | 0.99584 | -0.029117 | 0.012583 | 0.0031536
2 | 0.99841 | -0.011122 | 0 | 0
3 | 0.99512 | -0.03422 | 0.0047067 | 0.0011796
4 | 0.99666 | -0.023414 | 0.038996 | 0.0097734
5 | 1 | 0 | -0.15063 | -0.037618
6 | 0.99509 | -0.034376 | 0.0062395 | 0.0015638
7 | 0.99647 | -0.024747 | 0 | 0
8 | 0.99687 | -0.021914 | 0.0084924 | 0.0021284
9 | 0.99595 | -0.028383 | 0 | 0
10 | 0.9963 | -0.025919 | 0 | 0
11 | 0.99512 | -0.034254 | 0.0055994 | 0.0014034
12 | 0.99551 | -0.031528 | 0.011133 | 0.0027903
13 | 0.99574 | -0.029882 | 0.000377 | 9.4485e-05
14 | 0.99583 | -0.029228 | 0 | 0
15 | 0.99469 | -0.037338 | 0.0013925 | 0.000349
16 | 0.99494 | -0.035583 | 0 | 0
17 | 0.99462 | -0.03783 | 0.0012414 | 0.00031112
18 | 0.99505 | -0.03475 | 0 | 0
19 | 0.994 | -0.042202 | 0.0019833 | 0.00049705
20 | 0.99556 | -0.031181 | 0.00017315 | 4.3394e-05
21 | 0.99366 | -0.044643 | 0.0014275 | 0.00035776
22 | 0.99579 | -0.029568 | 0.0012359 | 0.00030975
23 | 0.99261 | -0.052066 | 0.0027489 | 0.00068894
24 | 0.99474 | -0.036853 | 0.0087378 | 0.0021899
25 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.023539 | 0.0059001 | -0.023537 | -0.0058994 | 1.9804e-06 | 7.2832e-07 | 0.03517 | 0.03517 | 0.03517 | 0.99593 | -0.028509 | 0.99584 | -0.029117 | 13.0259
1 | -0.065701 | -0.016467 | 0.065859 | 0.016527 | 0.00015855 | 6.0637e-05 | 0.098164 | 0.098164 | 0.098164 | 0.99593 | -0.028509 | 0.99841 | -0.011122 | 36.3569
2 | 0.010954 | 0.0027458 | -0.010946 | -0.0027434 | 7.7361e-06 | 2.3738e-06 | 0.016368 | 0.016368 | 0.016368 | 0.99584 | -0.029117 | 0.99512 | -0.03422 | 6.0623
3 | 0.047832 | 0.011999 | -0.04775 | -0.011968 | 8.1396e-05 | 3.0971e-05 | 0.071292 | 0.071292 | 0.071292 | 0.99841 | -0.011122 | 0.99666 | -0.023414 | 26.4044
4 | -0.11369 | -0.028526 | 0.11387 | 0.028593 | 0.00017572 | 6.7072e-05 | 0.16946 | 0.16946 | 0.16946 | 0.99841 | -0.011122 | 1 | 0 | 31.3806
5 | 0.0062396 | 0.0015638 | -0.0062395 | -0.0015638 | 1.3549e-07 | 1.9709e-08 | 0.0093302 | 0.0093302 | 0.0093302 | 0.99512 | -0.03422 | 0.99509 | -0.034376 | 3.4556
6 | 0.0087541 | 0.0021942 | -0.0087525 | -0.0021938 | 1.6156e-06 | 4.239e-07 | 0.01307 | 0.01307 | 0.01307 | 0.99666 | -0.023414 | 0.99647 | -0.024747 | 4.8408
7 | 0.035967 | 0.0090249 | -0.035858 | -0.0089838 | 0.00010904 | 4.1141e-05 | 0.053524 | 0.053524 | 0.053524 | 1 | 0 | 0.99687 | -0.021914 | 19.8237
8 | 0.0087525 | 0.0021938 | -0.0087481 | -0.0021926 | 4.406e-06 | 1.1565e-06 | 0.01307 | 0.01307 | 0.01307 | 0.99647 | -0.024747 | 0.99595 | -0.028383 | 4.8408
9 | 0.027366 | 0.0068554 | -0.027351 | -0.0068498 | 1.5151e-05 | 5.6377e-06 | 0.040848 | 0.040848 | 0.040848 | 0.99687 | -0.021914 | 0.9963 | -0.025919 | 15.1288
10 | 0.0087481 | 0.0021926 | -0.0087378 | -0.0021899 | 1.0252e-05 | 2.693e-06 | 0.01307 | 0.013071 | 0.013071 | 0.99595 | -0.028383 | 0.99474 | -0.036853 | 4.841
11 | 0.010226 | 0.0025568 | -0.010221 | -0.0025554 | 4.6604e-06 | 1.3756e-06 | 0.01527 | 0.01527 | 0.01527 | 0.9963 | -0.025919 | 0.99583 | -0.029228 | 5.6557
12 | 0.017125 | 0.004293 | -0.017116 | -0.0042897 | 9.3941e-06 | 3.3136e-06 | 0.025577 | 0.025578 | 0.025578 | 0.9963 | -0.025919 | 0.99574 | -0.029882 | 9.4732
13 | -0.0055994 | -0.0014034 | 0.0056016 | 0.0014035 | 2.113e-06 | 1.8493e-07 | 0.0083729 | 0.0083727 | 0.0083729 | 0.99512 | -0.034254 | 0.99551 | -0.031528 | 3.1011
14 | -0.016735 | -0.0041938 | 0.016739 | 0.0041952 | 3.8148e-06 | 1.3402e-06 | 0.025014 | 0.025014 | 0.025014 | 0.99551 | -0.031528 | 0.99574 | -0.029882 | 9.2645
15 | 0.001236 | 0.00030941 | -0.0012359 | -0.00030974 | 5.8252e-08 | -3.3369e-07 | 0.0018467 | 0.0018468 | 0.0018468 | 0.99583 | -0.029228 | 0.99579 | -0.029568 | 0.68401
16 | 0.008985 | 0.002246 | -0.0089826 | -0.0022454 | 2.4173e-06 | 6.5011e-07 | 0.013424 | 0.013424 | 0.013424 | 0.99583 | -0.029228 | 0.99556 | -0.031181 | 4.9718
17 | -0.002634 | -0.00065964 | 0.0026346 | 0.00065903 | 6.3846e-07 | -6.1019e-07 | 0.0039402 | 0.0039399 | 0.0039402 | 0.99469 | -0.037338 | 0.99494 | -0.035583 | 1.4593
18 | 0.0012415 | 0.00031064 | -0.0012414 | -0.00031112 | 8.4417e-08 | -4.7666e-07 | 0.001857 | 0.0018572 | 0.0018572 | 0.99469 | -0.037338 | 0.99462 | -0.03783 | 0.68785
19 | -0.0026346 | -0.00065903 | 0.0026349 | 0.00065874 | 3.0245e-07 | -2.8925e-07 | 0.0039399 | 0.0039397 | 0.0039399 | 0.99494 | -0.035583 | 0.99505 | -0.03475 | 1.4592
20 | 0.0061702 | 0.0015421 | -0.0061638 | -0.0015412 | 6.3296e-06 | 8.88e-07 | 0.0092254 | 0.009226 | 0.009226 | 0.99505 | -0.03475 | 0.994 | -0.042202 | 3.417
21 | -0.0088051 | -0.0022008 | 0.0088094 | 0.002202 | 4.3282e-06 | 1.1446e-06 | 0.013165 | 0.013165 | 0.013165 | 0.99505 | -0.03475 | 0.99556 | -0.031181 | 4.876
22 | 0.0041806 | 0.0010441 | -0.0041792 | -0.0010443 | 1.4035e-06 | -2.0459e-07 | 0.006257 | 0.0062573 | 0.0062573 | 0.994 | -0.042202 | 0.99366 | -0.044643 | 2.3175
23 | 0.0027517 | 0.00068658 | -0.0027489 | -0.00068894 | 2.814e-06 | -2.355e-06 | 0.0041197 | 0.0041209 | 0.0041209 | 0.99366 | -0.044643 | 0.99261 | -0.052066 | 1.5262

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18458 | 0.046126

## res_load
| p_mw | q_mvar
0 | 0.042162 | 0.010567
1 | 0.012583 | 0.0031536
2 | 0.0047067 | 0.0011796
3 | 0.038996 | 0.0097734
4 | 0.033946 | 0.0085077
5 | 0.0062395 | 0.0015638
6 | 0.0084924 | 0.0021284
7 | 0.0055994 | 0.0014034
8 | 0.011133 | 0.0027903
9 | 0.000377 | 9.4485e-05
10 | 0.0013925 | 0.000349
11 | 0.0012414 | 0.00031112
12 | 0.0019833 | 0.00049705
13 | 0.00017315 | 4.3394e-05
14 | 0.0014275 | 0.00035776
15 | 0.0012359 | 0.00030975
16 | 0.0027489 | 0.00068894
17 | 0.0087378 | 0.0021899

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1