## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2096-39_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2096-39_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2096-39_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2096-39_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2096-39_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2096-39_0_2_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_2096-39_0_2_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_2096-39_0_2_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_2096-39_0_2_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_2096-39_0_2_node_44 | 0.4 | n |  | TRUE
10 | bus_LV_2096-39_0_2_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_2096-39_0_2_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_2096-39_0_2_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2096-39_0_2_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2096-39_0_2_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2096-39_0_2_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2096-39_0_2_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2096-39_0_2_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2096-39_0_2_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2096-39_0_2_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_2096-39_0_2_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_2096-39_0_2_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_2096-39_0_2_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2096-39_0_2_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_2096-39_0_2_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2096-39_0_2_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2096-39_0_2_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_2096-39_0_2_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_2096-39_0_2_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2096-39_0_2_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2096-39_0_2_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_2096-39_0_2_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_2096-39_0_2_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2096-39_0_2_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_2096-39_0_2_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_2096-39_0_2_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_2096-39_0_2_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_2096-39_0_2_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_2096-39_0_2_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_2096-39_0_2_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_2096-39_0_2_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_2096-39_0_2_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_2096-39_0_2_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_2096-39_0_2_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_2096-39_0_2_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_2096-39_0_2_node_42 | 0.4 | n |  | TRUE
46 | bus_MV_33_0_node_7 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2096-39_0_2_load_0 | 0 | 0.0032295 | 0.0008094 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2096-39_0_2_load_1 | 1 | 0.0032831 | 0.00082283 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2096-39_0_2_load_2 | 2 | 0.0029073 | 0.00072863 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2096-39_0_2_load_3 | 3 | 0.00080861 | 0.00020266 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2096-39_0_2_load_43 | 6 | 0.0028835 | 0.00072268 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2096-39_0_2_load_36 | 7 | 0.0020944 | 0.0005249 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2096-39_0_2_load_44 | 9 | 0.0025194 | 0.00063143 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2096-39_0_2_load_35 | 10 | 0.0053679 | 0.0013453 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2096-39_0_2_load_5 | 11 | 0.0046709 | 0.0011706 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2096-39_0_2_load_6 | 12 | 0.0020024 | 0.00050185 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2096-39_0_2_load_9 | 15 | 0.003689 | 0.00092454 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2096-39_0_2_load_10 | 16 | 0.0027705 | 0.00069435 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2096-39_0_2_load_14 | 17 | 0.0019585 | 0.00049085 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2096-39_0_2_load_11 | 18 | 0.0024331 | 0.00060979 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2096-39_0_2_load_18 | 20 | 0.0030163 | 0.00075595 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2096-39_0_2_load_12 | 22 | 0.0022288 | 0.00055859 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2096-39_0_2_load_25 | 23 | 0.0060366 | 0.0015129 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2096-39_0_2_load_16 | 24 | 0.0031005 | 0.00077707 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2096-39_0_2_load_13 | 25 | 0.0064563 | 0.0016181 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2096-39_0_2_load_28 | 26 | 0.0031145 | 0.00078057 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2096-39_0_2_load_21 | 27 | 0.0040243 | 0.0010086 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2096-39_0_2_load_15 | 28 | 0.0026244 | 0.00065775 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2096-39_0_2_load_17 | 29 | 0.0024995 | 0.00062642 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2096-39_0_2_load_19 | 30 | 0.0053036 | 0.0013292 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2096-39_0_2_load_20 | 31 | 0.0031862 | 0.00079854 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2096-39_0_2_load_22 | 32 | 0.0017047 | 0.00042724 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2096-39_0_2_load_27 | 35 | 0.0058093 | 0.001456 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2096-39_0_2_load_30 | 36 | 0.0021443 | 0.00053742 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2096-39_0_2_load_32 | 37 | 0.0022564 | 0.0005655 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2096-39_0_2_load_40 | 39 | 0.002564 | 0.00064259 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2096-39_0_2_load_45 | 40 | 0.0060306 | 0.0015114 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2096-39_0_2_load_38 | 41 | 0.0011105 | 0.00027833 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2096-39_0_2_load_37 | 42 | 0.00077753 | 0.00019487 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2096-39_0_2_load_39 | 43 | 0.00075455 | 0.00018911 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2096-39_0_2_load_41 | 44 | 0.0010411 | 0.00026092 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2096-39_0_2_load_42 | 45 | 0.0042826 | 0.0010733 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2096-39_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.025438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2096-39_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.011651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2096-39_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.029358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2096-39_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0066759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2096-39_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.025454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2096-39_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.015321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2096-39_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.045921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2096-39_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.05837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2096-39_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.031751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2096-39_0_2_line_9 | NAYY 4x150 SE | 7 | 10 | 0.0088397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2096-39_0_2_line_10 | NAYY 4x150 SE | 8 | 38 | 0.01023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2096-39_0_2_line_11 | NAYY 4x150 SE | 8 | 39 | 0.0072227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2096-39_0_2_line_12 | NAYY 4x150 SE | 10 | 32 | 0.020206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2096-39_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.033986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2096-39_0_2_line_14 | NAYY 4x150 SE | 11 | 13 | 0.01622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2096-39_0_2_line_15 | NAYY 4x150 SE | 12 | 14 | 0.0059246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2096-39_0_2_line_16 | NAYY 4x150 SE | 13 | 15 | 0.049456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2096-39_0_2_line_17 | NAYY 4x150 SE | 13 | 16 | 0.0184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2096-39_0_2_line_18 | NAYY 4x150 SE | 14 | 17 | 0.0025944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2096-39_0_2_line_19 | NAYY 4x150 SE | 14 | 18 | 0.019432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2096-39_0_2_line_20 | NAYY 4x150 SE | 15 | 19 | 0.0011886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2096-39_0_2_line_21 | NAYY 4x150 SE | 16 | 20 | 0.0022899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2096-39_0_2_line_22 | NAYY 4x150 SE | 17 | 21 | 0.019276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2096-39_0_2_line_23 | NAYY 4x150 SE | 18 | 22 | 0.0027862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2096-39_0_2_line_24 | NAYY 4x150 SE | 19 | 23 | 0.018791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2096-39_0_2_line_25 | NAYY 4x150 SE | 20 | 24 | 0.017716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2096-39_0_2_line_26 | NAYY 4x150 SE | 21 | 26 | 0.015898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2096-39_0_2_line_27 | NAYY 4x150 SE | 21 | 27 | 0.019522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2096-39_0_2_line_28 | NAYY 4x150 SE | 22 | 25 | 0.019095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2096-39_0_2_line_29 | NAYY 4x150 SE | 23 | 34 | 0.0080807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2096-39_0_2_line_30 | NAYY 4x150 SE | 24 | 28 | 0.015527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2096-39_0_2_line_31 | NAYY 4x150 SE | 26 | 33 | 0.023706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2096-39_0_2_line_32 | NAYY 4x150 SE | 27 | 30 | 0.032382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2096-39_0_2_line_33 | NAYY 4x150 SE | 28 | 29 | 0.006494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2096-39_0_2_line_34 | NAYY 4x150 SE | 30 | 31 | 0.014619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2096-39_0_2_line_35 | NAYY 4x150 SE | 31 | 32 | 0.01518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2096-39_0_2_line_36 | NAYY 4x150 SE | 33 | 36 | 0.055713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2096-39_0_2_line_37 | NAYY 4x150 SE | 34 | 35 | 0.031088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2096-39_0_2_line_38 | NAYY 4x150 SE | 36 | 37 | 0.035252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2096-39_0_2_line_39 | NAYY 4x150 SE | 38 | 40 | 0.074964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2096-39_0_2_line_40 | NAYY 4x150 SE | 39 | 41 | 0.029413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2096-39_0_2_line_41 | NAYY 4x150 SE | 41 | 42 | 0.025681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2096-39_0_2_line_42 | NAYY 4x150 SE | 42 | 43 | 0.032823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2096-39_0_2_line_43 | NAYY 4x150 SE | 43 | 44 | 0.031566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2096-39_0_2_line_44 | NAYY 4x150 SE | 44 | 45 | 0.045693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2096-39_0_2_trafo_20 | 0.25 MVA 20/0.4 kV | 46 | 31 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2559284.5451 | 1171870.8555 | 2559293.4498 | 1171860.2993 | 2559300.1813 | 1171850.8183
1 | 2559284.5451 | 1171870.8555 | 2559277.0325 | 1171879.7614
2 | 2559317.1773 | 1171826.8799 | 2559300.1813 | 1171850.8183
3 | 2559272.728 | 1171884.8642 | 2559277.0325 | 1171879.7614
4 | 2559331.8765 | 1171806.0987 | 2559322.0656 | 1171819.9949 | 2559317.1773 | 1171826.8799
5 | 2559272.728 | 1171884.8642 | 2559262.0606 | 1171895.861
6 | 2559272.728 | 1171884.8642 | 2559243.7022 | 1171855.8687 | 2559240.6719 | 1171852.026
7 | 2559331.8765 | 1171806.0987 | 2559358.1172 | 1171807.9438 | 2559368.3165 | 1171807.3076 | 2559378.5158 | 1171806.6714 | 2559380.0013 | 1171809.1626 | 2559382.2246 | 1171811.0374 | 2559384.9318 | 1171812.0974 | 2559387.8393 | 1171812.2333
8 | 2559239.9533 | 1171918.6511 | 2559262.0606 | 1171895.861
9 | 2559240.6719 | 1171852.026 | 2559235.1981 | 1171845.0849
10 | 2559387.8393 | 1171812.2333 | 2559390.313 | 1171811.5606 | 2559392.4915 | 1171810.2118 | 2559394.1841 | 1171808.2882 | 2559395.2622 | 1171805.9686
11 | 2559387.8393 | 1171812.2333 | 2559386.5806 | 1171817.2334 | 2559385.4202 | 1171818.9435
12 | 2559222.6859 | 1171829.2186 | 2559235.1981 | 1171845.0849
13 | 2559129.06 | 1171809.3923 | 2559152.7307 | 1171785.0054
14 | 2559117.7631 | 1171821.0309 | 2559129.06 | 1171809.3923
15 | 2559156.8571 | 1171780.7542 | 2559152.7307 | 1171785.0054
16 | 2559117.7631 | 1171821.0309 | 2559147.9137 | 1171855.5878 | 2559150.922 | 1171857.5557
17 | 2559117.7631 | 1171821.0309 | 2559105.1825 | 1171807.6034
18 | 2559156.8571 | 1171780.7542 | 2559158.6646 | 1171778.8929
19 | 2559156.8571 | 1171780.7542 | 2559142.7988 | 1171767.3383
20 | 2559151.9166 | 1171858.2063 | 2559150.922 | 1171857.5557
21 | 2559105.1825 | 1171807.6034 | 2559103.6169 | 1171805.9324
22 | 2559172.0939 | 1171765.0643 | 2559158.6646 | 1171778.8929
23 | 2559140.7832 | 1171765.4147 | 2559142.7988 | 1171767.3383
24 | 2559151.9166 | 1171858.2063 | 2559157.8096 | 1171862.057 | 2559165.1646 | 1171871.2226
25 | 2559091.5044 | 1171793.0043 | 2559103.6169 | 1171805.9324
26 | 2559172.0939 | 1171765.0643 | 2559182.3654 | 1171752.93
27 | 2559172.0939 | 1171765.0643 | 2559184.1822 | 1171780.3931
28 | 2559126.9692 | 1171752.232 | 2559140.7832 | 1171765.4147
29 | 2559170.2221 | 1171877.525 | 2559165.1646 | 1171871.2226
30 | 2559091.5044 | 1171793.0043 | 2559080.8883 | 1171781.6734
31 | 2559200.7432 | 1171738.7108 | 2559194.2434 | 1171741.223 | 2559187.4365 | 1171746.9391 | 2559182.3654 | 1171752.93
32 | 2559184.1822 | 1171780.3931 | 2559204.2336 | 1171805.8197
33 | 2559076.4482 | 1171776.9344 | 2559080.8883 | 1171781.6734
34 | 2559213.2861 | 1171817.2989 | 2559204.2336 | 1171805.8197
35 | 2559222.6859 | 1171829.2186 | 2559213.2861 | 1171817.2989
36 | 2559200.7432 | 1171738.7108 | 2559245.5748 | 1171771.7882
37 | 2559170.2221 | 1171877.525 | 2559170.2778 | 1171885.6955 | 2559185.7293 | 1171902.6208
38 | 2559245.5748 | 1171771.7882 | 2559251.2201 | 1171775.9533 | 2559276.5756 | 1171788.3791
39 | 2559395.2622 | 1171805.9686 | 2559442.6184 | 1171791.5624 | 2559466.5014 | 1171782.7279
40 | 2559368.9055 | 1171843.2821 | 2559385.4202 | 1171818.9435
41 | 2559354.4864 | 1171864.5325 | 2559368.9055 | 1171843.2821
42 | 2559354.4864 | 1171864.5325 | 2559341.4147 | 1171883.797 | 2559334.755 | 1171890.6317
43 | 2559312.7261 | 1171913.2396 | 2559334.755 | 1171890.6317
44 | 2559280.838 | 1171945.9658 | 2559312.7261 | 1171913.2396

## bus_geodata
| x | y | coords
0 | 2559284.5451 | 1171870.8555
1 | 2559300.1813 | 1171850.8183
2 | 2559277.0325 | 1171879.7614
3 | 2559317.1773 | 1171826.8799
4 | 2559272.728 | 1171884.8642
5 | 2559331.8765 | 1171806.0987
6 | 2559262.0606 | 1171895.861
7 | 2559240.6719 | 1171852.026
8 | 2559387.8393 | 1171812.2333
9 | 2559239.9533 | 1171918.6511
10 | 2559235.1981 | 1171845.0849
11 | 2559129.06 | 1171809.3923
12 | 2559152.7307 | 1171785.0054
13 | 2559117.7631 | 1171821.0309
14 | 2559156.8571 | 1171780.7542
15 | 2559150.922 | 1171857.5557
16 | 2559105.1825 | 1171807.6034
17 | 2559158.6646 | 1171778.8929
18 | 2559142.7988 | 1171767.3383
19 | 2559151.9166 | 1171858.2063
20 | 2559103.6169 | 1171805.9324
21 | 2559172.0939 | 1171765.0643
22 | 2559140.7832 | 1171765.4147
23 | 2559165.1646 | 1171871.2226
24 | 2559091.5044 | 1171793.0043
25 | 2559126.9692 | 1171752.232
26 | 2559182.3654 | 1171752.93
27 | 2559184.1822 | 1171780.3931
28 | 2559080.8883 | 1171781.6734
29 | 2559076.4482 | 1171776.9344
30 | 2559204.2336 | 1171805.8197
31 | 2559213.2861 | 1171817.2989
32 | 2559222.6859 | 1171829.2186
33 | 2559200.7432 | 1171738.7108
34 | 2559170.2221 | 1171877.525
35 | 2559185.7293 | 1171902.6208
36 | 2559245.5748 | 1171771.7882
37 | 2559276.5756 | 1171788.3791
38 | 2559395.2622 | 1171805.9686
39 | 2559385.4202 | 1171818.9435
40 | 2559466.5014 | 1171782.7279
41 | 2559368.9055 | 1171843.2821
42 | 2559354.4864 | 1171864.5325
43 | 2559334.755 | 1171890.6317
44 | 2559312.7261 | 1171913.2396
45 | 2559280.838 | 1171945.9658
46 | 2559172.0939 | 1171765.0643

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99473 | -0.036849 | 0.0032295 | 0.0008094
1 | 0.99398 | -0.042162 | 0.0032831 | 0.00082283
2 | 0.99513 | -0.034039 | 0.0029073 | 0.00072863
3 | 0.99325 | -0.047327 | 0.00080861 | 0.00020266
4 | 0.99539 | -0.032234 | 0 | 0
5 | 0.99264 | -0.051602 | 0 | 0
6 | 0.99527 | -0.033069 | 0.0028835 | 0.00072268
7 | 0.99751 | -0.017354 | 0.0020944 | 0.0005249
8 | 0.99125 | -0.061423 | 0 | 0
9 | 0.99516 | -0.033875 | 0.0025194 | 0.00063143
10 | 0.99795 | -0.014311 | 0.0053679 | 0.0013453
11 | 0.99065 | -0.065491 | 0.0046709 | 0.0011706
12 | 0.99233 | -0.053678 | 0.0020024 | 0.00050185
13 | 0.98996 | -0.070371 | 0 | 0
14 | 0.99264 | -0.051503 | 0 | 0
15 | 0.98885 | -0.078208 | 0.003689 | 0.00092454
16 | 0.98959 | -0.072998 | 0.0027705 | 0.00069435
17 | 0.99281 | -0.050259 | 0.0019585 | 0.00049085
18 | 0.99233 | -0.053693 | 0.0024331 | 0.00060979
19 | 0.98883 | -0.078352 | 0 | 0
20 | 0.98955 | -0.073261 | 0.0030163 | 0.00075595
21 | 0.99418 | -0.040645 | 0 | 0
22 | 0.99229 | -0.053938 | 0.0022288 | 0.00055859
23 | 0.98851 | -0.080626 | 0.0060366 | 0.0015129
24 | 0.98934 | -0.074747 | 0.0031005 | 0.00077707
25 | 0.99211 | -0.055188 | 0.0064563 | 0.0016181
26 | 0.99401 | -0.041853 | 0.0031145 | 0.00078057
27 | 0.99578 | -0.029456 | 0.0040243 | 0.0010086
28 | 0.98923 | -0.075558 | 0.0026244 | 0.00065775
29 | 0.9892 | -0.075724 | 0.0024995 | 0.00062642
30 | 0.99861 | -0.0096702 | 0.0053036 | 0.0013292
31 | 1 | 0 | -0.1091 | -0.027236
32 | 0.9991 | -0.0062796 | 0.0017047 | 0.00042724
33 | 0.99386 | -0.04291 | 0 | 0
34 | 0.98844 | -0.081105 | 0 | 0
35 | 0.98818 | -0.082951 | 0.0058093 | 0.001456
36 | 0.99351 | -0.045391 | 0.0021443 | 0.00053742
37 | 0.99339 | -0.046196 | 0.0022564 | 0.0005655
38 | 0.99116 | -0.062051 | 0 | 0
39 | 0.99114 | -0.062197 | 0.002564 | 0.00064259
40 | 0.99051 | -0.066649 | 0.0060306 | 0.0015114
41 | 0.9908 | -0.064583 | 0.0011105 | 0.00027833
42 | 0.99055 | -0.066376 | 0.00077753 | 0.00019487
43 | 0.99026 | -0.068409 | 0.00075455 | 0.00018911
44 | 0.99002 | -0.070122 | 0.0010411 | 0.00026092
45 | 0.98974 | -0.072116 | 0.0042826 | 0.0010733
46 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.020727 | 0.0051994 | -0.020712 | -0.0051939 | 1.5261e-05 | 5.5396e-06 | 0.031007 | 0.031007 | 0.031007 | 0.99473 | -0.036849 | 0.99398 | -0.042162 | 11.484
1 | -0.023956 | -0.0060088 | 0.023966 | 0.0060123 | 9.3377e-06 | 3.4401e-06 | 0.035838 | 0.035838 | 0.035838 | 0.99473 | -0.036849 | 0.99513 | -0.034039 | 13.2732
2 | 0.017428 | 0.0043711 | -0.017416 | -0.0043666 | 1.2472e-05 | 4.4166e-06 | 0.026092 | 0.026092 | 0.026092 | 0.99398 | -0.042162 | 0.99325 | -0.047327 | 9.6637
3 | -0.026873 | -0.0067409 | 0.02688 | 0.0067434 | 6.727e-06 | 2.5006e-06 | 0.040185 | 0.040185 | 0.040185 | 0.99513 | -0.034039 | 0.99539 | -0.032234 | 14.8833
4 | 0.016607 | 0.004164 | -0.016597 | -0.0041605 | 9.8327e-06 | 3.4525e-06 | 0.024881 | 0.024881 | 0.024881 | 0.99325 | -0.047327 | 0.99264 | -0.051602 | 9.2151
5 | 0.0054039 | 0.0013539 | -0.0054033 | -0.0013538 | 6.2386e-07 | 4.0822e-08 | 0.0080781 | 0.0080782 | 0.0080782 | 0.99539 | -0.032234 | 0.99527 | -0.033069 | 2.9919
6 | -0.032284 | -0.0080973 | 0.03235 | 0.0081223 | 6.6746e-05 | 2.5073e-05 | 0.048263 | 0.048263 | 0.048263 | 0.99539 | -0.032234 | 0.99751 | -0.017354 | 17.8752
7 | 0.016597 | 0.0041605 | -0.016575 | -0.0041526 | 2.2548e-05 | 7.9188e-06 | 0.024881 | 0.024881 | 0.024881 | 0.99264 | -0.051602 | 0.99125 | -0.061423 | 9.2152
8 | 0.0025197 | 0.00063113 | -0.0025194 | -0.00063143 | 2.8117e-07 | -3.0443e-07 | 0.0037671 | 0.0037672 | 0.0037672 | 0.99527 | -0.033069 | 0.99516 | -0.033875 | 1.3953
9 | -0.034445 | -0.0086472 | 0.034459 | 0.0086527 | 1.4566e-05 | 5.4867e-06 | 0.051387 | 0.051387 | 0.051387 | 0.99751 | -0.017354 | 0.99795 | -0.014311 | 19.0322
10 | 0.006035 | 0.001512 | -0.0060344 | -0.0015119 | 5.239e-07 | 6.9639e-08 | 0.0090592 | 0.0090593 | 0.0090593 | 0.99125 | -0.061423 | 0.99116 | -0.062051 | 3.3553
11 | 0.01054 | 0.0026406 | -0.010539 | -0.0026403 | 1.1282e-06 | 3.4084e-07 | 0.015822 | 0.015822 | 0.015822 | 0.99125 | -0.061423 | 0.99114 | -0.062197 | 5.8599
12 | -0.039827 | -0.009998 | 0.039872 | 0.010015 | 4.4475e-05 | 1.6841e-05 | 0.059391 | 0.059391 | 0.059391 | 0.99795 | -0.014311 | 0.9991 | -0.0062796 | 21.9967
13 | -0.034268 | -0.0085926 | 0.034324 | 0.0086138 | 5.6188e-05 | 2.1172e-05 | 0.051473 | 0.051473 | 0.051473 | 0.99065 | -0.065491 | 0.99233 | -0.053678 | 19.0642
14 | 0.029597 | 0.007422 | -0.029577 | -0.0074145 | 2.0004e-05 | 7.4852e-06 | 0.044457 | 0.044457 | 0.044457 | 0.99065 | -0.065491 | 0.98996 | -0.070371 | 16.4657
15 | -0.036326 | -0.0091156 | 0.036337 | 0.0091198 | 1.0971e-05 | 4.1431e-06 | 0.054476 | 0.054476 | 0.054476 | 0.99233 | -0.053678 | 0.99264 | -0.051503 | 20.1763
16 | 0.015558 | 0.0039007 | -0.015541 | -0.0038949 | 1.6877e-05 | 5.856e-06 | 0.023385 | 0.023386 | 0.023386 | 0.98996 | -0.070371 | 0.98885 | -0.078208 | 8.6613
17 | 0.014019 | 0.0035138 | -0.014014 | -0.003512 | 5.0983e-06 | 1.7244e-06 | 0.021072 | 0.021072 | 0.021072 | 0.98996 | -0.070371 | 0.98959 | -0.072998 | 7.8045
18 | -0.04746 | -0.011908 | 0.047468 | 0.011911 | 8.1955e-06 | 3.1186e-06 | 0.07115 | 0.07115 | 0.07115 | 0.99264 | -0.051503 | 0.99281 | -0.050259 | 26.3518
19 | 0.011123 | 0.0027878 | -0.01112 | -0.0027867 | 3.3713e-06 | 1.0455e-06 | 0.016674 | 0.016674 | 0.016674 | 0.99264 | -0.051503 | 0.99233 | -0.053693 | 6.1756
20 | 0.011852 | 0.0029703 | -0.011852 | -0.0029703 | 2.359e-07 | 7.5482e-08 | 0.017834 | 0.017834 | 0.017834 | 0.98885 | -0.078208 | 0.98883 | -0.078352 | 6.6053
21 | 0.011243 | 0.0028177 | -0.011243 | -0.0028176 | 4.0841e-07 | 1.2766e-07 | 0.016906 | 0.016906 | 0.016906 | 0.98959 | -0.072998 | 0.98955 | -0.073261 | 6.2616
22 | -0.049427 | -0.012402 | 0.049493 | 0.012427 | 6.602e-05 | 2.5143e-05 | 0.074085 | 0.074085 | 0.074085 | 0.99281 | -0.050259 | 0.99418 | -0.040645 | 27.439
23 | 0.0086865 | 0.0021769 | -0.0086862 | -0.0021769 | 2.9498e-07 | 7.7461e-08 | 0.013026 | 0.013026 | 0.013026 | 0.99233 | -0.053693 | 0.99229 | -0.053938 | 4.8243
24 | 0.011852 | 0.0029703 | -0.011848 | -0.0029691 | 3.7296e-06 | 1.1935e-06 | 0.017834 | 0.017834 | 0.017834 | 0.98883 | -0.078352 | 0.98851 | -0.080626 | 6.6054
25 | 0.0082268 | 0.0020616 | -0.0082251 | -0.0020612 | 1.6918e-06 | 4.2314e-07 | 0.012371 | 0.012371 | 0.012371 | 0.98955 | -0.073261 | 0.98934 | -0.074747 | 4.5818
26 | 0.0075189 | 0.0018832 | -0.0075176 | -0.0018829 | 1.2563e-06 | 2.7707e-07 | 0.011253 | 0.011253 | 0.011253 | 0.99418 | -0.040645 | 0.99401 | -0.041853 | 4.1679
27 | -0.057012 | -0.01431 | 0.0571 | 0.014344 | 8.8714e-05 | 3.3867e-05 | 0.085338 | 0.085338 | 0.085338 | 0.99418 | -0.040645 | 0.99578 | -0.029456 | 31.6068
28 | 0.0064574 | 0.0016183 | -0.0064563 | -0.0016181 | 1.1173e-06 | 1.831e-07 | 0.0096834 | 0.0096834 | 0.0096834 | 0.99229 | -0.053938 | 0.99211 | -0.055188 | 3.5865
29 | 0.0058112 | 0.0014562 | -0.0058108 | -0.0014561 | 3.8584e-07 | 4.4817e-08 | 0.0087476 | 0.0087476 | 0.0087476 | 0.98851 | -0.080626 | 0.98844 | -0.081105 | 3.2399
30 | 0.0051245 | 0.0012841 | -0.005124 | -0.0012841 | 5.7557e-07 | 2.2012e-08 | 0.0077075 | 0.0077075 | 0.0077075 | 0.98934 | -0.074747 | 0.98923 | -0.075558 | 2.8546
31 | 0.0044031 | 0.0011024 | -0.0044024 | -0.0011024 | 6.4261e-07 | -6.0088e-08 | 0.0065909 | 0.0065911 | 0.0065911 | 0.99401 | -0.041853 | 0.99386 | -0.04291 | 2.4411
32 | -0.061125 | -0.015352 | 0.061293 | 0.015417 | 0.00016862 | 6.4433e-05 | 0.091352 | 0.091352 | 0.091352 | 0.99578 | -0.029456 | 0.99861 | -0.0096702 | 33.834
33 | 0.0024995 | 0.00062636 | -0.0024995 | -0.00062642 | 5.7283e-08 | -6.1337e-08 | 0.0037598 | 0.0037598 | 0.0037598 | 0.98923 | -0.075558 | 0.9892 | -0.075724 | 1.3925
34 | -0.066597 | -0.016746 | 0.066687 | 0.01678 | 8.9869e-05 | 3.4373e-05 | 0.099255 | 0.099254 | 0.099255 | 0.99861 | -0.0096702 | 1 | 0 | 36.7609
35 | 0.041613 | 0.010456 | -0.041576 | -0.010442 | 3.6329e-05 | 1.3774e-05 | 0.06193 | 0.06193 | 0.06193 | 1 | 0 | 0.9991 | -0.0062796 | 22.937
36 | 0.0044024 | 0.0011024 | -0.0044009 | -0.0011026 | 1.5103e-06 | -1.4082e-07 | 0.0065911 | 0.0065913 | 0.0065913 | 0.99386 | -0.04291 | 0.99351 | -0.045391 | 2.4412
37 | 0.0058108 | 0.0014561 | -0.0058093 | -0.0014559 | 1.4845e-06 | 1.7256e-07 | 0.0087476 | 0.0087477 | 0.0087477 | 0.98844 | -0.081105 | 0.98818 | -0.082951 | 3.2399
38 | 0.0022566 | 0.00056513 | -0.0022564 | -0.00056549 | 2.5127e-07 | -3.598e-07 | 0.0033797 | 0.0033798 | 0.0033798 | 0.99351 | -0.045391 | 0.99339 | -0.046196 | 1.2518
39 | 0.0060344 | 0.0015119 | -0.0060306 | -0.0015114 | 3.8392e-06 | 5.1109e-07 | 0.0090593 | 0.0090596 | 0.0090596 | 0.99116 | -0.062051 | 0.99051 | -0.066649 | 3.3554
40 | 0.0079748 | 0.0019977 | -0.0079722 | -0.0019971 | 2.6308e-06 | 6.3291e-07 | 0.011972 | 0.011973 | 0.011973 | 0.99114 | -0.062197 | 0.9908 | -0.064583 | 4.4343
41 | 0.0068616 | 0.0017187 | -0.0068599 | -0.0017184 | 1.7016e-06 | 3.2382e-07 | 0.010305 | 0.010305 | 0.010305 | 0.9908 | -0.064583 | 0.99055 | -0.066376 | 3.8166
42 | 0.0060824 | 0.0015235 | -0.0060807 | -0.0015233 | 1.7099e-06 | 2.3525e-07 | 0.0091368 | 0.0091369 | 0.0091369 | 0.99055 | -0.066376 | 0.99026 | -0.068409 | 3.3841
43 | 0.0053262 | 0.0013342 | -0.0053249 | -0.0013341 | 1.2616e-06 | 7.9243e-08 | 0.0080031 | 0.0080033 | 0.0080033 | 0.99026 | -0.068409 | 0.99002 | -0.070122 | 2.9642
44 | 0.0042838 | 0.0010732 | -0.0042826 | -0.0010733 | 1.182e-06 | -1.3277e-07 | 0.0064385 | 0.0064387 | 0.0064387 | 0.99002 | -0.070122 | 0.98974 | -0.072116 | 2.3847

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11229 | 0.028035

## res_load
| p_mw | q_mvar
0 | 0.0032295 | 0.0008094
1 | 0.0032831 | 0.00082283
2 | 0.0029073 | 0.00072863
3 | 0.00080861 | 0.00020266
4 | 0.0028835 | 0.00072268
5 | 0.0020944 | 0.0005249
6 | 0.0025194 | 0.00063143
7 | 0.0053679 | 0.0013453
8 | 0.0046709 | 0.0011706
9 | 0.0020024 | 0.00050185
10 | 0.003689 | 0.00092454
11 | 0.0027705 | 0.00069435
12 | 0.0019585 | 0.00049085
13 | 0.0024331 | 0.00060979
14 | 0.0030163 | 0.00075595
15 | 0.0022288 | 0.00055859
16 | 0.0060366 | 0.0015129
17 | 0.0031005 | 0.00077707
18 | 0.0064563 | 0.0016181
19 | 0.0031145 | 0.00078057
20 | 0.0040243 | 0.0010086
21 | 0.0026244 | 0.00065775
22 | 0.0024995 | 0.00062642
23 | 0.0053036 | 0.0013292
24 | 0.0031862 | 0.00079854
25 | 0.0017047 | 0.00042724
26 | 0.0058093 | 0.001456
27 | 0.0021443 | 0.00053742
28 | 0.0022564 | 0.0005655
29 | 0.002564 | 0.00064259
30 | 0.0060306 | 0.0015114
31 | 0.0011105 | 0.00027833
32 | 0.00077753 | 0.00019487
33 | 0.00075455 | 0.00018911
34 | 0.0010411 | 0.00026092
35 | 0.0042826 | 0.0010733

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1