## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2096-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2096-4_0_4_node_11 | 0.4 | n |  | TRUE
2 | bus_LV_2096-4_0_4_node_14 | 0.4 | n |  | TRUE
3 | bus_LV_2096-4_0_4_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_2096-4_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2096-4_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2096-4_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2096-4_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2096-4_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2096-4_0_4_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_2096-4_0_4_node_44 | 0.4 | n |  | TRUE
11 | bus_LV_2096-4_0_4_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_2096-4_0_4_node_27 | 0.4 | n |  | TRUE
13 | bus_LV_2096-4_0_4_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_2096-4_0_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_2096-4_0_4_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_2096-4_0_4_node_2 | 0.4 | n |  | TRUE
17 | bus_LV_2096-4_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2096-4_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2096-4_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2096-4_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_2096-4_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_2096-4_0_4_node_47 | 0.4 | n |  | TRUE
23 | bus_LV_2096-4_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2096-4_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2096-4_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_2096-4_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_2096-4_0_4_node_40 | 0.4 | n |  | TRUE
28 | bus_LV_2096-4_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2096-4_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2096-4_0_4_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_2096-4_0_4_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_2096-4_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_2096-4_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2096-4_0_4_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_2096-4_0_4_node_42 | 0.4 | n |  | TRUE
36 | bus_LV_2096-4_0_4_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_2096-4_0_4_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_2096-4_0_4_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_2096-4_0_4_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_2096-4_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_2096-4_0_4_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_2096-4_0_4_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_2096-4_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_MV_33_0_node_202 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2096-4_0_4_load_0 | 0 | 0.023544 | 0.0059006 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2096-4_0_4_load_14 | 2 | 0.0017464 | 0.00043768 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2096-4_0_4_load_3 | 4 | 0.0016859 | 0.00042253 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2096-4_0_4_load_4 | 5 | 0.0039273 | 0.00098427 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2096-4_0_4_load_7 | 7 | 0.00081499 | 0.00020426 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2096-4_0_4_load_8 | 8 | 0.0070677 | 0.0017713 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2096-4_0_4_load_36 | 9 | 0.0029286 | 0.00073398 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2096-4_0_4_load_44 | 10 | 0.011799 | 0.002957 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2096-4_0_4_load_26 | 11 | 0.0004575 | 0.00011466 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2096-4_0_4_load_27 | 12 | 0.0012567 | 0.00031496 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2096-4_0_4_load_28 | 13 | 0.0010361 | 0.00025966 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2096-4_0_4_load_29 | 14 | 0.0013552 | 0.00033965 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2096-4_0_4_load_30 | 15 | 0.00077642 | 0.00019459 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2096-4_0_4_load_2 | 16 | 0.0040282 | 0.0010096 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2096-4_0_4_load_15 | 17 | 0.0017583 | 0.00044066 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2096-4_0_4_load_9 | 18 | 0.0042857 | 0.0010741 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2096-4_0_4_load_47 | 22 | 0.002931 | 0.00073459 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2096-4_0_4_load_21 | 23 | 0.0091282 | 0.0022877 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2096-4_0_4_load_18 | 24 | 0.0026905 | 0.00067431 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2096-4_0_4_load_22 | 26 | 0.004733 | 0.0011862 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2096-4_0_4_load_40 | 27 | 0.0061 | 0.0015288 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2096-4_0_4_load_16 | 28 | 0.0017434 | 0.00043694 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2096-4_0_4_load_31 | 30 | 0.00090364 | 0.00022647 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2096-4_0_4_load_32 | 31 | 0.0014666 | 0.00036757 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2096-4_0_4_load_25 | 33 | 0.003958 | 0.00099198 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2096-4_0_4_load_23 | 34 | 0.022514 | 0.0056426 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2096-4_0_4_load_42 | 35 | 0.020181 | 0.0050578 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2096-4_0_4_load_33 | 36 | 0.0011186 | 0.00028036 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2096-4_0_4_load_35 | 38 | 0.00082678 | 0.00020721 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2096-4_0_4_load_45 | 39 | 0.00021863 | 5.4795e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2096-4_0_4_load_41 | 40 | 0.00063112 | 0.00015817 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2096-4_0_4_load_37 | 41 | 0.026097 | 0.0065405 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2096-4_0_4_load_38 | 42 | 0.031376 | 0.0078636 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2096-4_0_4_load_39 | 43 | 0.002111 | 0.00052906 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2096-4_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.057417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2096-4_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.04537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2096-4_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.041228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2096-4_0_4_line_3 | NAYY 4x150 SE | 2 | 17 | 0.02421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2096-4_0_4_line_4 | NAYY 4x150 SE | 3 | 19 | 0.00468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2096-4_0_4_line_5 | NAYY 4x150 SE | 4 | 5 | 0.033312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2096-4_0_4_line_6 | NAYY 4x150 SE | 4 | 6 | 0.022151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2096-4_0_4_line_7 | NAYY 4x150 SE | 6 | 7 | 0.042843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2096-4_0_4_line_8 | NAYY 4x150 SE | 6 | 8 | 0.00084823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2096-4_0_4_line_9 | NAYY 4x150 SE | 7 | 9 | 0.041893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2096-4_0_4_line_10 | NAYY 4x150 SE | 8 | 10 | 0.071226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2096-4_0_4_line_11 | NAYY 4x150 SE | 9 | 14 | 0.048773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2096-4_0_4_line_12 | NAYY 4x150 SE | 10 | 16 | 0.07391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2096-4_0_4_line_13 | NAYY 4x150 SE | 11 | 12 | 0.010771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2096-4_0_4_line_14 | NAYY 4x150 SE | 11 | 13 | 0.018921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2096-4_0_4_line_15 | NAYY 4x150 SE | 12 | 14 | 0.031431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2096-4_0_4_line_16 | NAYY 4x150 SE | 13 | 15 | 0.002033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2096-4_0_4_line_17 | NAYY 4x150 SE | 16 | 17 | 0.038967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2096-4_0_4_line_18 | NAYY 4x150 SE | 18 | 19 | 0.035839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2096-4_0_4_line_19 | NAYY 4x150 SE | 19 | 20 | 0.03457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_2096-4_0_4_line_20 | NAYY 4x150 SE | 20 | 21 | 0.06447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2096-4_0_4_line_21 | NAYY 4x150 SE | 20 | 22 | 0.01269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2096-4_0_4_line_22 | NAYY 4x150 SE | 21 | 23 | 0.029131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2096-4_0_4_line_23 | NAYY 4x150 SE | 21 | 24 | 0.010132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2096-4_0_4_line_24 | NAYY 4x150 SE | 22 | 27 | 0.037966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2096-4_0_4_line_25 | NAYY 4x150 SE | 23 | 32 | 0.026136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2096-4_0_4_line_26 | NAYY 4x150 SE | 24 | 25 | 0.0098145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2096-4_0_4_line_27 | NAYY 4x150 SE | 25 | 26 | 0.032277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2096-4_0_4_line_28 | NAYY 4x150 SE | 27 | 42 | 0.02518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2096-4_0_4_line_29 | NAYY 4x150 SE | 28 | 29 | 0.072306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2096-4_0_4_line_30 | NAYY 4x150 SE | 29 | 30 | 0.057393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2096-4_0_4_line_31 | NAYY 4x150 SE | 30 | 31 | 0.036154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2096-4_0_4_line_32 | NAYY 4x150 SE | 31 | 36 | 0.0071249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2096-4_0_4_line_33 | NAYY 4x150 SE | 32 | 33 | 0.015865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2096-4_0_4_line_34 | NAYY 4x150 SE | 32 | 34 | 0.020721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2096-4_0_4_line_35 | NAYY 4x150 SE | 33 | 35 | 0.054549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2096-4_0_4_line_36 | NAYY 4x150 SE | 36 | 37 | 0.11692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2096-4_0_4_line_37 | NAYY 4x150 SE | 37 | 38 | 0.030824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2096-4_0_4_line_38 | NAYY 4x150 SE | 38 | 39 | 0.034269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2096-4_0_4_line_39 | NAYY 4x150 SE | 39 | 40 | 0.0024785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2096-4_0_4_line_40 | NAYY 4x150 SE | 40 | 43 | 0.034899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2096-4_0_4_line_41 | NAYY 4x150 SE | 41 | 42 | 0.026358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2096-4_0_4_line_42 | NAYY 4x150 SE | 41 | 43 | 0.030525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2096-4_0_4_trafo_10 | 0.25 MVA 20/0.4 kV | 44 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2559607.2914 | 1171335.7439 | 2559550.5902 | 1171344.7803
1 | 2559607.2914 | 1171335.7439 | 2559609.4955 | 1171341.5654 | 2559601.0972 | 1171360.9544 | 2559601.4893 | 1171363.5198 | 2559602.839 | 1171366.2899 | 2559613.2967 | 1171372.8387
2 | 2559592.6731 | 1171297.1889 | 2559607.2914 | 1171335.7439
3 | 2559613.2967 | 1171372.8387 | 2559623.6339 | 1171379.3121 | 2559631.8577 | 1171388.0692
4 | 2559592.6731 | 1171297.1889 | 2559593.9584 | 1171292.689
5 | 2559509.8354 | 1171435.0648 | 2559484.5871 | 1171413.3336
6 | 2559526.624 | 1171449.5147 | 2559509.8354 | 1171435.0648
7 | 2559526.624 | 1171449.5147 | 2559501.5347 | 1171479.0109 | 2559498.6574 | 1171481.9587
8 | 2559527.1991 | 1171448.8912 | 2559526.624 | 1171449.5147
9 | 2559466.0056 | 1171507.9147 | 2559483.8271 | 1171496.0396 | 2559489.3877 | 1171491.4551 | 2559498.6574 | 1171481.9587
10 | 2559585.1072 | 1171467.4371 | 2559563.8705 | 1171448.6405 | 2559557.3292 | 1171443.96 | 2559552.5217 | 1171441.1354 | 2559548.441 | 1171439.4843 | 2559544.0302 | 1171438.7804 | 2559540.4751 | 1171439.049 | 2559537.0874 | 1171440.3281 | 2559532.3193 | 1171443.3397 | 2559527.1991 | 1171448.8912
11 | 2559421.5373 | 1171527.0256 | 2559428.5695 | 1171525.5402 | 2559436.7988 | 1171523.0832 | 2559445.8014 | 1171519.6093 | 2559464.9496 | 1171508.6183 | 2559466.0056 | 1171507.9147
12 | 2559645.3544 | 1171424.6239 | 2559585.1072 | 1171467.4371
13 | 2559390.3495 | 1171530.4372 | 2559379.5794 | 1171530.5527
14 | 2559360.7431 | 1171528.7681 | 2559379.5794 | 1171530.5527 | 2559379.5794 | 1171530.5527
15 | 2559421.5373 | 1171527.0256 | 2559418.5099 | 1171527.665 | 2559408.6076 | 1171529.3219 | 2559393.7066 | 1171530.4012 | 2559390.3495 | 1171530.4372
16 | 2559358.7192 | 1171528.5763 | 2559360.7431 | 1171528.7681
17 | 2559631.8577 | 1171388.0692 | 2559645.3544 | 1171424.6239
18 | 2559593.9584 | 1171292.689 | 2559626.7158 | 1171307.2276
19 | 2559593.9584 | 1171292.689 | 2559597.4636 | 1171280.4701 | 2559617.9997 | 1171287.9577
20 | 2559671.7842 | 1171312.9974 | 2559669.3738 | 1171314.0253 | 2559667.2732 | 1171315.5958 | 2559665.6115 | 1171317.6191 | 2559654.7616 | 1171308.1095 | 2559640.9544 | 1171297.9305 | 2559617.9997 | 1171287.9577
21 | 2559617.9997 | 1171287.9577 | 2559619.6443 | 1171282.277 | 2559619.6553 | 1171277.1076 | 2559618.9991 | 1171275.6414
22 | 2559671.7842 | 1171312.9974 | 2559670.0487 | 1171306.3278 | 2559671.7673 | 1171293.4539 | 2559673.8083 | 1171284.4307
23 | 2559671.7842 | 1171312.9974 | 2559675.7593 | 1171312.6037 | 2559679.6065 | 1171313.6673 | 2559681.3294 | 1171314.9461
24 | 2559599.4084 | 1171243.1929 | 2559600.0269 | 1171244.3005 | 2559613.115 | 1171264.6451 | 2559616.2923 | 1171269.593 | 2559618.9991 | 1171275.6414
25 | 2559679.5745 | 1171258.9388 | 2559673.8083 | 1171284.4307
26 | 2559685.7146 | 1171323.3201 | 2559684.9463 | 1171319.4121 | 2559682.8124 | 1171316.047 | 2559681.3294 | 1171314.9461
27 | 2559685.7146 | 1171323.3201 | 2559696.5812 | 1171323.9473 | 2559713.9087 | 1171327.566 | 2559717.5232 | 1171328.313
28 | 2559599.4084 | 1171243.1929 | 2559587.132 | 1171221.2085
29 | 2559422.5272 | 1171233.3391 | 2559430.8065 | 1171246.1119 | 2559444.9647 | 1171262.8581 | 2559475.5247 | 1171280.235
30 | 2559458.7644 | 1171188.8326 | 2559422.5272 | 1171233.3391
31 | 2559458.7644 | 1171188.8326 | 2559440.802 | 1171157.4571
32 | 2559437.262 | 1171151.2738 | 2559440.802 | 1171157.4571
33 | 2559679.5745 | 1171258.9388 | 2559683.7123 | 1171243.6229
34 | 2559679.5745 | 1171258.9388 | 2559697.4689 | 1171253.5489 | 2559699.2331 | 1171252.5398
35 | 2559683.7123 | 1171243.6229 | 2559684.172 | 1171241.9212 | 2559685.465 | 1171231.7294 | 2559685.3696 | 1171222.1027 | 2559683.9543 | 1171214.1414 | 2559675.8627 | 1171197.3538 | 2559672.7474 | 1171192.0357
36 | 2559513.0422 | 1171080.1574 | 2559437.7641 | 1171125.9018 | 2559433.7506 | 1171129.6754 | 2559431.263 | 1171137.3629 | 2559433.4773 | 1171144.6628 | 2559437.262 | 1171151.2738
37 | 2559513.0422 | 1171080.1574 | 2559526.8663 | 1171107.707
38 | 2559526.8663 | 1171107.707 | 2559529.9931 | 1171113.9383 | 2559532.0875 | 1171118.2264 | 2559542.4344 | 1171138.2341
39 | 2559543.5729 | 1171140.4356 | 2559542.4344 | 1171138.2341
40 | 2559543.5729 | 1171140.4356 | 2559559.6039 | 1171171.4344
41 | 2559574.2811 | 1171198.1955 | 2559587.132 | 1171221.2085
42 | 2559574.2811 | 1171198.1955 | 2559562.9443 | 1171177.8937 | 2559559.6039 | 1171171.4344

## bus_geodata
| x | y | coords
0 | 2559550.5902 | 1171344.7803
1 | 2559607.2914 | 1171335.7439
2 | 2559613.2967 | 1171372.8387
3 | 2559592.6731 | 1171297.1889
4 | 2559509.8354 | 1171435.0648
5 | 2559484.5871 | 1171413.3336
6 | 2559526.624 | 1171449.5147
7 | 2559498.6574 | 1171481.9587
8 | 2559527.1991 | 1171448.8912
9 | 2559466.0056 | 1171507.9147
10 | 2559585.1072 | 1171467.4371
11 | 2559379.5794 | 1171530.5527
12 | 2559390.3495 | 1171530.4372
13 | 2559360.7431 | 1171528.768
14 | 2559421.5373 | 1171527.0256
15 | 2559358.7192 | 1171528.5763
16 | 2559645.3544 | 1171424.6239
17 | 2559631.8577 | 1171388.0692
18 | 2559626.7158 | 1171307.2276
19 | 2559593.9584 | 1171292.689
20 | 2559617.9997 | 1171287.9577
21 | 2559671.7842 | 1171312.9974
22 | 2559618.9991 | 1171275.6414
23 | 2559673.8083 | 1171284.4307
24 | 2559681.3294 | 1171314.9461
25 | 2559685.7146 | 1171323.3201
26 | 2559717.5232 | 1171328.313
27 | 2559599.4084 | 1171243.1929
28 | 2559475.5247 | 1171280.235
29 | 2559422.5272 | 1171233.3391
30 | 2559458.7644 | 1171188.8326
31 | 2559440.802 | 1171157.4571
32 | 2559679.5745 | 1171258.9388
33 | 2559683.7123 | 1171243.6229
34 | 2559699.2331 | 1171252.5398
35 | 2559672.7474 | 1171192.0357
36 | 2559437.262 | 1171151.2738
37 | 2559513.0422 | 1171080.1574
38 | 2559526.8663 | 1171107.707
39 | 2559542.4344 | 1171138.2341
40 | 2559543.5729 | 1171140.4356
41 | 2559574.2811 | 1171198.1955
42 | 2559587.132 | 1171221.2085
43 | 2559559.6039 | 1171171.4344
44 | 2559592.6731 | 1171297.1889

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99381 | -0.043193 | 0.023544 | 0.0059006
1 | 0.99575 | -0.029558 | 0 | 0
2 | 0.99308 | -0.048187 | 0.0017464 | 0.00043768
3 | 0.99957 | -0.0030018 | 0 | 0
4 | 0.98369 | -0.11456 | 0.0016859 | 0.00042253
5 | 0.9835 | -0.11591 | 0.0039273 | 0.00098427
6 | 0.98387 | -0.11327 | 0 | 0
7 | 0.98333 | -0.11709 | 0.00081499 | 0.00020426
8 | 0.98389 | -0.11315 | 0.0070677 | 0.0017713
9 | 0.98286 | -0.12048 | 0.0029286 | 0.00073398
10 | 0.98608 | -0.097519 | 0.011799 | 0.002957
11 | 0.98232 | -0.12434 | 0.0004575 | 0.00011466
12 | 0.98235 | -0.12409 | 0.0012567 | 0.00031496
13 | 0.98227 | -0.1247 | 0.0010361 | 0.00025966
14 | 0.98251 | -0.12294 | 0.0013552 | 0.00033965
15 | 0.98226 | -0.12472 | 0.00077642 | 0.00019459
16 | 0.98963 | -0.072469 | 0.0040282 | 0.0010096
17 | 0.99172 | -0.057739 | 0.0017583 | 0.00044066
18 | 0.99978 | -0.0015339 | 0.0042857 | 0.0010741
19 | 1 | 0 | -0.21043 | -0.052846
20 | 0.99654 | -0.024029 | 0 | 0
21 | 0.99065 | -0.065238 | 0 | 0
22 | 0.99516 | -0.03368 | 0.002931 | 0.00073459
23 | 0.9883 | -0.081807 | 0.0091282 | 0.0022877
24 | 0.99054 | -0.066004 | 0.0026905 | 0.00067431
25 | 0.99047 | -0.066477 | 0 | 0
26 | 0.99025 | -0.068032 | 0.004733 | 0.0011862
27 | 0.99118 | -0.061585 | 0.0061 | 0.0015288
28 | 0.98473 | -0.10734 | 0.0017434 | 0.00043694
29 | 0.98491 | -0.10604 | 0 | 0
30 | 0.98506 | -0.105 | 0.00090364 | 0.00022647
31 | 0.9852 | -0.10401 | 0.0014666 | 0.00036757
32 | 0.98654 | -0.094291 | 0 | 0
33 | 0.98598 | -0.098221 | 0.003958 | 0.00099198
34 | 0.98586 | -0.099078 | 0.022514 | 0.0056426
35 | 0.98439 | -0.10954 | 0.020181 | 0.0050578
36 | 0.98524 | -0.10371 | 0.0011186 | 0.00028036
37 | 0.98613 | -0.097399 | 0 | 0
38 | 0.98636 | -0.095735 | 0.00082678 | 0.00020721
39 | 0.98666 | -0.093594 | 0.00021863 | 5.4795e-05
40 | 0.98668 | -0.093434 | 0.00063112 | 0.00015817
41 | 0.98743 | -0.088119 | 0.026097 | 0.0065405
42 | 0.98876 | -0.078646 | 0.031376 | 0.0078636
43 | 0.98703 | -0.09095 | 0.002111 | 0.00052906
44 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.023544 | -0.0059006 | 0.023588 | 0.005917 | 4.4522e-05 | 1.6378e-05 | 0.035252 | 0.035251 | 0.035252 | 0.99381 | -0.043193 | 0.99575 | -0.029558 | 13.0561
1 | 0.041047 | 0.010336 | -0.040941 | -0.010295 | 0.00010658 | 4.0404e-05 | 0.061357 | 0.061357 | 0.061357 | 0.99575 | -0.029558 | 0.99308 | -0.048187 | 22.7249
2 | -0.064636 | -0.016253 | 0.064876 | 0.016345 | 0.00024011 | 9.181e-05 | 0.096608 | 0.096608 | 0.096608 | 0.99575 | -0.029558 | 0.99957 | -0.0030018 | 35.7808
3 | 0.039194 | 0.0098578 | -0.039142 | -0.009838 | 5.2126e-05 | 1.9736e-05 | 0.05874 | 0.058741 | 0.058741 | 0.99308 | -0.048187 | 0.99172 | -0.057739 | 21.7558
4 | -0.064876 | -0.016345 | 0.064903 | 0.016355 | 2.7256e-05 | 1.0422e-05 | 0.096608 | 0.096608 | 0.096608 | 0.99957 | -0.0030018 | 1 | 0 | 35.7807
5 | 0.003928 | 0.00098412 | -0.0039273 | -0.00098427 | 7.3389e-07 | -1.4055e-07 | 0.0059417 | 0.0059419 | 0.0059419 | 0.98369 | -0.11456 | 0.9835 | -0.11591 | 2.2007
6 | -0.0056139 | -0.0014067 | 0.0056149 | 0.0014068 | 9.9675e-07 | 1.0212e-07 | 0.008492 | 0.0084919 | 0.008492 | 0.98369 | -0.11456 | 0.98387 | -0.11327 | 3.1452
7 | 0.0086361 | 0.0021633 | -0.0086315 | -0.0021621 | 4.5606e-06 | 1.2103e-06 | 0.013061 | 0.013061 | 0.013061 | 0.98387 | -0.11327 | 0.98333 | -0.11709 | 4.8375
8 | -0.014251 | -0.0035701 | 0.014251 | 0.0035702 | 2.4587e-07 | 8.3794e-08 | 0.021553 | 0.021553 | 0.021553 | 0.98387 | -0.11327 | 0.98389 | -0.11315 | 7.9825
9 | 0.0078165 | 0.0019579 | -0.0078129 | -0.001957 | 3.6572e-06 | 8.7543e-07 | 0.011828 | 0.011828 | 0.011828 | 0.98333 | -0.11709 | 0.98286 | -0.12048 | 4.3808
10 | -0.021319 | -0.0053415 | 0.021365 | 0.0053584 | 4.6202e-05 | 1.6863e-05 | 0.032242 | 0.032242 | 0.032242 | 0.98389 | -0.11315 | 0.98608 | -0.097519 | 11.9414
11 | 0.0048843 | 0.001223 | -0.0048826 | -0.001223 | 1.664e-06 | 2.2119e-08 | 0.0073943 | 0.0073945 | 0.0073945 | 0.98286 | -0.12048 | 0.98251 | -0.12294 | 2.7387
12 | -0.033164 | -0.0083154 | 0.033279 | 0.0083589 | 0.00011551 | 4.3481e-05 | 0.050046 | 0.050046 | 0.050046 | 0.98608 | -0.097519 | 0.98963 | -0.072469 | 18.5356
13 | -0.0022701 | -0.00056868 | 0.0022701 | 0.00056857 | 7.9468e-08 | -1.0579e-07 | 0.0034386 | 0.0034386 | 0.0034386 | 0.98232 | -0.12434 | 0.98235 | -0.12409 | 1.2736
14 | 0.0018126 | 0.00045402 | -0.0018125 | -0.00045422 | 8.9003e-08 | -2.0528e-07 | 0.0027456 | 0.0027457 | 0.0027457 | 0.98232 | -0.12434 | 0.98227 | -0.1247 | 1.0169
15 | -0.0035268 | -0.00088353 | 0.0035274 | 0.00088335 | 5.5972e-07 | -1.8272e-07 | 0.0053421 | 0.005342 | 0.0053421 | 0.98235 | -0.12409 | 0.98251 | -0.12294 | 1.9786
16 | 0.00077642 | 0.00019456 | -0.00077642 | -0.00019459 | 1.755e-09 | -2.5058e-08 | 0.0011762 | 0.0011762 | 0.0011762 | 0.98227 | -0.1247 | 0.98226 | -0.12472 | 0.43563
17 | -0.037308 | -0.0093685 | 0.037384 | 0.0093974 | 7.6532e-05 | 2.8934e-05 | 0.056103 | 0.056102 | 0.056103 | 0.98963 | -0.072469 | 0.99172 | -0.057739 | 20.7787
18 | -0.0042857 | -0.0010741 | 0.0042866 | 0.001074 | 9.0987e-07 | -1.2012e-07 | 0.0063786 | 0.0063785 | 0.0063786 | 0.99978 | -0.0015339 | 1 | 0 | 2.3625
19 | 0.14044 | 0.035417 | -0.13997 | -0.035236 | 0.0004714 | 0.0001804 | 0.20906 | 0.20906 | 0.20906 | 1 | 0 | 0.99654 | -0.024029 | 38.7142
20 | 0.063843 | 0.016083 | -0.063477 | -0.015943 | 0.00036581 | 0.00013986 | 0.095358 | 0.095358 | 0.095358 | 0.99654 | -0.024029 | 0.99065 | -0.065238 | 35.3179
21 | 0.076128 | 0.019154 | -0.076025 | -0.019114 | 0.00010236 | 3.9206e-05 | 0.1137 | 0.1137 | 0.1137 | 0.99654 | -0.024029 | 0.99516 | -0.03368 | 42.1107
22 | 0.056051 | 0.014082 | -0.055922 | -0.014033 | 0.00012889 | 4.9198e-05 | 0.084205 | 0.084205 | 0.084205 | 0.99065 | -0.065238 | 0.9883 | -0.081807 | 31.187
23 | 0.0074257 | 0.0018607 | -0.0074249 | -0.0018605 | 7.8651e-07 | 1.7207e-07 | 0.011154 | 0.011154 | 0.011154 | 0.99065 | -0.065238 | 0.99054 | -0.066004 | 4.131
24 | 0.073094 | 0.01838 | -0.072811 | -0.018271 | 0.00028311 | 0.0001084 | 0.10932 | 0.10932 | 0.10932 | 0.99516 | -0.03368 | 0.99118 | -0.061585 | 40.4875
25 | 0.046794 | 0.011745 | -0.046713 | -0.011714 | 8.0969e-05 | 3.0808e-05 | 0.070461 | 0.070461 | 0.070461 | 0.9883 | -0.081807 | 0.98654 | -0.094291 | 26.0968
26 | 0.0047343 | 0.0011862 | -0.004734 | -0.0011862 | 3.0976e-07 | -7.187e-09 | 0.0071119 | 0.007112 | 0.007112 | 0.99054 | -0.066004 | 0.99047 | -0.066477 | 2.6341
27 | 0.004734 | 0.0011862 | -0.004733 | -0.0011862 | 1.0187e-06 | -2.3505e-08 | 0.007112 | 0.0071121 | 0.0071121 | 0.99047 | -0.066477 | 0.99025 | -0.068032 | 2.6341
28 | 0.066711 | 0.016743 | -0.066553 | -0.016682 | 0.00015762 | 6.03e-05 | 0.10016 | 0.10016 | 0.10016 | 0.99118 | -0.061585 | 0.98876 | -0.078646 | 37.0959
29 | -0.0017434 | -0.00043694 | 0.0017437 | 0.00043614 | 3.131e-07 | -7.996e-07 | 0.0026344 | 0.0026341 | 0.0026344 | 0.98473 | -0.10734 | 0.98491 | -0.10604 | 0.97572
30 | -0.0017437 | -0.00043614 | 0.001744 | 0.0004355 | 2.4847e-07 | -6.3495e-07 | 0.0026341 | 0.0026339 | 0.0026341 | 0.98491 | -0.10604 | 0.98506 | -0.105 | 0.9756
31 | -0.0026476 | -0.00066198 | 0.002648 | 0.00066166 | 3.6074e-07 | -3.2156e-07 | 0.0039989 | 0.0039987 | 0.0039989 | 0.98506 | -0.105 | 0.9852 | -0.10401 | 1.4811
32 | -0.0041146 | -0.0010292 | 0.0041148 | 0.0010292 | 1.7167e-07 | -2.4705e-08 | 0.0062139 | 0.0062138 | 0.0062139 | 0.9852 | -0.10401 | 0.98524 | -0.10371 | 2.3014
33 | 0.024184 | 0.0060662 | -0.024171 | -0.0060613 | 1.3174e-05 | 4.8644e-06 | 0.036479 | 0.036479 | 0.036479 | 0.98654 | -0.094291 | 0.98598 | -0.098221 | 13.5108
34 | 0.022529 | 0.0056481 | -0.022514 | -0.0056426 | 1.4931e-05 | 5.4784e-06 | 0.033982 | 0.033982 | 0.033982 | 0.98654 | -0.094291 | 0.98586 | -0.099078 | 12.586
35 | 0.020213 | 0.0050693 | -0.020181 | -0.0050578 | 3.1676e-05 | 1.1489e-05 | 0.030506 | 0.030506 | 0.030506 | 0.98598 | -0.098221 | 0.98439 | -0.10954 | 11.2985
36 | -0.0052334 | -0.0013096 | 0.005238 | 0.0013098 | 4.5569e-06 | 2.6235e-07 | 0.0079033 | 0.0079028 | 0.0079033 | 0.98524 | -0.10371 | 0.98613 | -0.097399 | 2.9272
37 | -0.005238 | -0.0013098 | 0.0052392 | 0.0013099 | 1.2012e-06 | 6.8676e-08 | 0.0079028 | 0.0079027 | 0.0079028 | 0.98613 | -0.097399 | 0.98636 | -0.095735 | 2.927
38 | -0.006066 | -0.0015171 | 0.0060677 | 0.0015174 | 1.7903e-06 | 2.5102e-07 | 0.00915 | 0.0091498 | 0.00915 | 0.98636 | -0.095735 | 0.98666 | -0.093594 | 3.3889
39 | -0.0062864 | -0.0015722 | 0.0062865 | 0.0015722 | 1.3898e-07 | 2.1798e-08 | 0.0094795 | 0.0094795 | 0.0094795 | 0.98666 | -0.093594 | 0.98668 | -0.093434 | 3.5109
40 | -0.0069176 | -0.0017303 | 0.00692 | 0.0017308 | 2.3695e-06 | 4.6547e-07 | 0.010431 | 0.010431 | 0.010431 | 0.98668 | -0.093434 | 0.98703 | -0.09095 | 3.8634
41 | -0.035131 | -0.0088013 | 0.035177 | 0.0088187 | 4.6097e-05 | 1.7392e-05 | 0.05294 | 0.05294 | 0.05294 | 0.98743 | -0.088119 | 0.98876 | -0.078646 | 19.6075
42 | 0.0090345 | 0.0022608 | -0.009031 | -0.0022599 | 3.53e-06 | 9.6739e-07 | 0.013613 | 0.013614 | 0.013614 | 0.98743 | -0.088119 | 0.98703 | -0.09095 | 5.0421

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21043 | 0.052846

## res_load
| p_mw | q_mvar
0 | 0.023544 | 0.0059006
1 | 0.0017464 | 0.00043768
2 | 0.0016859 | 0.00042253
3 | 0.0039273 | 0.00098427
4 | 0.00081499 | 0.00020426
5 | 0.0070677 | 0.0017713
6 | 0.0029286 | 0.00073398
7 | 0.011799 | 0.002957
8 | 0.0004575 | 0.00011466
9 | 0.0012567 | 0.00031496
10 | 0.0010361 | 0.00025966
11 | 0.0013552 | 0.00033965
12 | 0.00077642 | 0.00019459
13 | 0.0040282 | 0.0010096
14 | 0.0017583 | 0.00044066
15 | 0.0042857 | 0.0010741
16 | 0.002931 | 0.00073459
17 | 0.0091282 | 0.0022877
18 | 0.0026905 | 0.00067431
19 | 0.004733 | 0.0011862
20 | 0.0061 | 0.0015288
21 | 0.0017434 | 0.00043694
22 | 0.00090364 | 0.00022647
23 | 0.0014666 | 0.00036757
24 | 0.003958 | 0.00099198
25 | 0.022514 | 0.0056426
26 | 0.020181 | 0.0050578
27 | 0.0011186 | 0.00028036
28 | 0.00082678 | 0.00020721
29 | 0.00021863 | 5.4795e-05
30 | 0.00063112 | 0.00015817
31 | 0.026097 | 0.0065405
32 | 0.031376 | 0.0078636
33 | 0.002111 | 0.00052906

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1