## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2096-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2096-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2096-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2096-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2096-5_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2096-5_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2096-5_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2096-5_0_4_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_2096-5_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_2096-5_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_2096-5_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2096-5_0_4_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_2096-5_0_4_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_2096-5_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2096-5_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2096-5_0_4_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_2096-5_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_2096-5_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2096-5_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_2096-5_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_2096-5_0_4_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_2096-5_0_4_node_34 | 0.4 | n |  | TRUE
22 | bus_LV_2096-5_0_4_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_2096-5_0_4_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_2096-5_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_2096-5_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2096-5_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_2096-5_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2096-5_0_4_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_2096-5_0_4_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_2096-5_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_2096-5_0_4_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_2096-5_0_4_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_2096-5_0_4_node_33 | 0.4 | n |  | TRUE
34 | bus_MV_33_0_node_129 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2096-5_0_4_load_0 | 0 | 0.053971 | 0.013527 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2096-5_0_4_load_1 | 1 | 0.0089863 | 0.0022522 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2096-5_0_4_load_3 | 3 | 0.0049364 | 0.0012372 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2096-5_0_4_load_6 | 6 | 0.017986 | 0.0045076 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2096-5_0_4_load_27 | 7 | 0.015654 | 0.0039233 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2096-5_0_4_load_10 | 9 | 0.0086916 | 0.0021783 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2096-5_0_4_load_7 | 10 | 0.012462 | 0.0031233 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2096-5_0_4_load_28 | 11 | 0.011728 | 0.0029393 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2096-5_0_4_load_31 | 12 | 0.010124 | 0.0025374 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2096-5_0_4_load_9 | 13 | 0.013362 | 0.0033488 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2096-5_0_4_load_8 | 14 | 0.003792 | 0.00095037 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2096-5_0_4_load_29 | 15 | 0.0037914 | 0.00095022 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2096-5_0_4_load_14 | 16 | 0.0019314 | 0.00048404 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2096-5_0_4_load_16 | 18 | 0.0015299 | 0.00038343 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2096-5_0_4_load_34 | 21 | 0.0032068 | 0.00080371 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2096-5_0_4_load_35 | 22 | 0.0044878 | 0.0011248 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2096-5_0_4_load_30 | 23 | 0.025736 | 0.00645 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2096-5_0_4_load_18 | 25 | 0.0055159 | 0.0013824 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2096-5_0_4_load_19 | 26 | 0.0075595 | 0.0018946 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2096-5_0_4_load_24 | 29 | 0.0040894 | 0.0010249 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2096-5_0_4_load_21 | 30 | 0.0045814 | 0.0011482 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2096-5_0_4_load_32 | 31 | 0.0014382 | 0.00036045 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2096-5_0_4_load_26 | 32 | 0.0070047 | 0.0017556 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2096-5_0_4_load_33 | 33 | 0.0013607 | 0.00034101 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2096-5_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.027131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2096-5_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.024206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2096-5_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0069971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2096-5_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.036786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2096-5_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.033622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_2096-5_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0096742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2096-5_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.017793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2096-5_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.008133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2096-5_0_4_line_8 | NAYY 4x150 SE | 5 | 9 | 0.048445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2096-5_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.0134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2096-5_0_4_line_10 | NAYY 4x150 SE | 7 | 11 | 0.011666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2096-5_0_4_line_11 | NAYY 4x150 SE | 8 | 12 | 0.036552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2096-5_0_4_line_12 | NAYY 4x150 SE | 9 | 13 | 0.0099566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2096-5_0_4_line_13 | NAYY 4x150 SE | 12 | 15 | 0.017037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2096-5_0_4_line_14 | NAYY 4x150 SE | 13 | 14 | 0.031231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2096-5_0_4_line_15 | NAYY 4x150 SE | 15 | 23 | 0.0087021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2096-5_0_4_line_16 | NAYY 4x150 SE | 16 | 17 | 0.020201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2096-5_0_4_line_17 | NAYY 4x150 SE | 17 | 18 | 0.014824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2096-5_0_4_line_18 | NAYY 4x150 SE | 17 | 19 | 0.00607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2096-5_0_4_line_19 | NAYY 4x150 SE | 18 | 20 | 0.015651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2096-5_0_4_line_20 | NAYY 4x150 SE | 19 | 21 | 0.004408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2096-5_0_4_line_21 | NAYY 4x150 SE | 19 | 22 | 0.026185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2096-5_0_4_line_22 | NAYY 4x150 SE | 20 | 23 | 0.019441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2096-5_0_4_line_23 | NAYY 4x150 SE | 20 | 24 | 0.020366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2096-5_0_4_line_24 | NAYY 4x150 SE | 24 | 32 | 0.026848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2096-5_0_4_line_25 | NAYY 4x150 SE | 24 | 30 | 0.026331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2096-5_0_4_line_26 | NAYY 4x150 SE | 25 | 26 | 0.0074938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2096-5_0_4_line_27 | NAYY 4x150 SE | 26 | 27 | 0.031755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2096-5_0_4_line_28 | NAYY 4x150 SE | 27 | 28 | 0.035274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2096-5_0_4_line_29 | NAYY 4x150 SE | 27 | 29 | 0.018392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2096-5_0_4_line_30 | NAYY 4x150 SE | 27 | 30 | 0.028229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2096-5_0_4_line_31 | NAYY 4x150 SE | 28 | 31 | 0.0064713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2096-5_0_4_line_32 | NAYY 4x150 SE | 31 | 33 | 0.038554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2096-5_0_4_trafo_5 | 0.25 MVA 20/0.4 kV | 34 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2560229.1944 | 1171886.088 | 2560213.4351 | 1171864.0036
1 | 2560242.5241 | 1171906.2479 | 2560239.2329 | 1171900.1554 | 2560229.1944 | 1171886.088
2 | 2560209.3707 | 1171858.3079 | 2560213.4351 | 1171864.0036
3 | 2560242.5241 | 1171906.2479 | 2560262.0794 | 1171895.4902 | 2560274.7519 | 1171888.3469
4 | 2560242.5241 | 1171906.2479 | 2560255.7018 | 1171937.1877
5 | 2560209.3707 | 1171858.3079 | 2560203.7513 | 1171850.4332
6 | 2560274.7519 | 1171888.3469 | 2560266.3565 | 1171872.6588
7 | 2560255.7018 | 1171937.1877 | 2560258.9714 | 1171944.6366
8 | 2560255.7018 | 1171937.1877 | 2560222.627 | 1171939.2306 | 2560212.2489 | 1171939.4108 | 2560207.4431 | 1171938.3229
9 | 2560195.9556 | 1171839.5348 | 2560197.7418 | 1171842.0117 | 2560203.7513 | 1171850.4332
10 | 2560266.3565 | 1171872.6588 | 2560261.6863 | 1171863.9319 | 2560261.0646 | 1171862.2771
11 | 2560258.9714 | 1171944.6366 | 2560258.2223 | 1171955.0693 | 2560268.4801 | 1171979.0608
12 | 2560198.1021 | 1171935.0386 | 2560203.0413 | 1171937.3264 | 2560207.4431 | 1171938.3229
13 | 2560275.4399 | 1171994.5947 | 2560274.2426 | 1171992.5382 | 2560268.4801 | 1171979.0608
14 | 2560169.7633 | 1171921.9121 | 2560198.1021 | 1171935.0386
15 | 2560275.4399 | 1171994.5947 | 2560278.4205 | 1171999.7142 | 2560280.1338 | 1172001.9011
16 | 2560282.1211 | 1172043.3125 | 2560302.1445 | 1172045.9866
17 | 2560282.1211 | 1172043.3125 | 2560287.9425 | 1172029.6792
18 | 2560279.7412 | 1172048.8979 | 2560282.1211 | 1172043.3125
19 | 2560294.0888 | 1172015.2851 | 2560287.9425 | 1172029.6792
20 | 2560279.7412 | 1172048.8979 | 2560275.5256 | 1172047.5696
21 | 2560279.7412 | 1172048.8979 | 2560285.6252 | 1172050.393 | 2560301.4605 | 1172051.9555 | 2560302.5208 | 1172052.6822 | 2560303.2207 | 1172055.579
22 | 2560294.0888 | 1172015.2851 | 2560287.8469 | 1172010.5907 | 2560282.7094 | 1172005.1886 | 2560280.1338 | 1172001.9011
23 | 2560294.0888 | 1172015.2851 | 2560297.921 | 1172017.6387 | 2560304.4337 | 1172020.4971 | 2560310.7787 | 1172022.3004 | 2560312.9754 | 1172022.5415
24 | 2560312.9754 | 1172022.5415 | 2560312.816 | 1172001.954 | 2560313.2388 | 1171999.9724 | 2560315.5142 | 1171996.4019
25 | 2560312.9754 | 1172022.5415 | 2560316.4887 | 1172022.9184 | 2560323.1088 | 1172022.3743 | 2560329.1586 | 1172021.1891 | 2560338.8412 | 1172018.7276
26 | 2560363.13 | 1171980.4846 | 2560363.372 | 1171978.6292 | 2560364.7413 | 1171973.1758
27 | 2560366.1997 | 1172011.7723 | 2560363.826 | 1172002.1385 | 2560362.5561 | 1171995.1655 | 2560362.2201 | 1171990.632 | 2560362.3748 | 1171986.2731 | 2560363.13 | 1171980.4846
28 | 2560366.1997 | 1172011.7723 | 2560376.2094 | 1172033.3729 | 2560378.838 | 1172039.9256 | 2560380.1509 | 1172044.1414
29 | 2560366.1997 | 1172011.7723 | 2560379.8837 | 1172008.4022 | 2560383.9713 | 1172007.0704
30 | 2560366.1997 | 1172011.7723 | 2560338.8412 | 1172018.7276
31 | 2560380.1509 | 1172044.1414 | 2560380.6258 | 1172047.7179 | 2560380.8374 | 1172050.5734
32 | 2560380.8374 | 1172050.5734 | 2560380.9198 | 1172051.6847 | 2560380.7954 | 1172055.9989 | 2560380.4178 | 1172059.0474 | 2560379.479 | 1172062.8111 | 2560377.9652 | 1172067.5236 | 2560375.6311 | 1172071.9414 | 2560372.9336 | 1172075.7835 | 2560368.4628 | 1172080.9491 | 2560364.9362 | 1172084.0569

## bus_geodata
| x | y | coords
0 | 2560229.1944 | 1171886.088
1 | 2560213.4351 | 1171864.0036
2 | 2560242.5241 | 1171906.2479
3 | 2560209.3707 | 1171858.3079
4 | 2560274.7519 | 1171888.3469
5 | 2560255.7018 | 1171937.1877
6 | 2560203.7513 | 1171850.4332
7 | 2560266.3565 | 1171872.6588
8 | 2560258.9714 | 1171944.6366
9 | 2560207.4431 | 1171938.3229
10 | 2560195.9556 | 1171839.5348
11 | 2560261.0646 | 1171862.2771
12 | 2560268.4801 | 1171979.0608
13 | 2560198.1021 | 1171935.0386
14 | 2560169.7633 | 1171921.9121
15 | 2560275.4399 | 1171994.5947
16 | 2560302.1445 | 1172045.9866
17 | 2560282.1211 | 1172043.3125
18 | 2560287.9425 | 1172029.6792
19 | 2560279.7412 | 1172048.8979
20 | 2560294.0888 | 1172015.2851
21 | 2560275.5256 | 1172047.5696
22 | 2560303.2207 | 1172055.579
23 | 2560280.1338 | 1172001.9011
24 | 2560312.9754 | 1172022.5415
25 | 2560364.7413 | 1171973.1758
26 | 2560363.13 | 1171980.4846
27 | 2560366.1997 | 1172011.7723
28 | 2560380.1509 | 1172044.1414
29 | 2560383.9713 | 1172007.0704
30 | 2560338.8412 | 1172018.7276
31 | 2560380.8374 | 1172050.5734
32 | 2560315.5142 | 1171996.4019
33 | 2560364.9362 | 1172084.0569
34 | 2560258.9714 | 1171944.6366

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99355 | -0.045148 | 0.053971 | 0.013527
1 | 0.99182 | -0.057341 | 0.0089863 | 0.0022522
2 | 0.99697 | -0.021161 | 0 | 0
3 | 0.99146 | -0.059854 | 0.0049364 | 0.0012372
4 | 0.99552 | -0.031292 | 0 | 0
5 | 1 | 0 | -0.23638 | -0.059255
6 | 0.99104 | -0.062846 | 0.017986 | 0.0045076
7 | 0.99482 | -0.036202 | 0.015654 | 0.0039233
8 | 0.99904 | -0.0066946 | 0 | 0
9 | 0.99821 | -0.012522 | 0.0086916 | 0.0021783
10 | 0.9908 | -0.064544 | 0.012462 | 0.0031233
11 | 0.99463 | -0.037582 | 0.011728 | 0.0029393
12 | 0.99471 | -0.036942 | 0.010124 | 0.0025374
13 | 0.99797 | -0.014233 | 0.013362 | 0.0033488
14 | 0.9978 | -0.015421 | 0.003792 | 0.00095037
15 | 0.99293 | -0.049383 | 0.0037914 | 0.00095022
16 | 0.99037 | -0.067482 | 0.0019314 | 0.00048404
17 | 0.99042 | -0.067085 | 0 | 0
18 | 0.99063 | -0.065633 | 0.0015299 | 0.00038343
19 | 0.99036 | -0.06756 | 0 | 0
20 | 0.99088 | -0.063856 | 0 | 0
21 | 0.99034 | -0.067704 | 0.0032068 | 0.00080371
22 | 0.99019 | -0.068757 | 0.0044878 | 0.0011248
23 | 0.99208 | -0.05542 | 0.025736 | 0.00645
24 | 0.98995 | -0.070398 | 0 | 0
25 | 0.98755 | -0.087419 | 0.0055159 | 0.0013824
26 | 0.98761 | -0.086996 | 0.0075595 | 0.0018946
27 | 0.98821 | -0.08275 | 0 | 0
28 | 0.98807 | -0.083761 | 0 | 0
29 | 0.9881 | -0.083519 | 0.0040894 | 0.0010249
30 | 0.98902 | -0.076991 | 0.0045814 | 0.0011482
31 | 0.98804 | -0.083946 | 0.0014382 | 0.00036045
32 | 0.98968 | -0.072314 | 0.0070047 | 0.0017556
33 | 0.98796 | -0.084483 | 0.0013607 | 0.00034101
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.044474 | 0.011159 | -0.044398 | -0.011131 | 7.5119e-05 | 2.8541e-05 | 0.066612 | 0.066612 | 0.066612 | 0.99355 | -0.045148 | 0.99182 | -0.057341 | 24.6711
1 | -0.098445 | -0.024686 | 0.098773 | 0.024812 | 0.00032837 | 0.00012598 | 0.14744 | 0.14744 | 0.14744 | 0.99355 | -0.045148 | 0.99697 | -0.021161 | 54.6088
2 | 0.035412 | 0.0088785 | -0.0354 | -0.0088738 | 1.2325e-05 | 4.65e-06 | 0.05313 | 0.05313 | 0.05313 | 0.99182 | -0.057341 | 0.99146 | -0.059854 | 19.6777
3 | 0.027441 | 0.0068846 | -0.027403 | -0.0068702 | 3.8512e-05 | 1.4333e-05 | 0.04096 | 0.04096 | 0.04096 | 0.99697 | -0.021161 | 0.99552 | -0.031292 | 15.1705
4 | -0.12621 | -0.031696 | 0.12659 | 0.031839 | 0.00037235 | 0.00014233 | 0.1884 | 0.1884 | 0.1884 | 0.99697 | -0.021161 | 1 | 0 | 34.8896
5 | 0.030463 | 0.0076366 | -0.030451 | -0.0076319 | 1.2619e-05 | 4.7288e-06 | 0.045721 | 0.045721 | 0.045721 | 0.99146 | -0.059854 | 0.99104 | -0.062846 | 16.9338
6 | 0.027403 | 0.0068702 | -0.027384 | -0.0068633 | 1.8628e-05 | 6.9334e-06 | 0.04096 | 0.04096 | 0.04096 | 0.99552 | -0.031292 | 0.99482 | -0.036202 | 15.1705
7 | 0.083101 | 0.020921 | -0.083023 | -0.020892 | 7.7642e-05 | 2.9756e-05 | 0.12369 | 0.12369 | 0.12369 | 1 | 0 | 0.99904 | -0.0066946 | 45.8107
8 | 0.025895 | 0.0064954 | -0.02585 | -0.0064788 | 4.4888e-05 | 1.663e-05 | 0.038534 | 0.038535 | 0.038535 | 1 | 0 | 0.99821 | -0.012522 | 14.2721
9 | 0.012465 | 0.0031243 | -0.012462 | -0.0031233 | 2.929e-06 | 9.5391e-07 | 0.018716 | 0.018716 | 0.018716 | 0.99104 | -0.062846 | 0.9908 | -0.064544 | 6.932
10 | 0.01173 | 0.00294 | -0.011728 | -0.0029393 | 2.2409e-06 | 7.1045e-07 | 0.017545 | 0.017545 | 0.017545 | 0.99482 | -0.036202 | 0.99463 | -0.037582 | 6.4983
11 | 0.083023 | 0.020892 | -0.082675 | -0.020758 | 0.00034895 | 0.00013373 | 0.12369 | 0.12369 | 0.12369 | 0.99904 | -0.0066946 | 0.99471 | -0.036942 | 45.8108
12 | 0.017159 | 0.0043005 | -0.017155 | -0.004299 | 4.0648e-06 | 1.4333e-06 | 0.025578 | 0.025578 | 0.025578 | 0.99821 | -0.012522 | 0.99797 | -0.014233 | 9.4734
13 | 0.07255 | 0.01822 | -0.072425 | -0.018172 | 0.00012525 | 4.7954e-05 | 0.10854 | 0.10854 | 0.10854 | 0.99471 | -0.036942 | 0.99293 | -0.049383 | 40.2013
14 | 0.0037926 | 0.0009502 | -0.003792 | -0.00095037 | 6.2321e-07 | -1.683e-07 | 0.0056549 | 0.005655 | 0.005655 | 0.99797 | -0.014233 | 0.9978 | -0.015421 | 2.0945
15 | 0.068633 | 0.017222 | -0.068576 | -0.0172 | 5.7453e-05 | 2.1985e-05 | 0.10286 | 0.10286 | 0.10286 | 0.99293 | -0.049383 | 0.99208 | -0.05542 | 38.097
16 | -0.0019314 | -0.00048404 | 0.0019315 | 0.00048382 | 1.0614e-07 | -2.1913e-07 | 0.0029018 | 0.0029018 | 0.0029018 | 0.99037 | -0.067482 | 0.99042 | -0.067085 | 1.0748
17 | -0.0096274 | -0.0024123 | 0.0096294 | 0.0024129 | 1.9352e-06 | 5.5351e-07 | 0.014464 | 0.014464 | 0.014464 | 0.99042 | -0.067085 | 0.99063 | -0.065633 | 5.3571
18 | 0.007696 | 0.0019285 | -0.0076955 | -0.0019284 | 5.0637e-07 | 1.1665e-07 | 0.011562 | 0.011562 | 0.011562 | 0.99042 | -0.067085 | 0.99036 | -0.06756 | 4.2824
19 | -0.011159 | -0.0027963 | 0.011162 | 0.0027972 | 2.7441e-06 | 8.5385e-07 | 0.016762 | 0.016762 | 0.016762 | 0.99063 | -0.065633 | 0.99088 | -0.063856 | 6.2082
20 | 0.0032069 | 0.00080367 | -0.0032068 | -0.00080371 | 6.386e-08 | -3.2157e-08 | 0.0048184 | 0.0048184 | 0.0048184 | 0.99036 | -0.06756 | 0.99034 | -0.067704 | 1.7846
21 | 0.0044886 | 0.0011247 | -0.0044878 | -0.0011248 | 7.4316e-07 | -5.1046e-08 | 0.006744 | 0.0067441 | 0.0067441 | 0.99036 | -0.06756 | 0.99019 | -0.068757 | 2.4978
22 | -0.04279 | -0.010731 | 0.04284 | 0.01075 | 5.0096e-05 | 1.9017e-05 | 0.06426 | 0.06426 | 0.06426 | 0.99088 | -0.063856 | 0.99208 | -0.05542 | 23.8002
23 | 0.031628 | 0.007934 | -0.031599 | -0.0079233 | 2.8671e-05 | 1.0765e-05 | 0.047498 | 0.047499 | 0.047499 | 0.99088 | -0.063856 | 0.98995 | -0.070398 | 17.592
24 | 0.0070066 | 0.0017559 | -0.0070047 | -0.0017556 | 1.8582e-06 | 3.6962e-07 | 0.010532 | 0.010532 | 0.010532 | 0.98995 | -0.070398 | 0.98968 | -0.072314 | 3.9007
25 | 0.024593 | 0.0061673 | -0.02457 | -0.006159 | 2.2453e-05 | 8.2977e-06 | 0.036967 | 0.036967 | 0.036967 | 0.98995 | -0.070398 | 0.98902 | -0.076991 | 13.6915
26 | -0.0055159 | -0.0013824 | 0.0055162 | 0.0013824 | 3.2301e-07 | 2.8348e-08 | 0.0083112 | 0.0083112 | 0.0083112 | 0.98755 | -0.087419 | 0.98761 | -0.086996 | 3.0782
27 | -0.013076 | -0.003277 | 0.013083 | 0.0032796 | 7.6908e-06 | 2.5514e-06 | 0.019701 | 0.019701 | 0.019701 | 0.98761 | -0.086996 | 0.98821 | -0.08275 | 7.2967
28 | 0.0027994 | 0.00070065 | -0.0027991 | -0.00070095 | 3.9106e-07 | -3.0145e-07 | 0.004215 | 0.0042151 | 0.0042151 | 0.98821 | -0.08275 | 0.98807 | -0.083761 | 1.5612
29 | 0.0040898 | 0.0010248 | -0.0040894 | -0.0010249 | 4.3524e-07 | -6.8206e-08 | 0.0061582 | 0.0061583 | 0.0061583 | 0.98821 | -0.08275 | 0.9881 | -0.083519 | 2.2809
30 | -0.019973 | -0.0050051 | 0.019989 | 0.0050108 | 1.5932e-05 | 5.7656e-06 | 0.030074 | 0.030074 | 0.030074 | 0.98821 | -0.08275 | 0.98902 | -0.076991 | 11.1386
31 | 0.0027991 | 0.00070095 | -0.002799 | -0.00070101 | 7.1747e-08 | -5.5287e-08 | 0.0042151 | 0.0042152 | 0.0042152 | 0.98807 | -0.083761 | 0.98804 | -0.083946 | 1.5612
32 | 0.0013608 | 0.00034056 | -0.0013607 | -0.00034101 | 1.0103e-07 | -4.5488e-07 | 0.0020492 | 0.0020494 | 0.0020494 | 0.98804 | -0.083946 | 0.98796 | -0.084483 | 0.75902

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23638 | 0.059255

## res_load
| p_mw | q_mvar
0 | 0.053971 | 0.013527
1 | 0.0089863 | 0.0022522
2 | 0.0049364 | 0.0012372
3 | 0.017986 | 0.0045076
4 | 0.015654 | 0.0039233
5 | 0.0086916 | 0.0021783
6 | 0.012462 | 0.0031233
7 | 0.011728 | 0.0029393
8 | 0.010124 | 0.0025374
9 | 0.013362 | 0.0033488
10 | 0.003792 | 0.00095037
11 | 0.0037914 | 0.00095022
12 | 0.0019314 | 0.00048404
13 | 0.0015299 | 0.00038343
14 | 0.0032068 | 0.00080371
15 | 0.0044878 | 0.0011248
16 | 0.025736 | 0.00645
17 | 0.0055159 | 0.0013824
18 | 0.0075595 | 0.0018946
19 | 0.0040894 | 0.0010249
20 | 0.0045814 | 0.0011482
21 | 0.0014382 | 0.00036045
22 | 0.0070047 | 0.0017556
23 | 0.0013607 | 0.00034101

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1