## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2102-10_1_2_node_45 | 0.4 | n |  | TRUE
1 | bus_LV_2102-10_1_2_node_75 | 0.4 | n |  | TRUE
2 | bus_LV_2102-10_1_2_node_46 | 0.4 | n |  | TRUE
3 | bus_LV_2102-10_1_2_node_47 | 0.4 | n |  | TRUE
4 | bus_LV_2102-10_1_2_node_48 | 0.4 | n |  | TRUE
5 | bus_LV_2102-10_1_2_node_49 | 0.4 | n |  | TRUE
6 | bus_LV_2102-10_1_2_node_50 | 0.4 | n |  | TRUE
7 | bus_LV_2102-10_1_2_node_51 | 0.4 | n |  | TRUE
8 | bus_LV_2102-10_1_2_node_52 | 0.4 | n |  | TRUE
9 | bus_LV_2102-10_1_2_node_53 | 0.4 | n |  | TRUE
10 | bus_LV_2102-10_1_2_node_55 | 0.4 | n |  | TRUE
11 | bus_LV_2102-10_1_2_node_74 | 0.4 | n |  | TRUE
12 | bus_LV_2102-10_1_2_node_54 | 0.4 | n |  | TRUE
13 | bus_LV_2102-10_1_2_node_58 | 0.4 | n |  | TRUE
14 | bus_LV_2102-10_1_2_node_56 | 0.4 | n |  | TRUE
15 | bus_LV_2102-10_1_2_node_57 | 0.4 | n |  | TRUE
16 | bus_LV_2102-10_1_2_node_67 | 0.4 | n |  | TRUE
17 | bus_LV_2102-10_1_2_node_68 | 0.4 | n |  | TRUE
18 | bus_LV_2102-10_1_2_node_73 | 0.4 | n |  | TRUE
19 | bus_LV_2102-10_1_2_node_59 | 0.4 | n |  | TRUE
20 | bus_LV_2102-10_1_2_node_60 | 0.4 | n |  | TRUE
21 | bus_LV_2102-10_1_2_node_61 | 0.4 | n |  | TRUE
22 | bus_LV_2102-10_1_2_node_62 | 0.4 | n |  | TRUE
23 | bus_LV_2102-10_1_2_node_63 | 0.4 | n |  | TRUE
24 | bus_LV_2102-10_1_2_node_64 | 0.4 | n |  | TRUE
25 | bus_LV_2102-10_1_2_node_65 | 0.4 | n |  | TRUE
26 | bus_LV_2102-10_1_2_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_2102-10_1_2_node_69 | 0.4 | n |  | TRUE
28 | bus_LV_2102-10_1_2_node_70 | 0.4 | n |  | TRUE
29 | bus_LV_2102-10_1_2_node_78 | 0.4 | n |  | TRUE
30 | bus_LV_2102-10_1_2_node_71 | 0.4 | n |  | TRUE
31 | bus_LV_2102-10_1_2_node_72 | 0.4 | n |  | TRUE
32 | bus_MV_366_0_node_107 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2102-10_1_2_load_45 | 0 | 0.0058557 | 0.0014676 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2102-10_1_2_load_75 | 1 | 0.0025387 | 0.00063625 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2102-10_1_2_load_46 | 2 | 0.0074511 | 0.0018674 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2102-10_1_2_load_47 | 3 | 0.0012188 | 0.00030547 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2102-10_1_2_load_50 | 6 | 0.0012909 | 0.00032353 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2102-10_1_2_load_51 | 7 | 0.0011025 | 0.0002763 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2102-10_1_2_load_52 | 8 | 0.0044896 | 0.0011252 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2102-10_1_2_load_53 | 9 | 0.0024491 | 0.00061381 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2102-10_1_2_load_74 | 11 | 0.0019437 | 0.00048713 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2102-10_1_2_load_54 | 12 | 0.0012667 | 0.00031747 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2102-10_1_2_load_58 | 13 | 0.0026958 | 0.00067563 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2102-10_1_2_load_57 | 15 | 0.0022685 | 0.00056854 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2102-10_1_2_load_67 | 16 | 0.0023776 | 0.00059587 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2102-10_1_2_load_68 | 17 | 0.0023885 | 0.00059862 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2102-10_1_2_load_73 | 18 | 0.0024612 | 0.00061683 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2102-10_1_2_load_59 | 19 | 0.0023934 | 0.00059984 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2102-10_1_2_load_61 | 21 | 0.01673 | 0.0041928 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2102-10_1_2_load_62 | 22 | 0.0016858 | 0.00042251 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2102-10_1_2_load_63 | 23 | 0.0011518 | 0.00028866 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2102-10_1_2_load_64 | 24 | 0.002393 | 0.00059974 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2102-10_1_2_load_65 | 25 | 0.0014261 | 0.0003574 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2102-10_1_2_load_66 | 26 | 0.0013845 | 0.000347 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2102-10_1_2_load_69 | 27 | 0.0052372 | 0.0013126 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2102-10_1_2_load_70 | 28 | 0.0052288 | 0.0013105 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2102-10_1_2_load_78 | 29 | 0.0014044 | 0.00035197 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2102-10_1_2_load_71 | 30 | 0.0023562 | 0.00059053 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2102-10_1_2_load_72 | 31 | 0.0025415 | 0.00063696 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2102-10_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.12901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2102-10_1_2_line_1 | NAYY 4x150 SE | 1 | 12 | 0.090833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2102-10_1_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.027486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2102-10_1_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.017966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2102-10_1_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0011067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2102-10_1_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.020958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2102-10_1_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.035634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2102-10_1_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.030623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2102-10_1_2_line_8 | NAYY 4x150 SE | 5 | 9 | 0.059381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2102-10_1_2_line_9 | NAYY 4x150 SE | 6 | 10 | 0.051067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2102-10_1_2_line_10 | NAYY 4x150 SE | 7 | 11 | 0.0079132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2102-10_1_2_line_11 | NAYY 4x150 SE | 8 | 12 | 0.0024541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2102-10_1_2_line_12 | NAYY 4x150 SE | 9 | 13 | 0.040751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2102-10_1_2_line_13 | NAYY 4x150 SE | 10 | 14 | 0.035607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2102-10_1_2_line_14 | NAYY 4x150 SE | 10 | 15 | 0.025915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2102-10_1_2_line_15 | NAYY 4x150 SE | 13 | 19 | 0.032141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2102-10_1_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.01827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2102-10_1_2_line_17 | NAYY 4x150 SE | 14 | 17 | 0.0058403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2102-10_1_2_line_18 | NAYY 4x150 SE | 15 | 18 | 0.020792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2102-10_1_2_line_19 | NAYY 4x150 SE | 16 | 26 | 0.0034094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2102-10_1_2_line_20 | NAYY 4x150 SE | 17 | 27 | 0.20386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2102-10_1_2_line_21 | NAYY 4x150 SE | 18 | 31 | 0.021112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2102-10_1_2_line_22 | NAYY 4x150 SE | 19 | 20 | 0.043424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2102-10_1_2_line_23 | NAYY 4x150 SE | 20 | 21 | 0.029599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2102-10_1_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.032849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2102-10_1_2_line_25 | NAYY 4x150 SE | 23 | 24 | 0.019744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2102-10_1_2_line_26 | NAYY 4x150 SE | 24 | 25 | 0.013187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2102-10_1_2_line_27 | NAYY 4x150 SE | 25 | 26 | 0.016581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2102-10_1_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.032171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2102-10_1_2_line_29 | NAYY 4x150 SE | 28 | 29 | 0.016076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2102-10_1_2_line_30 | NAYY 4x150 SE | 30 | 31 | 0.02221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2102-10_1_2_trafo_46 | 0.25 MVA 20/0.4 kV | 32 | 2 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2554807.2375 | 1163388.2386 | 2554872.0526 | 1163276.6871
1 | 2554728.6766 | 1163433.8331 | 2554807.2375 | 1163388.2386
2 | 2554695.5882 | 1163439.0856 | 2554703.0737 | 1163450.5017 | 2554712.4063 | 1163460.7144
3 | 2554689.3034 | 1163422.3465 | 2554690.995 | 1163429.293 | 2554695.5882 | 1163439.0856
4 | 2554713.1529 | 1163461.5314 | 2554712.4063 | 1163460.7144
5 | 2554689.3034 | 1163422.3465 | 2554684.3429 | 1163418.6932 | 2554669.8317 | 1163415.7976
6 | 2554689.3034 | 1163422.3465 | 2554708.2045 | 1163392.1388
7 | 2554713.1529 | 1163461.5314 | 2554721.5944 | 1163448.4275 | 2554727.7214 | 1163443.2563 | 2554728.4291 | 1163436.2747
8 | 2554713.1529 | 1163461.5314 | 2554713.848 | 1163462.2932 | 2554729.6864 | 1163492.4895 | 2554740.8159 | 1163514.0365
9 | 2554621.7467 | 1163400.3235 | 2554639.8971 | 1163410.0246 | 2554664.5894 | 1163414.7515 | 2554669.8317 | 1163415.7976
10 | 2554712.4019 | 1163385.4306 | 2554708.2045 | 1163392.1388
11 | 2554728.6766 | 1163433.8331 | 2554728.4291 | 1163436.2747
12 | 2554740.8159 | 1163514.0365 | 2554749.2826 | 1163530.4282 | 2554760.7112 | 1163549.579
13 | 2554621.7467 | 1163400.3235 | 2554606.9164 | 1163395.1107 | 2554594.1666 | 1163393.5731 | 2554587.0535 | 1163392.9266
14 | 2554621.7467 | 1163400.3235 | 2554620.4127 | 1163408.2488 | 2554622.9607 | 1163425.9446
15 | 2554760.7112 | 1163549.579 | 2554765.1004 | 1163556.9338 | 2554770.5902 | 1163576.9696 | 2554771.1852 | 1163579.7079
16 | 2554587.0535 | 1163392.9266 | 2554587.4537 | 1163411.1918
17 | 2554587.0535 | 1163392.9266 | 2554586.1705 | 1163387.1534
18 | 2554625.9239 | 1163446.5239 | 2554622.9607 | 1163425.9446
19 | 2554587.5283 | 1163414.6004 | 2554587.4537 | 1163411.1918
20 | 2554586.1705 | 1163387.1534 | 2554490.0838 | 1163207.3603
21 | 2554628.9327 | 1163467.4201 | 2554625.9239 | 1163446.5239
22 | 2554780.4057 | 1163622.1415 | 2554771.1852 | 1163579.7079
23 | 2554780.4057 | 1163622.1415 | 2554805.7417 | 1163606.7202
24 | 2554600.1418 | 1163495.5172 | 2554592.4166 | 1163470.9824 | 2554591.6251 | 1163463.8999
25 | 2554591.6251 | 1163463.8999 | 2554589.432 | 1163444.2778
26 | 2554587.9672 | 1163431.1721 | 2554589.432 | 1163444.2778
27 | 2554587.9672 | 1163431.1721 | 2554587.8729 | 1163430.3288 | 2554587.5283 | 1163414.6004
28 | 2554490.0838 | 1163207.3603 | 2554473.6972 | 1163179.6756
29 | 2554473.6972 | 1163179.6756 | 2554470.8075 | 1163174.7935 | 2554465.3303 | 1163165.9497
30 | 2554632.098 | 1163489.4033 | 2554628.9327 | 1163467.4201

## bus_geodata
| x | y | coords
0 | 2554872.0526 | 1163276.6871
1 | 2554807.2375 | 1163388.2386
2 | 2554695.5882 | 1163439.0856
3 | 2554712.4063 | 1163460.7144
4 | 2554689.3034 | 1163422.3465
5 | 2554713.1529 | 1163461.5314
6 | 2554669.8317 | 1163415.7976
7 | 2554708.2045 | 1163392.1388
8 | 2554728.4291 | 1163436.2747
9 | 2554740.8159 | 1163514.0365
10 | 2554621.7467 | 1163400.3235
11 | 2554712.4019 | 1163385.4306
12 | 2554728.6766 | 1163433.8331
13 | 2554760.7112 | 1163549.579
14 | 2554587.0535 | 1163392.9266
15 | 2554622.9607 | 1163425.9446
16 | 2554587.4537 | 1163411.1918
17 | 2554586.1705 | 1163387.1534
18 | 2554625.9239 | 1163446.5239
19 | 2554771.1852 | 1163579.7079
20 | 2554780.4057 | 1163622.1415
21 | 2554805.7417 | 1163606.7202
22 | 2554600.1418 | 1163495.5172
23 | 2554591.6251 | 1163463.9
24 | 2554589.432 | 1163444.2778
25 | 2554587.9672 | 1163431.1721
26 | 2554587.5283 | 1163414.6004
27 | 2554490.0838 | 1163207.3603
28 | 2554473.6972 | 1163179.6756
29 | 2554465.3303 | 1163165.9497
30 | 2554632.098 | 1163489.4033
31 | 2554628.9327 | 1163467.4201
32 | 2554689.3034 | 1163422.3465

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99555 | -0.031192 | 0.0058557 | 0.0014676
1 | 0.99663 | -0.023584 | 0.0025387 | 0.00063625
2 | 1 | 0 | -0.079532 | -0.019778
3 | 0.99844 | -0.010903 | 0.0012188 | 0.00030547
4 | 0.999 | -0.0069462 | 0 | 0
5 | 0.99838 | -0.011329 | 0 | 0
6 | 0.99793 | -0.014426 | 0.0012909 | 0.00032353
7 | 0.99885 | -0.0080328 | 0.0011025 | 0.0002763
8 | 0.99776 | -0.015678 | 0.0044896 | 0.0011252
9 | 0.99631 | -0.025798 | 0.0024491 | 0.00061381
10 | 0.99542 | -0.032052 | 0 | 0
11 | 0.99883 | -0.0081867 | 0.0019437 | 0.00048713
12 | 0.99772 | -0.015916 | 0.0012667 | 0.00031747
13 | 0.99503 | -0.034754 | 0.0026958 | 0.00067563
14 | 0.99416 | -0.040927 | 0 | 0
15 | 0.99506 | -0.034568 | 0.0022685 | 0.00056854
16 | 0.99388 | -0.042851 | 0.0023776 | 0.00059587
17 | 0.99404 | -0.041769 | 0.0023885 | 0.00059862
18 | 0.99484 | -0.036111 | 0.0024612 | 0.00061683
19 | 0.99415 | -0.040958 | 0.0023934 | 0.00059984
20 | 0.99311 | -0.048304 | 0 | 0
21 | 0.9924 | -0.053319 | 0.01673 | 0.0041928
22 | 0.99343 | -0.046071 | 0.0016858 | 0.00042251
23 | 0.99351 | -0.04551 | 0.0011518 | 0.00028866
24 | 0.99359 | -0.044943 | 0.002393 | 0.00059974
25 | 0.99369 | -0.044245 | 0.0014261 | 0.0003574
26 | 0.99384 | -0.043129 | 0.0013845 | 0.000347
27 | 0.99055 | -0.066327 | 0.0052372 | 0.0013126
28 | 0.99025 | -0.068499 | 0.0052288 | 0.0013105
29 | 0.99021 | -0.068729 | 0.0014044 | 0.00035197
30 | 0.99462 | -0.037683 | 0.0023562 | 0.00059053
31 | 0.99469 | -0.037155 | 0.0025415 | 0.00063696
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0058557 | -0.0014676 | 0.0058619 | 0.0014683 | 6.1666e-06 | 6.9239e-07 | 0.0087524 | 0.0087518 | 0.0087524 | 0.99555 | -0.031192 | 0.99663 | -0.023584 | 3.2416
1 | -0.0084006 | -0.0021045 | 0.0084095 | 0.0021068 | 8.9157e-06 | 2.2442e-06 | 0.012542 | 0.012542 | 0.012542 | 0.99663 | -0.023584 | 0.99772 | -0.015916 | 4.6452
2 | 0.039845 | 0.010008 | -0.039785 | -0.0099848 | 6.0308e-05 | 2.2835e-05 | 0.059298 | 0.059298 | 0.059298 | 1 | 0 | 0.99844 | -0.010903 | 21.9622
3 | 0.038887 | 0.0097707 | -0.038849 | -0.0097565 | 3.7548e-05 | 1.4206e-05 | 0.057873 | 0.057873 | 0.057873 | 1 | 0 | 0.999 | -0.0069462 | 21.4345
4 | 0.038566 | 0.0096794 | -0.038564 | -0.0096785 | 2.2819e-06 | 8.6317e-07 | 0.057482 | 0.057482 | 0.057482 | 0.99844 | -0.010903 | 0.99838 | -0.011329 | 21.2895
5 | 0.035803 | 0.0089935 | -0.035766 | -0.0089794 | 3.7202e-05 | 1.4034e-05 | 0.053335 | 0.053335 | 0.053335 | 0.999 | -0.0069462 | 0.99793 | -0.014426 | 19.7539
6 | 0.0030466 | 0.00076305 | -0.0030462 | -0.00076334 | 4.5787e-07 | -2.9038e-07 | 0.0045378 | 0.0045379 | 0.0045379 | 0.999 | -0.0069462 | 0.99885 | -0.0080328 | 1.6807
7 | 0.014175 | 0.0035524 | -0.014166 | -0.0035495 | 8.5286e-06 | 2.88e-06 | 0.021126 | 0.021126 | 0.021126 | 0.99838 | -0.011329 | 0.99776 | -0.015678 | 7.8246
8 | 0.024389 | 0.0061261 | -0.02434 | -0.006108 | 4.8974e-05 | 1.8061e-05 | 0.036355 | 0.036356 | 0.036356 | 0.99838 | -0.011329 | 0.99631 | -0.025798 | 13.465
9 | 0.034475 | 0.0086559 | -0.03439 | -0.0086242 | 8.4223e-05 | 3.1728e-05 | 0.051411 | 0.051411 | 0.051411 | 0.99793 | -0.014426 | 0.99542 | -0.032052 | 19.0411
10 | 0.0019437 | 0.00048704 | -0.0019437 | -0.00048713 | 4.1401e-08 | -8.7651e-08 | 0.0028956 | 0.0028956 | 0.0028956 | 0.99885 | -0.0080328 | 0.99883 | -0.0081867 | 1.0724
11 | 0.0096765 | 0.0024243 | -0.0096762 | -0.0024242 | 3.1891e-07 | 9.0607e-08 | 0.014431 | 0.014431 | 0.014431 | 0.99776 | -0.015678 | 0.99772 | -0.015916 | 5.3448
12 | 0.021891 | 0.0054942 | -0.021864 | -0.0054843 | 2.7187e-05 | 9.9265e-06 | 0.032698 | 0.032698 | 0.032698 | 0.99631 | -0.025798 | 0.99503 | -0.034754 | 12.1103
13 | 0.024757 | 0.0062103 | -0.024727 | -0.006199 | 3.0435e-05 | 1.1244e-05 | 0.037011 | 0.037011 | 0.037011 | 0.99542 | -0.032052 | 0.99416 | -0.040927 | 13.7077
14 | 0.0096332 | 0.0024139 | -0.0096299 | -0.002413 | 3.3534e-06 | 9.53e-07 | 0.0144 | 0.0144 | 0.0144 | 0.99542 | -0.032052 | 0.99506 | -0.034568 | 5.3335
15 | 0.019168 | 0.0048087 | -0.019152 | -0.0048027 | 1.6482e-05 | 5.922e-06 | 0.028666 | 0.028667 | 0.028667 | 0.99503 | -0.034754 | 0.99415 | -0.040958 | 10.6173
16 | 0.010424 | 0.0026117 | -0.010421 | -0.0026109 | 2.7749e-06 | 8.3045e-07 | 0.015602 | 0.015602 | 0.015602 | 0.99416 | -0.040927 | 0.99388 | -0.042851 | 5.7784
17 | 0.014303 | 0.0035873 | -0.014301 | -0.0035867 | 1.6704e-06 | 5.6674e-07 | 0.021409 | 0.021409 | 0.021409 | 0.99416 | -0.040927 | 0.99404 | -0.041769 | 7.9294
18 | 0.0073614 | 0.0018444 | -0.0073598 | -0.0018441 | 1.5722e-06 | 3.3465e-07 | 0.011008 | 0.011008 | 0.011008 | 0.99506 | -0.034568 | 0.99484 | -0.036111 | 4.0771
19 | 0.0080433 | 0.002015 | -0.008043 | -0.002015 | 3.085e-07 | 7.4473e-08 | 0.012042 | 0.012042 | 0.012042 | 0.99388 | -0.042851 | 0.99384 | -0.043129 | 4.46
20 | 0.011913 | 0.0029881 | -0.011872 | -0.0029752 | 4.046e-05 | 1.2928e-05 | 0.017834 | 0.017835 | 0.017835 | 0.99404 | -0.041769 | 0.99055 | -0.066327 | 6.6055
21 | 0.0048986 | 0.0012273 | -0.0048979 | -0.0012273 | 7.0721e-07 | -2.0762e-09 | 0.0073268 | 0.0073269 | 0.0073269 | 0.99484 | -0.036111 | 0.99469 | -0.037155 | 2.7137
22 | 0.016758 | 0.0042029 | -0.016741 | -0.0041969 | 1.705e-05 | 5.9952e-06 | 0.025084 | 0.025084 | 0.025084 | 0.99415 | -0.040958 | 0.99311 | -0.048304 | 9.2905
23 | 0.016741 | 0.0041969 | -0.01673 | -0.0041928 | 1.1622e-05 | 4.0872e-06 | 0.025084 | 0.025085 | 0.025085 | 0.99311 | -0.048304 | 0.9924 | -0.053319 | 9.2906
24 | -0.0016858 | -0.00042251 | 0.0016859 | 0.00042213 | 1.3069e-07 | -3.7507e-07 | 0.0025251 | 0.002525 | 0.0025251 | 0.99343 | -0.046071 | 0.99351 | -0.04551 | 0.93523
25 | -0.0028377 | -0.00071079 | 0.0028379 | 0.00071062 | 2.2254e-07 | -1.7011e-07 | 0.00425 | 0.0042499 | 0.00425 | 0.99351 | -0.04551 | 0.99359 | -0.044943 | 1.5741
26 | -0.0052309 | -0.0013104 | 0.0052314 | 0.0013104 | 5.0498e-07 | 2.3409e-08 | 0.0078337 | 0.0078336 | 0.0078337 | 0.99359 | -0.044943 | 0.99369 | -0.044245 | 2.9014
27 | -0.0066575 | -0.0016678 | 0.0066585 | 0.001668 | 1.0282e-06 | 1.8066e-07 | 0.0099691 | 0.009969 | 0.0099691 | 0.99369 | -0.044245 | 0.99384 | -0.043129 | 3.6923
28 | 0.0066352 | 0.0016626 | -0.0066333 | -0.0016622 | 1.9944e-06 | 3.5309e-07 | 0.0099674 | 0.0099675 | 0.0099675 | 0.99055 | -0.066327 | 0.99025 | -0.068499 | 3.6917
29 | 0.0014044 | 0.00035178 | -0.0014044 | -0.00035197 | 4.4674e-08 | -1.8962e-07 | 0.0021103 | 0.0021104 | 0.0021104 | 0.99025 | -0.068499 | 0.99021 | -0.068729 | 0.78162
30 | -0.0023562 | -0.00059053 | 0.0023564 | 0.00059031 | 1.7221e-07 | -2.2204e-07 | 0.0035251 | 0.003525 | 0.0035251 | 0.99462 | -0.037683 | 0.99469 | -0.037155 | 1.3056

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.086983 | 0.021646

## res_load
| p_mw | q_mvar
0 | 0.0058557 | 0.0014676
1 | 0.0025387 | 0.00063625
2 | 0.0074511 | 0.0018674
3 | 0.0012188 | 0.00030547
4 | 0.0012909 | 0.00032353
5 | 0.0011025 | 0.0002763
6 | 0.0044896 | 0.0011252
7 | 0.0024491 | 0.00061381
8 | 0.0019437 | 0.00048713
9 | 0.0012667 | 0.00031747
10 | 0.0026958 | 0.00067563
11 | 0.0022685 | 0.00056854
12 | 0.0023776 | 0.00059587
13 | 0.0023885 | 0.00059862
14 | 0.0024612 | 0.00061683
15 | 0.0023934 | 0.00059984
16 | 0.01673 | 0.0041928
17 | 0.0016858 | 0.00042251
18 | 0.0011518 | 0.00028866
19 | 0.002393 | 0.00059974
20 | 0.0014261 | 0.0003574
21 | 0.0013845 | 0.000347
22 | 0.0052372 | 0.0013126
23 | 0.0052288 | 0.0013105
24 | 0.0014044 | 0.00035197
25 | 0.0023562 | 0.00059053
26 | 0.0025415 | 0.00063696

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1