## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2102-3_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2102-3_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2102-3_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2102-3_0_7_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2102-3_0_7_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_2102-3_0_7_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_2102-3_0_7_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_2102-3_0_7_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_2102-3_0_7_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_2102-3_0_7_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_2102-3_0_7_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_2102-3_0_7_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_2102-3_0_7_node_27 | 0.4 | n |  | TRUE
13 | bus_LV_2102-3_0_7_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_2102-3_0_7_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_2102-3_0_7_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_2102-3_0_7_node_40 | 0.4 | n |  | TRUE
17 | bus_LV_2102-3_0_7_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_2102-3_0_7_node_41 | 0.4 | n |  | TRUE
19 | bus_LV_2102-3_0_7_node_42 | 0.4 | n |  | TRUE
20 | bus_LV_2102-3_0_7_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_2102-3_0_7_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_2102-3_0_7_node_110 | 0.4 | n |  | TRUE
23 | bus_LV_2102-3_0_7_node_3 | 0.4 | n |  | TRUE
24 | bus_LV_2102-3_0_7_node_114 | 0.4 | n |  | TRUE
25 | bus_LV_2102-3_0_7_node_113 | 0.4 | n |  | TRUE
26 | bus_LV_2102-3_0_7_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_2102-3_0_7_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_2102-3_0_7_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_2102-3_0_7_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_2102-3_0_7_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_2102-3_0_7_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_2102-3_0_7_node_86 | 0.4 | n |  | TRUE
33 | bus_LV_2102-3_0_7_node_112 | 0.4 | n |  | TRUE
34 | bus_LV_2102-3_0_7_node_9 | 0.4 | n |  | TRUE
35 | bus_LV_2102-3_0_7_node_10 | 0.4 | n |  | TRUE
36 | bus_LV_2102-3_0_7_node_127 | 0.4 | n |  | TRUE
37 | bus_LV_2102-3_0_7_node_15 | 0.4 | n |  | TRUE
38 | bus_LV_2102-3_0_7_node_16 | 0.4 | n |  | TRUE
39 | bus_LV_2102-3_0_7_node_17 | 0.4 | n |  | TRUE
40 | bus_LV_2102-3_0_7_node_18 | 0.4 | n |  | TRUE
41 | bus_LV_2102-3_0_7_node_14 | 0.4 | n |  | TRUE
42 | bus_LV_2102-3_0_7_node_19 | 0.4 | n |  | TRUE
43 | bus_LV_2102-3_0_7_node_20 | 0.4 | n |  | TRUE
44 | bus_LV_2102-3_0_7_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_2102-3_0_7_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_2102-3_0_7_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_2102-3_0_7_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_2102-3_0_7_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_2102-3_0_7_node_128 | 0.4 | n |  | TRUE
50 | bus_LV_2102-3_0_7_node_11 | 0.4 | n |  | TRUE
51 | bus_LV_2102-3_0_7_node_12 | 0.4 | n |  | TRUE
52 | bus_LV_2102-3_0_7_node_13 | 0.4 | n |  | TRUE
53 | bus_LV_2102-3_0_7_node_130 | 0.4 | n |  | TRUE
54 | bus_LV_2102-3_0_7_node_129 | 0.4 | n |  | TRUE
55 | bus_LV_2102-3_0_7_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_2102-3_0_7_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_2102-3_0_7_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_2102-3_0_7_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_2102-3_0_7_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_2102-3_0_7_node_57 | 0.4 | n |  | TRUE
61 | bus_LV_2102-3_0_7_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_2102-3_0_7_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_2102-3_0_7_node_55 | 0.4 | n |  | TRUE
64 | bus_LV_2102-3_0_7_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_2102-3_0_7_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_2102-3_0_7_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_2102-3_0_7_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_2102-3_0_7_node_62 | 0.4 | n |  | TRUE
69 | bus_LV_2102-3_0_7_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_2102-3_0_7_node_126 | 0.4 | n |  | TRUE
71 | bus_LV_2102-3_0_7_node_125 | 0.4 | n |  | TRUE
72 | bus_LV_2102-3_0_7_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_2102-3_0_7_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_2102-3_0_7_node_64 | 0.4 | n |  | TRUE
75 | bus_LV_2102-3_0_7_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_2102-3_0_7_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_2102-3_0_7_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_2102-3_0_7_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_2102-3_0_7_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_2102-3_0_7_node_71 | 0.4 | n |  | TRUE
81 | bus_LV_2102-3_0_7_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_2102-3_0_7_node_73 | 0.4 | n |  | TRUE
83 | bus_LV_2102-3_0_7_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_2102-3_0_7_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_2102-3_0_7_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_2102-3_0_7_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_2102-3_0_7_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_2102-3_0_7_node_79 | 0.4 | n |  | TRUE
89 | bus_LV_2102-3_0_7_node_80 | 0.4 | n |  | TRUE
90 | bus_LV_2102-3_0_7_node_85 | 0.4 | n |  | TRUE
91 | bus_LV_2102-3_0_7_node_82 | 0.4 | n |  | TRUE
92 | bus_LV_2102-3_0_7_node_115 | 0.4 | n |  | TRUE
93 | bus_LV_2102-3_0_7_node_88 | 0.4 | n |  | TRUE
94 | bus_LV_2102-3_0_7_node_81 | 0.4 | n |  | TRUE
95 | bus_LV_2102-3_0_7_node_116 | 0.4 | n |  | TRUE
96 | bus_LV_2102-3_0_7_node_117 | 0.4 | n |  | TRUE
97 | bus_LV_2102-3_0_7_node_83 | 0.4 | n |  | TRUE
98 | bus_LV_2102-3_0_7_node_84 | 0.4 | n |  | TRUE
99 | bus_LV_2102-3_0_7_node_87 | 0.4 | n |  | TRUE
100 | bus_LV_2102-3_0_7_node_97 | 0.4 | n |  | TRUE
101 | bus_LV_2102-3_0_7_node_89 | 0.4 | n |  | TRUE
102 | bus_LV_2102-3_0_7_node_107 | 0.4 | n |  | TRUE
103 | bus_LV_2102-3_0_7_node_95 | 0.4 | n |  | TRUE
104 | bus_LV_2102-3_0_7_node_90 | 0.4 | n |  | TRUE
105 | bus_LV_2102-3_0_7_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_2102-3_0_7_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_2102-3_0_7_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_2102-3_0_7_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_2102-3_0_7_node_105 | 0.4 | n |  | TRUE
110 | bus_LV_2102-3_0_7_node_94 | 0.4 | n |  | TRUE
111 | bus_LV_2102-3_0_7_node_96 | 0.4 | n |  | TRUE
112 | bus_LV_2102-3_0_7_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_2102-3_0_7_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_2102-3_0_7_node_99 | 0.4 | n |  | TRUE
115 | bus_LV_2102-3_0_7_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_2102-3_0_7_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_2102-3_0_7_node_102 | 0.4 | n |  | TRUE
118 | bus_LV_2102-3_0_7_node_103 | 0.4 | n |  | TRUE
119 | bus_LV_2102-3_0_7_node_123 | 0.4 | n |  | TRUE
120 | bus_LV_2102-3_0_7_node_104 | 0.4 | n |  | TRUE
121 | bus_LV_2102-3_0_7_node_124 | 0.4 | n |  | TRUE
122 | bus_LV_2102-3_0_7_node_109 | 0.4 | n |  | TRUE
123 | bus_LV_2102-3_0_7_node_111 | 0.4 | n |  | TRUE
124 | bus_LV_2102-3_0_7_node_120 | 0.4 | n |  | TRUE
125 | bus_LV_2102-3_0_7_node_118 | 0.4 | n |  | TRUE
126 | bus_LV_2102-3_0_7_node_121 | 0.4 | n |  | TRUE
127 | bus_LV_2102-3_0_7_node_119 | 0.4 | n |  | TRUE
128 | bus_LV_2102-3_0_7_node_122 | 0.4 | n |  | TRUE
129 | bus_MV_367_0_node_254 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2102-3_0_7_load_0 | 0 | 0.00023347 | 5.8513e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2102-3_0_7_load_2 | 2 | 0.0039842 | 0.00099854 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2102-3_0_7_load_4 | 3 | 0.0015357 | 0.00038488 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2102-3_0_7_load_7 | 5 | 0.0031187 | 0.00078163 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2102-3_0_7_load_8 | 6 | 0.0036244 | 0.00090836 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2102-3_0_7_load_22 | 7 | 0.0023203 | 0.00058151 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2102-3_0_7_load_24 | 8 | 0.0029259 | 0.00073331 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2102-3_0_7_load_21 | 9 | 0.002687 | 0.00067342 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2102-3_0_7_load_26 | 11 | 0.0016313 | 0.00040885 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2102-3_0_7_load_28 | 14 | 0.001286 | 0.00032229 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2102-3_0_7_load_30 | 15 | 0.0022368 | 0.0005606 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2102-3_0_7_load_40 | 16 | 0.0034287 | 0.0008593 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2102-3_0_7_load_41 | 18 | 0.0053955 | 0.0013522 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2102-3_0_7_load_42 | 19 | 0.0016505 | 0.00041365 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2102-3_0_7_load_39 | 20 | 0.0017684 | 0.00044319 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2102-3_0_7_load_43 | 21 | 0.0017185 | 0.00043071 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2102-3_0_7_load_110 | 22 | 0.0030481 | 0.00076392 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2102-3_0_7_load_114 | 24 | 0.0039622 | 0.00099303 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2102-3_0_7_load_113 | 25 | 0.0032146 | 0.00080566 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2102-3_0_7_load_31 | 27 | 0.0032719 | 0.00082001 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2102-3_0_7_load_32 | 28 | 0.0030398 | 0.00076185 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2102-3_0_7_load_34 | 29 | 0.0031005 | 0.00077707 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2102-3_0_7_load_38 | 30 | 0.0038871 | 0.00097419 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2102-3_0_7_load_86 | 32 | 0.0013887 | 0.00034803 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2102-3_0_7_load_112 | 33 | 0.0021827 | 0.00054703 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2102-3_0_7_load_10 | 35 | 0.0026409 | 0.00066186 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2102-3_0_7_load_127 | 36 | 0.0028994 | 0.00072666 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2102-3_0_7_load_15 | 37 | 0.0042959 | 0.0010766 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2102-3_0_7_load_19 | 42 | 0.0023666 | 0.00059314 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2102-3_0_7_load_20 | 43 | 0.0042919 | 0.0010757 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2102-3_0_7_load_33 | 44 | 0.0036631 | 0.00091805 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2102-3_0_7_load_23 | 46 | 0.0020007 | 0.00050143 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2102-3_0_7_load_46 | 47 | 0.0029798 | 0.00074682 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2102-3_0_7_load_45 | 48 | 0.0054799 | 0.0013734 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2102-3_0_7_load_11 | 50 | 0.0018243 | 0.00045722 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2102-3_0_7_load_12 | 51 | 0.0036251 | 0.00090854 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2102-3_0_7_load_13 | 52 | 0.0042103 | 0.0010552 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2102-3_0_7_load_130 | 53 | 0.0051165 | 0.0012823 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2102-3_0_7_load_48 | 55 | 0.00063992 | 0.00016038 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2102-3_0_7_load_49 | 56 | 0.0001691 | 4.2381e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2102-3_0_7_load_50 | 57 | 0.00011966 | 2.9989e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2102-3_0_7_load_54 | 58 | 0.00034059 | 8.536e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2102-3_0_7_load_53 | 59 | 0.001068 | 0.00026766 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2102-3_0_7_load_59 | 61 | 0.0011336 | 0.00028411 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2102-3_0_7_load_55 | 63 | 0.00081821 | 0.00020506 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2102-3_0_7_load_51 | 64 | 0.0008845 | 0.00022168 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2102-3_0_7_load_56 | 65 | 0.0001884 | 4.7217e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2102-3_0_7_load_58 | 66 | 0.00050523 | 0.00012662 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2102-3_0_7_load_60 | 67 | 0.0001493 | 3.7417e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2102-3_0_7_load_62 | 68 | 0.0001965 | 4.9248e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2102-3_0_7_load_61 | 69 | 0.0012067 | 0.00030244 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2102-3_0_7_load_125 | 71 | 0.00082062 | 0.00020567 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2102-3_0_7_load_63 | 72 | 0.0004069 | 0.00010198 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2102-3_0_7_load_65 | 73 | 0.00015281 | 3.8299e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2102-3_0_7_load_64 | 74 | 0.00076353 | 0.00019136 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2102-3_0_7_load_66 | 75 | 0.00027662 | 6.9327e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2102-3_0_7_load_67 | 76 | 0.0004628 | 0.00011599 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2102-3_0_7_load_68 | 77 | 0.00015713 | 3.9381e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2102-3_0_7_load_69 | 78 | 0.00046298 | 0.00011603 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2102-3_0_7_load_70 | 79 | 0.00053244 | 0.00013344 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2102-3_0_7_load_71 | 80 | 0.0068249 | 0.0017105 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2102-3_0_7_load_72 | 81 | 0.0028697 | 0.00071922 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2102-3_0_7_load_73 | 82 | 0.0035989 | 0.00090198 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2102-3_0_7_load_74 | 83 | 0.0033083 | 0.00082915 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2102-3_0_7_load_75 | 84 | 0.0031379 | 0.00078643 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2102-3_0_7_load_76 | 85 | 0.003517 | 0.00088144 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2102-3_0_7_load_77 | 86 | 0.0046825 | 0.0011735 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2102-3_0_7_load_80 | 89 | 0.0011751 | 0.0002945 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2102-3_0_7_load_85 | 90 | 0.00089151 | 0.00022343 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2102-3_0_7_load_82 | 91 | 0.0013121 | 0.00032885 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2102-3_0_7_load_88 | 93 | 0.0011723 | 0.0002938 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2102-3_0_7_load_81 | 94 | 0.00033766 | 8.4626e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2102-3_0_7_load_117 | 96 | 0.00349 | 0.00087468 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2102-3_0_7_load_83 | 97 | 0.0026023 | 0.0006522 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2102-3_0_7_load_87 | 99 | 0.0025748 | 0.0006453 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2102-3_0_7_load_89 | 101 | 0.0008687 | 0.00021772 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2102-3_0_7_load_107 | 102 | 0.0030934 | 0.00077528 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2102-3_0_7_load_90 | 104 | 0.00051195 | 0.00012831 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2102-3_0_7_load_92 | 106 | 0.0024508 | 0.00061422 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2102-3_0_7_load_93 | 107 | 0.0007664 | 0.00019208 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2102-3_0_7_load_106 | 108 | 0.0015022 | 0.00037649 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2102-3_0_7_load_94 | 110 | 0.003803 | 0.00095313 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2102-3_0_7_load_96 | 111 | 0.0019463 | 0.00048778 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2102-3_0_7_load_108 | 112 | 0.0024522 | 0.00061458 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2102-3_0_7_load_98 | 113 | 0.0013669 | 0.00034257 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2102-3_0_7_load_99 | 114 | 0.0060678 | 0.0015207 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2102-3_0_7_load_100 | 115 | 0.0037118 | 0.00093027 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2102-3_0_7_load_101 | 116 | 0.0012318 | 0.00030871 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2102-3_0_7_load_102 | 117 | 0.0069484 | 0.0017414 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2102-3_0_7_load_103 | 118 | 0.0011604 | 0.00029081 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2102-3_0_7_load_123 | 119 | 0.0012762 | 0.00031985 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2102-3_0_7_load_104 | 120 | 0.0015801 | 0.000396 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2102-3_0_7_load_124 | 121 | 0.00084368 | 0.00021145 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2102-3_0_7_load_109 | 122 | 0.0021386 | 0.00053598 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2102-3_0_7_load_111 | 123 | 0.0015487 | 0.00038815 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2102-3_0_7_load_120 | 124 | 0.0011653 | 0.00029205 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2102-3_0_7_load_118 | 125 | 0.0080026 | 0.0020056 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2102-3_0_7_load_121 | 126 | 0.0018841 | 0.00047221 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2102-3_0_7_load_119 | 127 | 0.0067471 | 0.001691 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2102-3_0_7_load_122 | 128 | 0.0041306 | 0.0010352 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2102-3_0_7_line_0 | NAYY 4x150 SE | 0 | 1 | 0.27822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2102-3_0_7_line_1 | NAYY 4x150 SE | 1 | 2 | 0.029887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2102-3_0_7_line_2 | NAYY 4x150 SE | 2 | 22 | 0.0392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2102-3_0_7_line_3 | NAYY 4x150 SE | 3 | 4 | 0.0020295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2102-3_0_7_line_4 | NAYY 4x150 SE | 4 | 5 | 0.019536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2102-3_0_7_line_5 | NAYY 4x150 SE | 5 | 6 | 0.030663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2102-3_0_7_line_6 | NAYY 4x150 SE | 6 | 34 | 0.021953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2102-3_0_7_line_7 | NAYY 4x150 SE | 7 | 8 | 0.0073456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2102-3_0_7_line_8 | NAYY 4x150 SE | 7 | 9 | 0.022112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2102-3_0_7_line_9 | NAYY 4x150 SE | 8 | 10 | 0.025392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2102-3_0_7_line_10 | NAYY 4x150 SE | 9 | 46 | 0.059323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2102-3_0_7_line_11 | NAYY 4x150 SE | 10 | 11 | 0.027273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2102-3_0_7_line_12 | NAYY 4x150 SE | 10 | 12 | 0.016751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2102-3_0_7_line_13 | NAYY 4x150 SE | 12 | 13 | 0.01669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2102-3_0_7_line_14 | NAYY 4x150 SE | 13 | 15 | 0.021683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2102-3_0_7_line_15 | NAYY 4x150 SE | 13 | 14 | 0.0078062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2102-3_0_7_line_16 | NAYY 4x150 SE | 16 | 17 | 0.05121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2102-3_0_7_line_17 | NAYY 4x150 SE | 17 | 20 | 0.019869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2102-3_0_7_line_18 | NAYY 4x150 SE | 17 | 29 | 0.016292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2102-3_0_7_line_19 | NAYY 4x150 SE | 18 | 19 | 0.01443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2102-3_0_7_line_20 | NAYY 4x150 SE | 18 | 20 | 0.041681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2102-3_0_7_line_21 | NAYY 4x150 SE | 19 | 21 | 0.020751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2102-3_0_7_line_22 | NAYY 4x150 SE | 22 | 32 | 0.036276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2102-3_0_7_line_23 | NAYY 4x150 SE | 23 | 24 | 0.02771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2102-3_0_7_line_24 | NAYY 4x150 SE | 23 | 25 | 0.017787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_2102-3_0_7_line_25 | NAYY 4x150 SE | 23 | 26 | 0.46122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_2102-3_0_7_line_26 | NAYY 4x150 SE | 25 | 33 | 0.029711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_2102-3_0_7_line_27 | NAYY 4x150 SE | 26 | 48 | 0.029031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_2102-3_0_7_line_28 | NAYY 4x150 SE | 27 | 28 | 0.025479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2102-3_0_7_line_29 | NAYY 4x150 SE | 28 | 44 | 0.027648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2102-3_0_7_line_30 | NAYY 4x150 SE | 29 | 31 | 0.033497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2102-3_0_7_line_31 | NAYY 4x150 SE | 30 | 31 | 0.05715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2102-3_0_7_line_32 | NAYY 4x150 SE | 31 | 45 | 0.010983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2102-3_0_7_line_33 | NAYY 4x150 SE | 32 | 98 | 0.023577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2102-3_0_7_line_34 | NAYY 4x150 SE | 33 | 123 | 0.0017149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_2102-3_0_7_line_35 | NAYY 4x150 SE | 34 | 35 | 0.016261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2102-3_0_7_line_36 | NAYY 4x150 SE | 35 | 36 | 0.0074047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2102-3_0_7_line_37 | NAYY 4x150 SE | 36 | 49 | 0.042338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2102-3_0_7_line_38 | NAYY 4x150 SE | 37 | 38 | 0.03205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_2102-3_0_7_line_39 | NAYY 4x150 SE | 37 | 39 | 0.0078253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_2102-3_0_7_line_40 | NAYY 4x150 SE | 38 | 40 | 0.021196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_2102-3_0_7_line_41 | NAYY 4x150 SE | 38 | 41 | 0.050749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2102-3_0_7_line_42 | NAYY 4x150 SE | 39 | 42 | 0.022757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2102-3_0_7_line_43 | NAYY 4x150 SE | 39 | 43 | 0.022156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_2102-3_0_7_line_44 | NAYY 4x150 SE | 40 | 53 | 0.0376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_2102-3_0_7_line_45 | NAYY 4x150 SE | 40 | 46 | 0.014063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2102-3_0_7_line_46 | NAYY 4x150 SE | 41 | 51 | 0.03366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2102-3_0_7_line_47 | NAYY 4x150 SE | 42 | 44 | 0.0010205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2102-3_0_7_line_48 | NAYY 4x150 SE | 43 | 45 | 0.017634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_2102-3_0_7_line_49 | NAYY 4x150 SE | 45 | 47 | 0.038855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_2102-3_0_7_line_50 | NAYY 4x150 SE | 47 | 48 | 0.0022991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_2102-3_0_7_line_51 | NAYY 4x150 SE | 49 | 54 | 0.009136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2102-3_0_7_line_52 | NAYY 4x150 SE | 50 | 51 | 0.031701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2102-3_0_7_line_53 | NAYY 4x150 SE | 50 | 52 | 0.017834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2102-3_0_7_line_54 | NAYY 4x150 SE | 53 | 54 | 0.031229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2102-3_0_7_line_55 | NAYY 4x150 SE | 55 | 56 | 0.0052537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2102-3_0_7_line_56 | NAYY 4x150 SE | 56 | 57 | 0.011481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2102-3_0_7_line_57 | NAYY 4x150 SE | 57 | 58 | 0.088255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2102-3_0_7_line_58 | NAYY 4x150 SE | 58 | 59 | 0.0017389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2102-3_0_7_line_59 | NAYY 4x150 SE | 59 | 64 | 0.054482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2102-3_0_7_line_60 | NAYY 4x150 SE | 60 | 61 | 0.0095783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2102-3_0_7_line_61 | NAYY 4x150 SE | 60 | 62 | 0.069887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2102-3_0_7_line_62 | NAYY 4x150 SE | 60 | 63 | 0.030083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2102-3_0_7_line_63 | NAYY 4x150 SE | 61 | 68 | 0.026576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2102-3_0_7_line_64 | NAYY 4x150 SE | 62 | 64 | 0.02391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2102-3_0_7_line_65 | NAYY 4x150 SE | 63 | 65 | 0.028959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2102-3_0_7_line_66 | NAYY 4x150 SE | 65 | 66 | 0.029573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2102-3_0_7_line_67 | NAYY 4x150 SE | 66 | 67 | 0.12856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2102-3_0_7_line_68 | NAYY 4x150 SE | 67 | 69 | 0.031916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2102-3_0_7_line_69 | NAYY 4x150 SE | 68 | 72 | 0.023993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2102-3_0_7_line_70 | NAYY 4x150 SE | 69 | 70 | 0.24288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2102-3_0_7_line_71 | NAYY 4x150 SE | 70 | 71 | 0.01628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2102-3_0_7_line_72 | NAYY 4x150 SE | 72 | 73 | 0.014974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2102-3_0_7_line_73 | NAYY 4x150 SE | 73 | 74 | 0.0075389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2102-3_0_7_line_74 | NAYY 4x150 SE | 74 | 75 | 0.01899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2102-3_0_7_line_75 | NAYY 4x150 SE | 75 | 76 | 0.026335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2102-3_0_7_line_76 | NAYY 4x150 SE | 76 | 77 | 0.0068263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2102-3_0_7_line_77 | NAYY 4x150 SE | 77 | 78 | 0.010392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2102-3_0_7_line_78 | NAYY 4x150 SE | 78 | 79 | 0.02798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2102-3_0_7_line_79 | NAYY 4x150 SE | 79 | 80 | 0.058612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2102-3_0_7_line_80 | NAYY 4x150 SE | 80 | 81 | 0.01038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2102-3_0_7_line_81 | NAYY 4x150 SE | 81 | 82 | 0.017945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2102-3_0_7_line_82 | NAYY 4x150 SE | 82 | 83 | 0.018741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2102-3_0_7_line_83 | NAYY 4x150 SE | 83 | 84 | 0.033108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2102-3_0_7_line_84 | NAYY 4x150 SE | 84 | 85 | 0.0010012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2102-3_0_7_line_85 | NAYY 4x150 SE | 85 | 86 | 0.021321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2102-3_0_7_line_86 | NAYY 4x150 SE | 86 | 87 | 0.028487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2102-3_0_7_line_87 | NAYY 4x150 SE | 87 | 88 | 0.011287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2102-3_0_7_line_88 | NAYY 4x150 SE | 87 | 89 | 0.026262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2102-3_0_7_line_89 | NAYY 4x150 SE | 88 | 90 | 0.035982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2102-3_0_7_line_90 | NAYY 4x150 SE | 88 | 91 | 0.022836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
91 | LV_2102-3_0_7_line_91 | NAYY 4x150 SE | 89 | 92 | 0.026997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2102-3_0_7_line_92 | NAYY 4x150 SE | 90 | 93 | 0.0067088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2102-3_0_7_line_93 | NAYY 4x150 SE | 91 | 94 | 0.0086407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_2102-3_0_7_line_94 | NAYY 4x150 SE | 92 | 95 | 0.014554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2102-3_0_7_line_95 | NAYY 4x150 SE | 92 | 96 | 0.035461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2102-3_0_7_line_96 | NAYY 4x150 SE | 93 | 101 | 0.011398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2102-3_0_7_line_97 | NAYY 4x150 SE | 94 | 97 | 0.026598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_2102-3_0_7_line_98 | NAYY 4x150 SE | 95 | 124 | 0.057802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2102-3_0_7_line_99 | NAYY 4x150 SE | 95 | 125 | 0.028596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2102-3_0_7_line_100 | NAYY 4x150 SE | 97 | 98 | 0.051205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_2102-3_0_7_line_101 | NAYY 4x150 SE | 98 | 99 | 0.045476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_2102-3_0_7_line_102 | NAYY 4x150 SE | 99 | 100 | 0.014372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_2102-3_0_7_line_103 | NAYY 4x150 SE | 100 | 102 | 0.023613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_2102-3_0_7_line_104 | NAYY 4x150 SE | 100 | 103 | 0.010507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2102-3_0_7_line_105 | NAYY 4x150 SE | 101 | 104 | 0.021766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2102-3_0_7_line_106 | NAYY 4x150 SE | 102 | 112 | 0.022108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_2102-3_0_7_line_107 | NAYY 4x150 SE | 103 | 110 | 0.018122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2102-3_0_7_line_108 | NAYY 4x150 SE | 104 | 105 | 0.013152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2102-3_0_7_line_109 | NAYY 4x150 SE | 105 | 106 | 0.032925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2102-3_0_7_line_110 | NAYY 4x150 SE | 105 | 107 | 0.01695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2102-3_0_7_line_111 | NAYY 4x150 SE | 107 | 108 | 0.027973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2102-3_0_7_line_112 | NAYY 4x150 SE | 108 | 109 | 0.014503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2102-3_0_7_line_113 | NAYY 4x150 SE | 109 | 117 | 0.013279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2102-3_0_7_line_114 | NAYY 4x150 SE | 110 | 111 | 0.022777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2102-3_0_7_line_115 | NAYY 4x150 SE | 112 | 122 | 1.7163e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
116 | LV_2102-3_0_7_line_116 | NAYY 4x150 SE | 113 | 114 | 0.02042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2102-3_0_7_line_117 | NAYY 4x150 SE | 113 | 115 | 0.0093142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2102-3_0_7_line_118 | NAYY 4x150 SE | 114 | 116 | 0.0060264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2102-3_0_7_line_119 | NAYY 4x150 SE | 115 | 117 | 0.0247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2102-3_0_7_line_120 | NAYY 4x150 SE | 116 | 118 | 0.025592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2102-3_0_7_line_121 | NAYY 4x150 SE | 117 | 119 | 0.29598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2102-3_0_7_line_122 | NAYY 4x150 SE | 118 | 120 | 0.0036108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2102-3_0_7_line_123 | NAYY 4x150 SE | 119 | 121 | 0.0068262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2102-3_0_7_line_124 | NAYY 4x150 SE | 122 | 123 | 0.026424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
125 | LV_2102-3_0_7_line_125 | NAYY 4x150 SE | 124 | 126 | 0.028867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_2102-3_0_7_line_126 | NAYY 4x150 SE | 125 | 127 | 0.016506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_2102-3_0_7_line_127 | NAYY 4x150 SE | 126 | 128 | 0.095079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2102-3_0_7_trafo_3 | 0.25 MVA 20/0.4 kV | 129 | 23 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2554345.3474 | 1165627.8121 | 2554079.4634 | 1165709.7435
1 | 2554345.3474 | 1165627.8121 | 2554348.1037 | 1165632.8159 | 2554362.8849 | 1165651.9447
2 | 2554386.9083 | 1165682.9198 | 2554383.784 | 1165678.9909 | 2554362.8849 | 1165651.9447
3 | 2553988.0543 | 1165042.3128 | 2553986.4054 | 1165043.4961
4 | 2553988.0543 | 1165042.3128 | 2554003.9289 | 1165030.9262
5 | 2554003.9289 | 1165030.9262 | 2554028.8452 | 1165013.0541
6 | 2554047.269 | 1165001.126 | 2554031.9666 | 1165010.8151 | 2554028.8452 | 1165013.0541
7 | 2554030.2646 | 1165092.3061 | 2554024.3807 | 1165096.7035
8 | 2554030.2646 | 1165092.3061 | 2554047.9764 | 1165079.0688
9 | 2554004.0414 | 1165111.9045 | 2554024.3807 | 1165096.7035
10 | 2554096.625 | 1165045.1293 | 2554054.674 | 1165074.0632 | 2554047.9764 | 1165079.0688
11 | 2554004.0414 | 1165111.9045 | 2553997.7508 | 1165109.4181 | 2553978.2501 | 1165115.769
12 | 2553990.394 | 1165121.6588 | 2553995.4758 | 1165118.3069 | 2554004.0414 | 1165111.9045
13 | 2553990.394 | 1165121.6588 | 2553994.5382 | 1165137.8244
14 | 2553994.5382 | 1165137.8244 | 2554009.7327 | 1165141.0762 | 2554014.7268 | 1165140.2597 | 2554015.6185 | 1165139.6432
15 | 2553994.5382 | 1165137.8244 | 2553993.245 | 1165141.9254 | 2553990.3658 | 1165143.9263
16 | 2554080.6316 | 1165166.802 | 2554076.0142 | 1165175.8088 | 2554050.9532 | 1165201.0251 | 2554046.8406 | 1165204.7329
17 | 2554080.6316 | 1165166.802 | 2554064.0937 | 1165177.8153
18 | 2554080.6316 | 1165166.802 | 2554094.1898 | 1165157.7685
19 | 2554028.6114 | 1165199.6831 | 2554016.3099 | 1165207.2263
20 | 2554064.0937 | 1165177.8153 | 2554062.0041 | 1165179.2068 | 2554028.6114 | 1165199.6831
21 | 2553998.6198 | 1165218.0738 | 2554016.3099 | 1165207.2263
22 | 2554409.4873 | 1165711.313 | 2554386.9083 | 1165682.9198
23 | 2554394.0287 | 1165596.4696 | 2554418.3909 | 1165583.2669
24 | 2554394.0287 | 1165596.4696 | 2554401.4255 | 1165599.515 | 2554407.6041 | 1165607.1059
25 | 2554394.0287 | 1165596.4696 | 2554164.4092 | 1165196.4767
26 | 2554426.3593 | 1165630.1484 | 2554407.6041 | 1165607.1059
27 | 2554164.4092 | 1165196.4767 | 2554150.8005 | 1165170.8326
28 | 2554056.8627 | 1165142.1551 | 2554067.2483 | 1165130.0852 | 2554075.2675 | 1165124.8881
29 | 2554098.4691 | 1165109.8517 | 2554075.2675 | 1165124.8881
30 | 2554122.5808 | 1165140.0002 | 2554101.0723 | 1165153.1828 | 2554094.1898 | 1165157.7685
31 | 2554094.8698 | 1165188.182 | 2554096.5562 | 1165177.419 | 2554101.2028 | 1165167.2225 | 2554119.373 | 1165148.0845 | 2554122.5808 | 1165140.0002
32 | 2554122.5808 | 1165140.0002 | 2554131.9632 | 1165134.2476
33 | 2554424.1616 | 1165729.7661 | 2554409.4873 | 1165711.313
34 | 2554427.4418 | 1165631.4784 | 2554426.3593 | 1165630.1484
35 | 2554047.269 | 1165001.126 | 2554061.0079 | 1164992.4275
36 | 2554067.2641 | 1164988.4665 | 2554061.0079 | 1164992.4275
37 | 2554103.9157 | 1164967.4857 | 2554092.8943 | 1164972.2392 | 2554067.2641 | 1164988.4665
38 | 2554109.1814 | 1165058.1375 | 2554116.0115 | 1165088.0898 | 2554116.3614 | 1165089.3715
39 | 2554118.4223 | 1165096.9205 | 2554116.3614 | 1165089.3715
40 | 2554109.1814 | 1165058.1375 | 2554110.0589 | 1165047.7253 | 2554108.2013 | 1165037.1451
41 | 2554109.1814 | 1165058.1375 | 2554155.8373 | 1165037.8589
42 | 2554118.4223 | 1165096.9205 | 2554099.3254 | 1165109.2968
43 | 2554118.4223 | 1165096.9205 | 2554122.4249 | 1165111.6198 | 2554125.1135 | 1165117.9981
44 | 2554108.2013 | 1165037.1451 | 2554109.666 | 1165022.415 | 2554112.1625 | 1164999.7546
45 | 2554108.2013 | 1165037.1451 | 2554096.625 | 1165045.1293
46 | 2554155.8373 | 1165037.8589 | 2554169.528 | 1165068.6085
47 | 2554099.3254 | 1165109.2968 | 2554098.4691 | 1165109.8517
48 | 2554131.9632 | 1165134.2476 | 2554125.1135 | 1165117.9981
49 | 2554131.9632 | 1165134.2476 | 2554139.5081 | 1165149.5535 | 2554149.7227 | 1165168.8017
50 | 2554150.8005 | 1165170.8326 | 2554149.7227 | 1165168.8017
51 | 2554103.9157 | 1164967.4857 | 2554104.9116 | 1164968.5453 | 2554106.9341 | 1164969.6526 | 2554108.7972 | 1164969.9496 | 2554110.7244 | 1164969.6236 | 2554112.1205 | 1164968.9348
52 | 2554183.4427 | 1165096.979 | 2554175.6538 | 1165080.7411 | 2554174.3107 | 1165079.3506 | 2554169.528 | 1165068.6085
53 | 2554183.4427 | 1165096.979 | 2554188.4156 | 1165107.3464 | 2554194.2606 | 1165104.9019
54 | 2554112.1205 | 1164968.9348 | 2554113.7854 | 1164973.3466 | 2554114.0697 | 1164976.4794 | 2554113.7258 | 1164985.5646 | 2554112.1625 | 1164999.7546
55 | 2553989.3669 | 1166069.2077 | 2553994.4253 | 1166067.7884
56 | 2554005.4798 | 1166064.6868 | 2553994.4253 | 1166067.7884
57 | 2554075.507 | 1166010.9742 | 2554005.4798 | 1166064.6868
58 | 2554075.507 | 1166010.9742 | 2554077.1629 | 1166011.5051
59 | 2554119.6453 | 1166045.615 | 2554077.1629 | 1166011.5051
60 | 2554211.2111 | 1166025.2772 | 2554220.5608 | 1166023.1971
61 | 2554211.2111 | 1166025.2772 | 2554142.9862 | 1166040.4288
62 | 2554211.2111 | 1166025.2772 | 2554216.6124 | 1166054.8718
63 | 2554220.5608 | 1166023.1971 | 2554226.2686 | 1166021.9272 | 2554245.8085 | 1166015.0073
64 | 2554142.9862 | 1166040.4288 | 2554119.6453 | 1166045.615
65 | 2554216.6124 | 1166054.8718 | 2554217.3401 | 1166058.8592 | 2554226.6674 | 1166081.9519
66 | 2554226.6674 | 1166081.9519 | 2554228.4685 | 1166086.411 | 2554239.3221 | 1166099.057 | 2554244.9607 | 1166104.8701
67 | 2554244.9607 | 1166104.8701 | 2554279.5541 | 1166228.6932
68 | 2554289.5497 | 1166258.9691 | 2554282.4732 | 1166235.5774 | 2554279.5541 | 1166228.6932
69 | 2554245.8085 | 1166015.0073 | 2554268.4255 | 1166006.9976
70 | 2554289.5497 | 1166258.9691 | 2554161.5726 | 1166465.3993
71 | 2554161.5726 | 1166465.3993 | 2554152.0731 | 1166465.5831 | 2554147.9511 | 1166465.1588 | 2554145.433 | 1166464.3817
72 | 2554268.4255 | 1166006.9976 | 2554268.4255 | 1166006.9976 | 2554279.3334 | 1165996.7386
73 | 2554284.825 | 1165991.5736 | 2554279.3334 | 1165996.7386
74 | 2554284.825 | 1165991.5736 | 2554298.6582 | 1165978.5633
75 | 2554314.9877 | 1165957.9022 | 2554298.6582 | 1165978.5633 | 2554298.6582 | 1165978.5633
76 | 2554314.9877 | 1165957.9022 | 2554319.2204 | 1165952.5466
77 | 2554319.2204 | 1165952.5466 | 2554325.6642 | 1165944.3935
78 | 2554325.6642 | 1165944.3935 | 2554343.0137 | 1165922.4417
79 | 2554343.0137 | 1165922.4417 | 2554367.5001 | 1165891.4598 | 2554381.7697 | 1165878.7306
80 | 2554381.7697 | 1165878.7306 | 2554389.5158 | 1165871.8205
81 | 2554389.5158 | 1165871.8205 | 2554397.4027 | 1165864.785 | 2554404.2339 | 1165862.0024
82 | 2554404.2339 | 1165862.0024 | 2554421.5901 | 1165854.9327
83 | 2554452.2523 | 1165842.4429 | 2554421.5901 | 1165854.9327
84 | 2554453.1795 | 1165842.0652 | 2554452.2523 | 1165842.4429
85 | 2554453.1795 | 1165842.0652 | 2554458.4205 | 1165839.9304 | 2554472.9756 | 1165834.1471
86 | 2554497.485 | 1165819.8233 | 2554479.2143 | 1165831.6682 | 2554472.9756 | 1165834.1471
87 | 2554497.485 | 1165819.8233 | 2554497.0973 | 1165811.1105 | 2554497.9748 | 1165808.7026
88 | 2554497.485 | 1165819.8233 | 2554514.3307 | 1165816.9384 | 2554523.5013 | 1165816.8528
89 | 2554497.9748 | 1165808.7026 | 2554500.4425 | 1165801.9359 | 2554508.279 | 1165793.3608 | 2554521.8715 | 1165784.5308 | 2554522.67 | 1165784.0084
90 | 2554497.9748 | 1165808.7026 | 2554488.207 | 1165804.9414 | 2554479.521 | 1165796.1356
91 | 2554549.8083 | 1165821.5607 | 2554533.4479 | 1165816.76 | 2554523.5013 | 1165816.8528
92 | 2554522.67 | 1165784.0084 | 2554528.2838 | 1165780.3351
93 | 2554473.7159 | 1165789.7467 | 2554476.2779 | 1165792.8478 | 2554479.521 | 1165796.1356
94 | 2554549.8083 | 1165821.5607 | 2554561.6032 | 1165830.1314
95 | 2554549.8083 | 1165821.5607 | 2554584.8651 | 1165826.896
96 | 2554537.8211 | 1165774.0946 | 2554528.2838 | 1165780.3351
97 | 2554473.7159 | 1165789.7467 | 2554456.7749 | 1165769.2413
98 | 2554561.6032 | 1165830.1314 | 2554562.2422 | 1165830.5934 | 2554594.8519 | 1165857.8941 | 2554603.8364 | 1165869.2553
99 | 2554561.6032 | 1165830.1314 | 2554552.7076 | 1165841.4158 | 2554547.0277 | 1165850.6749 | 2554548.1848 | 1165853.8344
100 | 2554424.1616 | 1165729.7661 | 2554456.7749 | 1165769.2413
101 | 2554424.1616 | 1165729.7661 | 2554458.2185 | 1165699.6291
102 | 2554468.9816 | 1165690.1048 | 2554458.2185 | 1165699.6291
103 | 2554468.9816 | 1165690.1048 | 2554457.9291 | 1165669.2383
104 | 2554468.9816 | 1165690.1048 | 2554476.861 | 1165683.1302
105 | 2554537.8211 | 1165774.0946 | 2554556.0348 | 1165762.1768
106 | 2554457.9291 | 1165669.2383 | 2554457.469 | 1165668.3697 | 2554444.1333 | 1165651.9855
107 | 2554476.861 | 1165683.1302 | 2554482.9177 | 1165688.1869 | 2554488.1396 | 1165696.9862
108 | 2554567.5638 | 1165755.8805 | 2554559.0517 | 1165760.2028 | 2554556.0348 | 1165762.1768
109 | 2554567.5638 | 1165755.8805 | 2554554.2348 | 1165725.7657
110 | 2554567.5638 | 1165755.8805 | 2554582.6743 | 1165748.2009
111 | 2554608.2914 | 1165736.9732 | 2554584.5728 | 1165747.236 | 2554582.6743 | 1165748.2009
112 | 2554621.6019 | 1165731.2139 | 2554608.2914 | 1165736.9732
113 | 2554621.6019 | 1165731.2139 | 2554622.9499 | 1165721.154 | 2554621.513 | 1165718.3744
114 | 2554499.7638 | 1165716.5739 | 2554488.1396 | 1165696.9862
115 | 2554444.1225 | 1165651.9722 | 2554444.1333 | 1165651.9855
116 | 2554605.8933 | 1165688.1588 | 2554596.516 | 1165670.0189
117 | 2554605.8933 | 1165688.1588 | 2554610.1705 | 1165696.4328
118 | 2554593.7486 | 1165664.6655 | 2554596.516 | 1165670.0189
119 | 2554610.1705 | 1165696.4328 | 2554621.513 | 1165718.3744
120 | 2554593.7486 | 1165664.6655 | 2554581.9967 | 1165641.9318
121 | 2554621.513 | 1165718.3744 | 2554897.1691 | 1165610.5996
122 | 2554581.9967 | 1165641.9318 | 2554580.3385 | 1165638.7242
123 | 2554897.1691 | 1165610.5996 | 2554903.0737 | 1165607.1743
124 | 2554444.1225 | 1165651.9722 | 2554427.4418 | 1165631.4784
125 | 2554621.7398 | 1165891.8993 | 2554615.3535 | 1165883.8192 | 2554603.8364 | 1165869.2553
126 | 2554560.7918 | 1165864.4889 | 2554548.1848 | 1165853.8344
127 | 2554621.7398 | 1165891.8993 | 2554677.7345 | 1165968.7404

## bus_geodata
| x | y | coords
0 | 2554079.4634 | 1165709.7435
1 | 2554345.3474 | 1165627.8121
2 | 2554362.8849 | 1165651.9447
3 | 2553986.4054 | 1165043.4961
4 | 2553988.0543 | 1165042.3128
5 | 2554003.9289 | 1165030.9262
6 | 2554028.8452 | 1165013.0541
7 | 2554030.2646 | 1165092.3061
8 | 2554024.3807 | 1165096.7035
9 | 2554047.9764 | 1165079.0688
10 | 2554004.0414 | 1165111.9045
11 | 2553978.2501 | 1165115.769
12 | 2553990.394 | 1165121.6588
13 | 2553994.5382 | 1165137.8244
14 | 2553990.3658 | 1165143.9263
15 | 2554015.6185 | 1165139.6432
16 | 2554046.8406 | 1165204.7328
17 | 2554080.6316 | 1165166.802
18 | 2554028.6114 | 1165199.6831
19 | 2554016.3099 | 1165207.2263
20 | 2554064.0937 | 1165177.8153
21 | 2553998.6198 | 1165218.0738
22 | 2554386.9083 | 1165682.9198
23 | 2554394.0287 | 1165596.4696
24 | 2554418.3909 | 1165583.2669
25 | 2554407.6041 | 1165607.1059
26 | 2554164.4092 | 1165196.4767
27 | 2554056.8627 | 1165142.1551
28 | 2554075.2675 | 1165124.8881
29 | 2554094.1898 | 1165157.7685
30 | 2554094.8698 | 1165188.182
31 | 2554122.5808 | 1165140.0002
32 | 2554409.4873 | 1165711.313
33 | 2554426.3593 | 1165630.1484
34 | 2554047.269 | 1165001.126
35 | 2554061.0079 | 1164992.4275
36 | 2554067.2641 | 1164988.4665
37 | 2554116.3614 | 1165089.3715
38 | 2554109.1814 | 1165058.1375
39 | 2554118.4223 | 1165096.9205
40 | 2554108.2013 | 1165037.1451
41 | 2554155.8373 | 1165037.8589
42 | 2554099.3254 | 1165109.2968
43 | 2554125.1136 | 1165117.9981
44 | 2554098.4691 | 1165109.8517
45 | 2554131.9632 | 1165134.2476
46 | 2554096.625 | 1165045.1293
47 | 2554149.7227 | 1165168.8017
48 | 2554150.8005 | 1165170.8326
49 | 2554103.9157 | 1164967.4857
50 | 2554183.4427 | 1165096.9791
51 | 2554169.528 | 1165068.6085
52 | 2554194.2606 | 1165104.9019
53 | 2554112.1625 | 1164999.7546
54 | 2554112.1205 | 1164968.9348
55 | 2553989.3669 | 1166069.2077
56 | 2553994.4253 | 1166067.7884
57 | 2554005.4798 | 1166064.6868
58 | 2554075.507 | 1166010.9742
59 | 2554077.1629 | 1166011.5051
60 | 2554211.2111 | 1166025.2772
61 | 2554220.5608 | 1166023.1971
62 | 2554142.9862 | 1166040.4288
63 | 2554216.6124 | 1166054.8718
64 | 2554119.6453 | 1166045.615
65 | 2554226.6674 | 1166081.9519
66 | 2554244.9607 | 1166104.8701
67 | 2554279.5541 | 1166228.6932
68 | 2554245.8085 | 1166015.0073
69 | 2554289.5497 | 1166258.9691
70 | 2554161.5726 | 1166465.3993
71 | 2554145.433 | 1166464.3817
72 | 2554268.4255 | 1166006.9976
73 | 2554279.3334 | 1165996.7386
74 | 2554284.825 | 1165991.5736
75 | 2554298.6582 | 1165978.5633
76 | 2554314.9877 | 1165957.9022
77 | 2554319.2204 | 1165952.5466
78 | 2554325.6642 | 1165944.3935
79 | 2554343.0137 | 1165922.4417
80 | 2554381.7697 | 1165878.7306
81 | 2554389.5158 | 1165871.8205
82 | 2554404.2339 | 1165862.0024
83 | 2554421.5901 | 1165854.9327
84 | 2554452.2523 | 1165842.4429
85 | 2554453.1795 | 1165842.0652
86 | 2554472.9756 | 1165834.1471
87 | 2554497.485 | 1165819.8233
88 | 2554497.9748 | 1165808.7026
89 | 2554523.5013 | 1165816.8528
90 | 2554522.67 | 1165784.0084
91 | 2554479.521 | 1165796.1356
92 | 2554549.8083 | 1165821.5607
93 | 2554528.2838 | 1165780.3351
94 | 2554473.7159 | 1165789.7467
95 | 2554561.6032 | 1165830.1314
96 | 2554584.8651 | 1165826.896
97 | 2554456.7749 | 1165769.2413
98 | 2554424.1616 | 1165729.7661
99 | 2554458.2185 | 1165699.6291
100 | 2554468.9816 | 1165690.1048
101 | 2554537.8211 | 1165774.0946
102 | 2554457.9291 | 1165669.2383
103 | 2554476.861 | 1165683.1302
104 | 2554556.0348 | 1165762.1768
105 | 2554567.5638 | 1165755.8805
106 | 2554554.2348 | 1165725.7657
107 | 2554582.6743 | 1165748.2009
108 | 2554608.2914 | 1165736.9732
109 | 2554621.6019 | 1165731.2139
110 | 2554488.1396 | 1165696.9862
111 | 2554499.7638 | 1165716.5739
112 | 2554444.1333 | 1165651.9855
113 | 2554605.8933 | 1165688.1588
114 | 2554596.516 | 1165670.0189
115 | 2554610.1705 | 1165696.4328
116 | 2554593.7486 | 1165664.6655
117 | 2554621.513 | 1165718.3744
118 | 2554581.9967 | 1165641.9318
119 | 2554897.1691 | 1165610.5996
120 | 2554580.3385 | 1165638.7242
121 | 2554903.0737 | 1165607.1743
122 | 2554444.1225 | 1165651.9722
123 | 2554427.4418 | 1165631.4784
124 | 2554603.8364 | 1165869.2553
125 | 2554548.1848 | 1165853.8344
126 | 2554621.7398 | 1165891.8993
127 | 2554560.7918 | 1165864.4889
128 | 2554677.7345 | 1165968.7404
129 | 2554345.3474 | 1165627.8121

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98827 | -0.081752 | 0.00023347 | 5.8513e-05
1 | 0.98837 | -0.08105 | 0 | 0
2 | 0.98838 | -0.080971 | 0.0039842 | 0.00099854
3 | 0.9703 | -0.20888 | 0.0015357 | 0.00038488
4 | 0.97031 | -0.20885 | 0 | 0
5 | 0.97035 | -0.20853 | 0.0031187 | 0.00078163
6 | 0.97056 | -0.20702 | 0.0036244 | 0.00090836
7 | 0.97156 | -0.19984 | 0.0023203 | 0.00058151
8 | 0.97147 | -0.20047 | 0.0029259 | 0.00073331
9 | 0.97189 | -0.19741 | 0.002687 | 0.00067342
10 | 0.97128 | -0.20186 | 0 | 0
11 | 0.97121 | -0.20233 | 0.0016313 | 0.00040885
12 | 0.97119 | -0.20248 | 0 | 0
13 | 0.9711 | -0.20311 | 0 | 0
14 | 0.97109 | -0.20321 | 0.001286 | 0.00032229
15 | 0.97103 | -0.20362 | 0.0022368 | 0.0005606
16 | 0.97401 | -0.18219 | 0.0034287 | 0.0008593
17 | 0.97427 | -0.18034 | 0 | 0
18 | 0.97343 | -0.18639 | 0.0053955 | 0.0013522
19 | 0.97335 | -0.1869 | 0.0016505 | 0.00041365
20 | 0.97396 | -0.18254 | 0.0017684 | 0.00044319
21 | 0.9733 | -0.18728 | 0.0017185 | 0.00043071
22 | 0.98861 | -0.079269 | 0.0030481 | 0.00076392
23 | 1 | 0 | -0.23795 | -0.060022
24 | 0.99984 | -0.0010963 | 0.0039622 | 0.00099303
25 | 0.99884 | -0.0079688 | 0.0032146 | 0.00080566
26 | 0.97883 | -0.1477 | 0 | 0
27 | 0.97376 | -0.18397 | 0.0032719 | 0.00082001
28 | 0.97388 | -0.1831 | 0.0030398 | 0.00076185
29 | 0.9746 | -0.17795 | 0.0031005 | 0.00077707
30 | 0.97511 | -0.17427 | 0.0038871 | 0.00097419
31 | 0.97544 | -0.17194 | 0 | 0
32 | 0.98899 | -0.076566 | 0.0013887 | 0.00034803
33 | 0.99696 | -0.021001 | 0.0021827 | 0.00054703
34 | 0.97083 | -0.20509 | 0 | 0
35 | 0.97102 | -0.20366 | 0.0026409 | 0.00066186
36 | 0.97114 | -0.20281 | 0.0028994 | 0.00072666
37 | 0.97438 | -0.17952 | 0.0042959 | 0.0010766
38 | 0.9737 | -0.18443 | 0 | 0
39 | 0.97456 | -0.1782 | 0 | 0
40 | 0.97334 | -0.18697 | 0 | 0
41 | 0.97298 | -0.1896 | 0 | 0
42 | 0.97415 | -0.18115 | 0.0023666 | 0.00059314
43 | 0.97522 | -0.17351 | 0.0042919 | 0.0010757
44 | 0.97414 | -0.18126 | 0.0036631 | 0.00091805
45 | 0.97577 | -0.16952 | 0 | 0
46 | 0.97303 | -0.18921 | 0.0020007 | 0.00050143
47 | 0.9774 | -0.15791 | 0.0029798 | 0.00074682
48 | 0.9775 | -0.1572 | 0.0054799 | 0.0013734
49 | 0.972 | -0.19662 | 0 | 0
50 | 0.97222 | -0.19505 | 0.0018243 | 0.00045722
51 | 0.9725 | -0.19303 | 0.0036251 | 0.00090854
52 | 0.97211 | -0.19585 | 0.0042103 | 0.0010552
53 | 0.97282 | -0.19072 | 0.0051165 | 0.0012823
54 | 0.97219 | -0.19528 | 0 | 0
55 | 0.97258 | -0.19365 | 0.00063992 | 0.00016038
56 | 0.97258 | -0.19362 | 0.0001691 | 4.2381e-05
57 | 0.97259 | -0.19352 | 0.00011966 | 2.9989e-05
58 | 0.97271 | -0.19265 | 0.00034059 | 8.536e-05
59 | 0.97272 | -0.19262 | 0.001068 | 0.00026766
60 | 0.97335 | -0.18807 | 0 | 0
61 | 0.97344 | -0.18737 | 0.0011336 | 0.00028411
62 | 0.97302 | -0.19046 | 0 | 0
63 | 0.97318 | -0.18925 | 0.00081821 | 0.00020506
64 | 0.9729 | -0.19127 | 0.0008845 | 0.00022168
65 | 0.97306 | -0.19014 | 0.0001884 | 4.7217e-05
66 | 0.97295 | -0.19099 | 0.00050523 | 0.00012662
67 | 0.97254 | -0.19399 | 0.0001493 | 3.7417e-05
68 | 0.97376 | -0.18509 | 0.0001965 | 4.9248e-05
69 | 0.97244 | -0.19468 | 0.0012067 | 0.00030244
70 | 0.97215 | -0.19682 | 0 | 0
71 | 0.97213 | -0.19696 | 0.00082062 | 0.00020567
72 | 0.97405 | -0.183 | 0.0004069 | 0.00010198
73 | 0.97424 | -0.18162 | 0.00015281 | 3.8299e-05
74 | 0.97433 | -0.18092 | 0.00076353 | 0.00019136
75 | 0.9746 | -0.17899 | 0.00027662 | 6.9327e-05
76 | 0.97498 | -0.17625 | 0.0004628 | 0.00011599
77 | 0.97508 | -0.1755 | 0.00015713 | 3.9381e-05
78 | 0.97524 | -0.17435 | 0.00046298 | 0.00011603
79 | 0.97569 | -0.17112 | 0.00053244 | 0.00013344
80 | 0.97667 | -0.16404 | 0.0068249 | 0.0017105
81 | 0.97695 | -0.16204 | 0.0028697 | 0.00071922
82 | 0.9775 | -0.15806 | 0.0035989 | 0.00090198
83 | 0.97818 | -0.1532 | 0.0033083 | 0.00082915
84 | 0.97954 | -0.14349 | 0.0031379 | 0.00078643
85 | 0.97958 | -0.14316 | 0.003517 | 0.00088144
86 | 0.98066 | -0.13545 | 0.0046825 | 0.0011735
87 | 0.9823 | -0.12379 | 0 | 0
88 | 0.98339 | -0.11608 | 0 | 0
89 | 0.98128 | -0.13103 | 0.0011751 | 0.0002945
90 | 0.98169 | -0.12814 | 0.00089151 | 0.00022343
91 | 0.98502 | -0.10449 | 0.0013121 | 0.00032885
92 | 0.98029 | -0.13816 | 0 | 0
93 | 0.98138 | -0.13033 | 0.0011723 | 0.0002938
94 | 0.98544 | -0.10153 | 0.00033766 | 8.4626e-05
95 | 0.97982 | -0.14148 | 0 | 0
96 | 0.98011 | -0.13945 | 0.00349 | 0.00087468
97 | 0.98674 | -0.092416 | 0.0026023 | 0.0006522
98 | 0.98929 | -0.074475 | 0 | 0
99 | 0.99174 | -0.05728 | 0.0025748 | 0.0006453
100 | 0.99254 | -0.051738 | 0 | 0
101 | 0.98088 | -0.13391 | 0.0008687 | 0.00021772
102 | 0.99391 | -0.042194 | 0.0030934 | 0.00077528
103 | 0.99245 | -0.05235 | 0 | 0
104 | 0.97994 | -0.14057 | 0.00051195 | 0.00012831
105 | 0.97939 | -0.14453 | 0 | 0
106 | 0.97927 | -0.14537 | 0.0024508 | 0.00061422
107 | 0.97873 | -0.14921 | 0.0007664 | 0.00019208
108 | 0.97768 | -0.15671 | 0.0015022 | 0.00037649
109 | 0.97717 | -0.16038 | 0 | 0
110 | 0.9923 | -0.053407 | 0.003803 | 0.00095313
111 | 0.99224 | -0.053857 | 0.0019463 | 0.00048778
112 | 0.99522 | -0.033051 | 0.0024522 | 0.00061458
113 | 0.976 | -0.16877 | 0.0013669 | 0.00034257
114 | 0.9757 | -0.17092 | 0.0060678 | 0.0015207
115 | 0.97616 | -0.16766 | 0.0037118 | 0.00093027
116 | 0.97567 | -0.17117 | 0.0012318 | 0.00030871
117 | 0.9767 | -0.16375 | 0.0069484 | 0.0017414
118 | 0.97556 | -0.17191 | 0.0011604 | 0.00029081
119 | 0.97579 | -0.17036 | 0.0012762 | 0.00031985
120 | 0.97556 | -0.17197 | 0.0015801 | 0.000396
121 | 0.97578 | -0.17042 | 0.00084368 | 0.00021145
122 | 0.99522 | -0.033044 | 0.0021386 | 0.00053598
123 | 0.99685 | -0.021742 | 0.0015487 | 0.00038815
124 | 0.97922 | -0.14581 | 0.0011653 | 0.00029205
125 | 0.97921 | -0.14587 | 0.0080026 | 0.0020056
126 | 0.97896 | -0.14762 | 0.0018841 | 0.00047221
127 | 0.97905 | -0.14703 | 0.0067471 | 0.001691
128 | 0.97839 | -0.15171 | 0.0041306 | 0.0010352
129 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00023347 | -5.8513e-05 | 0.00023349 | 5.4956e-05 | 2.1378e-08 | -3.5571e-06 | 0.00035153 | 0.0003503 | 0.00035153 | 0.98827 | -0.081752 | 0.98837 | -0.08105 | 0.1302
1 | -0.00023349 | -5.4956e-05 | 0.00023349 | 5.4574e-05 | 2.2877e-09 | -3.8215e-07 | 0.0003503 | 0.00035017 | 0.0003503 | 0.98837 | -0.08105 | 0.98838 | -0.080971 | 0.12974
2 | -0.0042177 | -0.0010531 | 0.0042187 | 0.001053 | 9.858e-07 | -1.2335e-07 | 0.0063484 | 0.0063483 | 0.0063484 | 0.98838 | -0.080971 | 0.98861 | -0.079269 | 2.3513
3 | -0.0015357 | -0.00038488 | 0.0015357 | 0.00038486 | 7.024e-09 | -2.2367e-08 | 0.0023551 | 0.0023551 | 0.0023551 | 0.9703 | -0.20888 | 0.97031 | -0.20885 | 0.87225
4 | -0.0015357 | -0.00038486 | 0.0015358 | 0.00038464 | 6.761e-08 | -2.1531e-07 | 0.0023551 | 0.002355 | 0.0023551 | 0.97031 | -0.20885 | 0.97035 | -0.20853 | 0.87225
5 | -0.0046545 | -0.0011663 | 0.0046555 | 0.0011663 | 9.7473e-07 | -3.9623e-09 | 0.0071375 | 0.0071374 | 0.0071375 | 0.97035 | -0.20853 | 0.97056 | -0.20702 | 2.6435
6 | -0.0082799 | -0.0020746 | 0.0082821 | 0.0020752 | 2.2074e-06 | 5.7763e-07 | 0.012694 | 0.012694 | 0.012694 | 0.97056 | -0.20702 | 0.97083 | -0.20509 | 4.7015
7 | 0.0080826 | 0.0020245 | -0.0080819 | -0.0020243 | 7.0237e-07 | 1.7919e-07 | 0.012379 | 0.012379 | 0.012379 | 0.97156 | -0.19984 | 0.97147 | -0.20047 | 4.5847
8 | -0.010403 | -0.002606 | 0.010406 | 0.0026071 | 3.5024e-06 | 1.0732e-06 | 0.015932 | 0.015932 | 0.015932 | 0.97156 | -0.19984 | 0.97189 | -0.19741 | 5.9009
9 | 0.005156 | 0.001291 | -0.005155 | -0.001291 | 9.8815e-07 | 6.5733e-08 | 0.0078971 | 0.0078972 | 0.0078972 | 0.97147 | -0.20047 | 0.97128 | -0.20186 | 2.9249
10 | -0.013093 | -0.0032805 | 0.013108 | 0.0032855 | 1.4875e-05 | 4.9853e-06 | 0.020046 | 0.020046 | 0.020046 | 0.97189 | -0.19741 | 0.97303 | -0.18921 | 7.4245
11 | 0.0016314 | 0.00040855 | -0.0016313 | -0.00040885 | 1.0631e-07 | -2.9663e-07 | 0.0024993 | 0.0024994 | 0.0024994 | 0.97128 | -0.20186 | 0.97121 | -0.20233 | 0.9257
12 | 0.0035236 | 0.00088242 | -0.0035233 | -0.00088251 | 3.0457e-07 | -9.0157e-08 | 0.0053979 | 0.005398 | 0.005398 | 0.97128 | -0.20186 | 0.97119 | -0.20248 | 1.9993
13 | 0.0035233 | 0.00088251 | -0.003523 | -0.0008826 | 3.0347e-07 | -8.9789e-08 | 0.005398 | 0.0053981 | 0.0053981 | 0.97119 | -0.20248 | 0.9711 | -0.20311 | 1.9993
14 | 0.002237 | 0.00056039 | -0.0022368 | -0.0005606 | 1.5896e-07 | -2.071e-07 | 0.0034276 | 0.0034277 | 0.0034277 | 0.9711 | -0.20311 | 0.97103 | -0.20362 | 1.2695
15 | 0.001286 | 0.00032221 | -0.001286 | -0.00032229 | 1.8914e-08 | -8.9303e-08 | 0.0019705 | 0.0019705 | 0.0019705 | 0.9711 | -0.20311 | 0.97109 | -0.20321 | 0.72982
16 | -0.0034287 | -0.0008593 | 0.0034295 | 0.000859 | 8.7671e-07 | -3.0034e-07 | 0.005238 | 0.0052378 | 0.005238 | 0.97401 | -0.18219 | 0.97427 | -0.18034 | 1.94
17 | 0.010541 | 0.0026418 | -0.010538 | -0.0026408 | 3.2137e-06 | 9.8868e-07 | 0.0161 | 0.0161 | 0.0161 | 0.97427 | -0.18034 | 0.97396 | -0.18254 | 5.9628
18 | -0.013971 | -0.0035008 | 0.013975 | 0.0035023 | 4.6285e-06 | 1.5772e-06 | 0.021337 | 0.021337 | 0.021337 | 0.97427 | -0.18034 | 0.9746 | -0.17795 | 7.9027
19 | 0.0033693 | 0.00084404 | -0.0033691 | -0.00084413 | 2.3886e-07 | -8.7504e-08 | 0.0051504 | 0.0051504 | 0.0051504 | 0.97343 | -0.18639 | 0.97335 | -0.1869 | 1.9076
20 | -0.0087649 | -0.0021963 | 0.0087695 | 0.0021976 | 4.6689e-06 | 1.2773e-06 | 0.013398 | 0.013398 | 0.013398 | 0.97343 | -0.18639 | 0.97396 | -0.18254 | 4.9623
21 | 0.0017186 | 0.00043048 | -0.0017185 | -0.00043071 | 8.9382e-08 | -2.2353e-07 | 0.0026273 | 0.0026274 | 0.0026274 | 0.97335 | -0.1869 | 0.9733 | -0.18728 | 0.9731
22 | -0.0072668 | -0.0018169 | 0.0072695 | 0.0018175 | 2.7072e-06 | 5.7593e-07 | 0.010936 | 0.010936 | 0.010936 | 0.98861 | -0.079269 | 0.98899 | -0.076566 | 4.0504
23 | 0.0039628 | 0.00099289 | -0.0039622 | -0.00099303 | 6.0122e-07 | -1.3224e-07 | 0.0058966 | 0.0058968 | 0.0058968 | 1 | 0 | 0.99984 | -0.0010963 | 2.184
24 | 0.13666 | 0.034539 | -0.13651 | -0.03448 | 0.00015315 | 5.8204e-05 | 0.20346 | 0.20346 | 0.20346 | 1 | 0 | 0.99884 | -0.0079688 | 25.1184
25 | 0.096523 | 0.02449 | -0.094541 | -0.023746 | 0.001982 | 0.00074453 | 0.14373 | 0.14374 | 0.14374 | 1 | 0 | 0.97883 | -0.1477 | 17.7457
26 | 0.1333 | 0.033675 | -0.13305 | -0.033582 | 0.00024392 | 9.2649e-05 | 0.19867 | 0.19867 | 0.19867 | 0.99884 | -0.0079688 | 0.99696 | -0.021001 | 24.5272
27 | 0.094541 | 0.023746 | -0.094416 | -0.023699 | 0.00012476 | 4.6892e-05 | 0.14374 | 0.14374 | 0.14374 | 0.97883 | -0.1477 | 0.9775 | -0.1572 | 17.7457
28 | -0.0032719 | -0.00082001 | 0.0032723 | 0.00081985 | 3.9743e-07 | -1.6414e-07 | 0.0049998 | 0.0049997 | 0.0049998 | 0.97376 | -0.18397 | 0.97388 | -0.1831 | 1.8518
29 | -0.0063121 | -0.0015817 | 0.0063137 | 0.001582 | 1.6046e-06 | 2.7306e-07 | 0.0096443 | 0.0096442 | 0.0096443 | 0.97388 | -0.1831 | 0.97414 | -0.18126 | 3.572
30 | -0.017076 | -0.0042794 | 0.01709 | 0.0042844 | 1.4207e-05 | 5.0466e-06 | 0.026071 | 0.026071 | 0.026071 | 0.9746 | -0.17795 | 0.97544 | -0.17194 | 9.656
31 | -0.0038871 | -0.00097419 | 0.0038883 | 0.00097396 | 1.2547e-06 | -2.3058e-07 | 0.0059317 | 0.0059314 | 0.0059317 | 0.97511 | -0.17427 | 0.97544 | -0.17194 | 2.1969
32 | -0.020978 | -0.0052584 | 0.020985 | 0.005261 | 7.0189e-06 | 2.5625e-06 | 0.032002 | 0.032002 | 0.032002 | 0.97544 | -0.17194 | 0.97577 | -0.16952 | 11.8528
33 | -0.0086582 | -0.0021655 | 0.0086607 | 0.0021662 | 2.496e-06 | 6.5736e-07 | 0.013025 | 0.013025 | 0.013025 | 0.98899 | -0.076566 | 0.98929 | -0.074475 | 4.8242
34 | 0.13087 | 0.033035 | -0.13086 | -0.03303 | 1.3621e-05 | 5.1716e-06 | 0.19541 | 0.19541 | 0.19541 | 0.99696 | -0.021001 | 0.99685 | -0.021742 | 24.1251
35 | -0.0082821 | -0.0020752 | 0.0082837 | 0.0020756 | 1.635e-06 | 4.2775e-07 | 0.012694 | 0.012694 | 0.012694 | 0.97083 | -0.20509 | 0.97102 | -0.20366 | 4.7015
36 | -0.010925 | -0.0027375 | 0.010926 | 0.0027379 | 1.2949e-06 | 4.0644e-07 | 0.016741 | 0.016741 | 0.016741 | 0.97102 | -0.20366 | 0.97114 | -0.20281 | 6.2003
37 | -0.013825 | -0.0034646 | 0.013837 | 0.0034686 | 1.1855e-05 | 4.0353e-06 | 0.021183 | 0.021183 | 0.021183 | 0.97114 | -0.20281 | 0.972 | -0.19662 | 7.8457
38 | 0.043804 | 0.010985 | -0.043774 | -0.010975 | 2.9833e-05 | 1.0278e-05 | 0.066897 | 0.066897 | 0.066897 | 0.97438 | -0.17952 | 0.9737 | -0.18443 | 8.2589
39 | -0.0481 | -0.012061 | 0.048108 | 0.012065 | 8.7828e-06 | 3.0855e-06 | 0.073457 | 0.073457 | 0.073457 | 0.97438 | -0.17952 | 0.97456 | -0.1782 | 9.0688
40 | 0.0341 | 0.00855 | -0.034088 | -0.0085462 | 1.1974e-05 | 3.8147e-06 | 0.052114 | 0.052114 | 0.052114 | 0.9737 | -0.18443 | 0.97334 | -0.18697 | 6.4339
41 | 0.0096734 | 0.0024246 | -0.0096665 | -0.0024225 | 6.9207e-06 | 2.0311e-06 | 0.014783 | 0.014783 | 0.014783 | 0.9737 | -0.18443 | 0.97298 | -0.1896 | 5.4753
42 | 0.012349 | 0.0030949 | -0.012344 | -0.0030932 | 5.0481e-06 | 1.6581e-06 | 0.018855 | 0.018855 | 0.018855 | 0.97456 | -0.1782 | 0.97415 | -0.18115 | 6.9832
43 | -0.060457 | -0.015159 | 0.060496 | 0.015174 | 3.9271e-05 | 1.4275e-05 | 0.092312 | 0.092311 | 0.092312 | 0.97456 | -0.1782 | 0.97522 | -0.17351 | 11.3965
44 | 0.018975 | 0.0047576 | -0.018965 | -0.0047548 | 9.8721e-06 | 2.8628e-06 | 0.029009 | 0.029009 | 0.029009 | 0.97334 | -0.18697 | 0.97282 | -0.19072 | 5.3721
45 | 0.015114 | 0.0037886 | -0.015109 | -0.0037869 | 4.6848e-06 | 1.6271e-06 | 0.023106 | 0.023106 | 0.023106 | 0.97334 | -0.18697 | 0.97303 | -0.18921 | 8.5576
46 | 0.0096665 | 0.0024225 | -0.0096619 | -0.0024212 | 4.5903e-06 | 1.3477e-06 | 0.014783 | 0.014783 | 0.014783 | 0.97298 | -0.1896 | 0.9725 | -0.19303 | 5.4754
47 | 0.0099769 | 0.0025001 | -0.0099768 | -0.0025 | 1.4789e-07 | 4.4175e-08 | 0.01524 | 0.01524 | 0.01524 | 0.97415 | -0.18115 | 0.97414 | -0.18126 | 5.6443
48 | -0.064788 | -0.016249 | 0.064824 | 0.016262 | 3.5848e-05 | 1.3127e-05 | 0.09886 | 0.09886 | 0.09886 | 0.97522 | -0.17351 | 0.97577 | -0.16952 | 12.2049
49 | -0.085809 | -0.021523 | 0.085948 | 0.021575 | 0.0001384 | 5.1773e-05 | 0.13086 | 0.13086 | 0.13086 | 0.97577 | -0.16952 | 0.9774 | -0.15791 | 16.1558
50 | -0.088928 | -0.022322 | 0.088936 | 0.022325 | 8.767e-06 | 3.2855e-06 | 0.1354 | 0.1354 | 0.1354 | 0.9774 | -0.15791 | 0.9775 | -0.1572 | 16.7158
51 | -0.013837 | -0.0034686 | 0.01384 | 0.0034695 | 2.5581e-06 | 8.7063e-07 | 0.021183 | 0.021183 | 0.021183 | 0.972 | -0.19662 | 0.97219 | -0.19528 | 7.8456
52 | -0.0060351 | -0.0015124 | 0.0060368 | 0.0015126 | 1.6877e-06 | 2.559e-07 | 0.0092368 | 0.0092367 | 0.0092368 | 0.97222 | -0.19505 | 0.9725 | -0.19303 | 3.4211
53 | 0.0042107 | 0.0010552 | -0.0042103 | -0.0010552 | 4.622e-07 | -4.3354e-08 | 0.0064446 | 0.0064447 | 0.0064447 | 0.97222 | -0.19505 | 0.97211 | -0.19585 | 2.3869
54 | 0.013848 | 0.0034724 | -0.01384 | -0.0034695 | 8.7441e-06 | 2.9757e-06 | 0.021183 | 0.021183 | 0.021183 | 0.97282 | -0.19072 | 0.97219 | -0.19528 | 7.8456
55 | -0.00063992 | -0.00016038 | 0.00063992 | 0.00016032 | 3.1424e-09 | -6.3988e-08 | 0.00097906 | 0.00097904 | 0.00097906 | 0.97258 | -0.19365 | 0.97258 | -0.19362 | 0.36262
56 | -0.00080903 | -0.0002027 | 0.00080904 | 0.00020256 | 1.0976e-08 | -1.3826e-07 | 0.0012378 | 0.0012377 | 0.0012378 | 0.97258 | -0.19362 | 0.97259 | -0.19352 | 0.45843
57 | -0.00092869 | -0.00023255 | 0.00092881 | 0.00023149 | 1.1114e-07 | -1.0526e-06 | 0.0014208 | 0.0014204 | 0.0014208 | 0.97259 | -0.19352 | 0.97271 | -0.19265 | 0.52621
58 | -0.0012694 | -0.00031685 | 0.0012694 | 0.00031683 | 4.0896e-09 | -2.0012e-08 | 0.0019414 | 0.0019414 | 0.0019414 | 0.97271 | -0.19265 | 0.97272 | -0.19262 | 0.71904
59 | -0.0023374 | -0.00058449 | 0.0023378 | 0.00058398 | 4.345e-07 | -5.0931e-07 | 0.0035751 | 0.0035749 | 0.0035751 | 0.97272 | -0.19262 | 0.9729 | -0.19127 | 1.3241
60 | -0.0069148 | -0.0017242 | 0.0069155 | 0.0017243 | 6.675e-07 | 1.3767e-07 | 0.010568 | 0.010568 | 0.010568 | 0.97335 | -0.18807 | 0.97344 | -0.18737 | 3.914
61 | 0.0032237 | 0.00080504 | -0.0032227 | -0.0008055 | 1.0588e-06 | -4.6111e-07 | 0.0049273 | 0.0049276 | 0.0049276 | 0.97335 | -0.18807 | 0.97302 | -0.19046 | 1.825
62 | 0.0036911 | 0.00091911 | -0.0036905 | -0.00091926 | 5.9728e-07 | -1.4413e-07 | 0.0056406 | 0.0056408 | 0.0056408 | 0.97335 | -0.18807 | 0.97318 | -0.18925 | 2.0892
63 | -0.0080491 | -0.0020084 | 0.0080516 | 0.002009 | 2.5092e-06 | 6.3459e-07 | 0.012301 | 0.012301 | 0.012301 | 0.97344 | -0.18737 | 0.97376 | -0.18509 | 4.5558
64 | 0.0032227 | 0.0008055 | -0.0032223 | -0.00080566 | 3.6228e-07 | -1.5761e-07 | 0.0049276 | 0.0049277 | 0.0049277 | 0.97302 | -0.19046 | 0.9729 | -0.19127 | 1.8251
65 | 0.0028723 | 0.00071419 | -0.0028719 | -0.00071442 | 3.4822e-07 | -2.2584e-07 | 0.0043897 | 0.0043899 | 0.0043899 | 0.97318 | -0.18925 | 0.97306 | -0.19014 | 1.6259
66 | 0.0026835 | 0.0006672 | -0.0026832 | -0.00066745 | 3.1048e-07 | -2.4789e-07 | 0.0041018 | 0.0041019 | 0.0041019 | 0.97306 | -0.19014 | 0.97295 | -0.19099 | 1.5192
67 | 0.002178 | 0.00054083 | -0.0021771 | -0.00054208 | 8.8932e-07 | -1.2539e-06 | 0.0033292 | 0.0033298 | 0.0033298 | 0.97295 | -0.19099 | 0.97254 | -0.19399 | 1.2332
68 | 0.0020278 | 0.00050466 | -0.0020276 | -0.00050499 | 1.9156e-07 | -3.2232e-07 | 0.0031013 | 0.0031015 | 0.0031015 | 0.97254 | -0.19399 | 0.97244 | -0.19468 | 1.1487
69 | -0.0082481 | -0.0020583 | 0.0082505 | 0.0020589 | 2.3773e-06 | 6.1577e-07 | 0.012601 | 0.012601 | 0.012601 | 0.97376 | -0.18509 | 0.97405 | -0.183 | 4.667
70 | 0.00082087 | 0.00020255 | -0.00082064 | -0.00020547 | 2.3889e-07 | -2.9204e-06 | 0.001255 | 0.001256 | 0.001256 | 0.97244 | -0.19468 | 0.97215 | -0.19682 | 0.4652
71 | 0.00082064 | 0.00020547 | -0.00082062 | -0.00020567 | 1.6028e-08 | -1.9569e-07 | 0.001256 | 0.0012561 | 0.0012561 | 0.97215 | -0.19682 | 0.97213 | -0.19696 | 0.46522
72 | -0.0086574 | -0.0021609 | 0.008659 | 0.0021613 | 1.6336e-06 | 4.4189e-07 | 0.013222 | 0.013222 | 0.013222 | 0.97405 | -0.183 | 0.97424 | -0.18162 | 4.8972
73 | -0.0088118 | -0.0021996 | 0.0088127 | 0.0021999 | 8.5174e-07 | 2.3371e-07 | 0.013456 | 0.013456 | 0.013456 | 0.97424 | -0.18162 | 0.97433 | -0.18092 | 4.9836
74 | -0.0095762 | -0.0023912 | 0.0095787 | 0.002392 | 2.5334e-06 | 7.3782e-07 | 0.014622 | 0.014622 | 0.014622 | 0.97433 | -0.18092 | 0.9746 | -0.17899 | 5.4155
75 | -0.0098554 | -0.0024613 | 0.0098591 | 0.0024624 | 3.7191e-06 | 1.1021e-06 | 0.015044 | 0.015044 | 0.015044 | 0.9746 | -0.17899 | 0.97498 | -0.17625 | 5.5719
76 | -0.010322 | -0.0025784 | 0.010323 | 0.0025787 | 1.0567e-06 | 3.2128e-07 | 0.01575 | 0.01575 | 0.01575 | 0.97498 | -0.17625 | 0.97508 | -0.1755 | 5.8334
77 | -0.01048 | -0.0026181 | 0.010482 | 0.0026186 | 1.658e-06 | 5.0804e-07 | 0.01599 | 0.01599 | 0.01599 | 0.97508 | -0.1755 | 0.97524 | -0.17435 | 5.9222
78 | -0.010945 | -0.0027346 | 0.01095 | 0.0027361 | 4.8672e-06 | 1.5227e-06 | 0.016696 | 0.016696 | 0.016696 | 0.97524 | -0.17435 | 0.97569 | -0.17112 | 6.1838
79 | -0.011482 | -0.0028696 | 0.011493 | 0.0028732 | 1.1211e-05 | 3.5792e-06 | 0.017508 | 0.017508 | 0.017508 | 0.97569 | -0.17112 | 0.97667 | -0.16404 | 6.4845
80 | -0.018318 | -0.0045836 | 0.018323 | 0.0045855 | 5.0442e-06 | 1.8101e-06 | 0.027906 | 0.027906 | 0.027906 | 0.97667 | -0.16404 | 0.97695 | -0.16204 | 10.3356
81 | -0.021193 | -0.0053047 | 0.021205 | 0.0053089 | 1.1666e-05 | 4.262e-06 | 0.032277 | 0.032277 | 0.032277 | 0.97695 | -0.16204 | 0.9775 | -0.15806 | 11.9545
82 | -0.024803 | -0.0062109 | 0.02482 | 0.0062171 | 1.667e-05 | 6.1764e-06 | 0.037755 | 0.037755 | 0.037755 | 0.9775 | -0.15806 | 0.97818 | -0.1532 | 13.9835
83 | -0.028129 | -0.0070462 | 0.028166 | 0.0070604 | 3.7824e-05 | 1.4131e-05 | 0.042788 | 0.042788 | 0.042788 | 0.97818 | -0.1532 | 0.97954 | -0.14349 | 15.8474
84 | -0.031304 | -0.0078468 | 0.031306 | 0.0078473 | 1.4128e-06 | 5.3079e-07 | 0.047555 | 0.047555 | 0.047555 | 0.97954 | -0.14349 | 0.97958 | -0.14316 | 17.6129
85 | -0.034823 | -0.0087288 | 0.03486 | 0.0087428 | 3.7227e-05 | 1.4049e-05 | 0.052897 | 0.052897 | 0.052897 | 0.97958 | -0.14316 | 0.98066 | -0.13545 | 19.5915
86 | -0.039542 | -0.0099164 | 0.039606 | 0.0099406 | 6.3998e-05 | 2.4255e-05 | 0.060002 | 0.060002 | 0.060002 | 0.98066 | -0.13545 | 0.9823 | -0.12379 | 22.223
87 | -0.066282 | -0.016633 | 0.066353 | 0.01666 | 7.1014e-05 | 2.717e-05 | 0.10041 | 0.10041 | 0.10041 | 0.9823 | -0.12379 | 0.98339 | -0.11608 | 37.1901
88 | 0.026676 | 0.0066922 | -0.026649 | -0.0066823 | 2.6762e-05 | 9.961e-06 | 0.040411 | 0.040411 | 0.040411 | 0.9823 | -0.12379 | 0.98128 | -0.13103 | 14.9672
89 | 0.032556 | 0.0081796 | -0.032502 | -0.0081591 | 5.4505e-05 | 2.0508e-05 | 0.04927 | 0.04927 | 0.04927 | 0.98339 | -0.11608 | 0.98169 | -0.12814 | 18.2482
90 | -0.098909 | -0.02484 | 0.099069 | 0.0249 | 0.00015963 | 6.0816e-05 | 0.14968 | 0.14968 | 0.14968 | 0.98339 | -0.11608 | 0.98502 | -0.10449 | 27.7191
91 | 0.025474 | 0.0063877 | -0.025449 | -0.0063784 | 2.5139e-05 | 9.3281e-06 | 0.03863 | 0.03863 | 0.03863 | 0.98128 | -0.13103 | 0.98029 | -0.13816 | 14.3073
92 | 0.03161 | 0.0079356 | -0.031601 | -0.007932 | 9.6126e-06 | 3.6124e-06 | 0.047919 | 0.047919 | 0.047919 | 0.98169 | -0.12814 | 0.98138 | -0.13033 | 17.7477
93 | -0.10038 | -0.025229 | 0.10042 | 0.025245 | 4.1341e-05 | 1.557e-05 | 0.15166 | 0.15166 | 0.15166 | 0.98502 | -0.10449 | 0.98544 | -0.10153 | 18.7241
94 | 0.021958 | 0.0055039 | -0.021948 | -0.0055002 | 1.009e-05 | 3.6972e-06 | 0.033331 | 0.033331 | 0.033331 | 0.98029 | -0.13816 | 0.97982 | -0.14148 | 12.3449
95 | 0.0034906 | 0.00087448 | -0.00349 | -0.00087468 | 6.2122e-07 | -2.0804e-07 | 0.0052985 | 0.0052986 | 0.0052986 | 0.98029 | -0.13816 | 0.98011 | -0.13945 | 1.9625
96 | 0.030428 | 0.0076382 | -0.030413 | -0.0076325 | 1.5142e-05 | 5.6798e-06 | 0.046141 | 0.046141 | 0.046141 | 0.98138 | -0.13033 | 0.98088 | -0.13391 | 17.0894
97 | -0.10076 | -0.025329 | 0.10089 | 0.025378 | 0.00012812 | 4.8257e-05 | 0.15217 | 0.15217 | 0.15217 | 0.98544 | -0.10153 | 0.98674 | -0.092416 | 18.787
98 | 0.0071882 | 0.0018003 | -0.0071839 | -0.0017994 | 4.2979e-06 | 9.2547e-07 | 0.010916 | 0.010916 | 0.010916 | 0.97982 | -0.14148 | 0.97922 | -0.14581 | 4.043
99 | 0.01476 | 0.0036999 | -0.014751 | -0.0036968 | 8.9657e-06 | 3.0884e-06 | 0.022415 | 0.022415 | 0.022415 | 0.97982 | -0.14148 | 0.97921 | -0.14587 | 8.302
100 | -0.10349 | -0.02603 | 0.10375 | 0.026128 | 0.00025952 | 9.7848e-05 | 0.1561 | 0.1561 | 0.1561 | 0.98674 | -0.092416 | 0.98929 | -0.074475 | 19.2714
101 | -0.11241 | -0.028294 | 0.11268 | 0.028396 | 0.00027055 | 0.0001023 | 0.16912 | 0.16912 | 0.16912 | 0.98929 | -0.074475 | 0.99174 | -0.05728 | 20.8794
102 | -0.11526 | -0.029042 | 0.11535 | 0.029075 | 8.9454e-05 | 3.3849e-05 | 0.17299 | 0.17299 | 0.17299 | 0.99174 | -0.05728 | 0.99254 | -0.051738 | 21.3563
103 | -0.1211 | -0.030516 | 0.12126 | 0.030578 | 0.00016199 | 6.1385e-05 | 0.18161 | 0.18161 | 0.18161 | 0.99254 | -0.051738 | 0.99391 | -0.042194 | 22.4206
104 | 0.0057507 | 0.0014408 | -0.0057502 | -0.0014407 | 4.8732e-07 | 5.1649e-08 | 0.0086214 | 0.0086214 | 0.0086214 | 0.99254 | -0.051738 | 0.99245 | -0.05235 | 3.1931
105 | 0.029545 | 0.0074148 | -0.029517 | -0.0074046 | 2.7289e-05 | 1.0221e-05 | 0.044824 | 0.044824 | 0.044824 | 0.98088 | -0.13391 | 0.97994 | -0.14057 | 16.6013
106 | -0.12435 | -0.031353 | 0.12451 | 0.031413 | 0.0001595 | 6.0485e-05 | 0.18624 | 0.18624 | 0.18624 | 0.99391 | -0.042194 | 0.99522 | -0.033051 | 22.9923
107 | 0.0057502 | 0.0014407 | -0.0057494 | -0.0014407 | 8.4054e-07 | 8.9144e-08 | 0.0086214 | 0.0086215 | 0.0086215 | 0.99245 | -0.05235 | 0.9923 | -0.053407 | 3.1931
108 | 0.029005 | 0.0072763 | -0.028989 | -0.0072703 | 1.5922e-05 | 5.9582e-06 | 0.044046 | 0.044046 | 0.044046 | 0.97994 | -0.14057 | 0.97939 | -0.14453 | 16.3134
109 | 0.002451 | 0.00061391 | -0.0024508 | -0.00061422 | 2.8491e-07 | -3.047e-07 | 0.0037238 | 0.003724 | 0.003724 | 0.97939 | -0.14453 | 0.97927 | -0.14537 | 1.3792
110 | 0.026538 | 0.0066564 | -0.026521 | -0.00665 | 1.7197e-05 | 6.401e-06 | 0.040322 | 0.040323 | 0.040323 | 0.97939 | -0.14453 | 0.97873 | -0.14921 | 14.9343
111 | 0.025755 | 0.0064579 | -0.025728 | -0.006448 | 2.6764e-05 | 9.9428e-06 | 0.039157 | 0.039157 | 0.039157 | 0.97873 | -0.14921 | 0.97768 | -0.15671 | 14.5028
112 | 0.024226 | 0.0060715 | -0.024213 | -0.006067 | 1.2303e-05 | 4.5502e-06 | 0.036871 | 0.036871 | 0.036871 | 0.97768 | -0.15671 | 0.97717 | -0.16038 | 13.656
113 | 0.024213 | 0.006067 | -0.024202 | -0.0060628 | 1.1265e-05 | 4.1663e-06 | 0.036871 | 0.036871 | 0.036871 | 0.97717 | -0.16038 | 0.9767 | -0.16375 | 13.656
114 | 0.0019464 | 0.00048753 | -0.0019463 | -0.00048778 | 1.2107e-07 | -2.4765e-07 | 0.0029186 | 0.0029187 | 0.0029187 | 0.9923 | -0.053407 | 0.99224 | -0.053857 | 1.081
115 | -0.12696 | -0.032028 | 0.12696 | 0.032028 | 1.2874e-07 | 4.8858e-08 | 0.1899 | 0.1899 | 0.1899 | 0.99522 | -0.033051 | 0.99522 | -0.033044 | 23.4449
116 | 0.010043 | 0.0025169 | -0.01004 | -0.002516 | 2.9876e-06 | 8.9395e-07 | 0.015312 | 0.015312 | 0.015312 | 0.976 | -0.16877 | 0.9757 | -0.17092 | 5.6712
117 | -0.01141 | -0.0028594 | 0.011412 | 0.00286 | 1.7588e-06 | 5.6006e-07 | 0.017396 | 0.017396 | 0.017396 | 0.976 | -0.16877 | 0.97616 | -0.16766 | 6.443
118 | 0.0039726 | 0.00099525 | -0.0039725 | -0.00099527 | 1.3802e-07 | -2.2177e-08 | 0.0060584 | 0.0060584 | 0.0060584 | 0.9757 | -0.17092 | 0.97567 | -0.17117 | 2.2439
119 | -0.015124 | -0.0037903 | 0.015132 | 0.0037931 | 8.1917e-06 | 2.8417e-06 | 0.023054 | 0.023054 | 0.023054 | 0.97616 | -0.16766 | 0.9767 | -0.16375 | 8.5386
120 | 0.0027407 | 0.00068656 | -0.0027404 | -0.00068677 | 2.79e-07 | -2.1226e-07 | 0.0041798 | 0.0041799 | 0.0041799 | 0.97567 | -0.17117 | 0.97556 | -0.17191 | 1.5481
121 | 0.0021218 | 0.00052826 | -0.0021199 | -0.00053122 | 1.9293e-06 | -2.9587e-06 | 0.0032314 | 0.0032327 | 0.0032327 | 0.9767 | -0.16375 | 0.97579 | -0.17036 | 1.1973
122 | 0.0015801 | 0.00039596 | -0.0015801 | -0.000396 | 1.3087e-08 | -4.0051e-08 | 0.0024101 | 0.0024101 | 0.0024101 | 0.97556 | -0.17191 | 0.97556 | -0.17197 | 0.89262
123 | 0.00084369 | 0.00021136 | -0.00084368 | -0.00021145 | 7.0506e-09 | -8.2558e-08 | 0.0012865 | 0.0012866 | 0.0012866 | 0.97579 | -0.17036 | 0.97578 | -0.17042 | 0.47651
124 | -0.1291 | -0.032564 | 0.12931 | 0.032642 | 0.00020494 | 7.7793e-05 | 0.1931 | 0.1931 | 0.1931 | 0.99522 | -0.033044 | 0.99685 | -0.021742 | 23.8397
125 | 0.0060186 | 0.0015073 | -0.006017 | -0.0015071 | 1.5066e-06 | 2.1642e-07 | 0.0091454 | 0.0091455 | 0.0091455 | 0.97922 | -0.14581 | 0.97896 | -0.14762 | 3.3872
126 | 0.0067482 | 0.0016912 | -0.0067471 | -0.001691 | 1.0831e-06 | 2.0898e-07 | 0.010255 | 0.010255 | 0.010255 | 0.97921 | -0.14587 | 0.97905 | -0.14703 | 3.798
127 | 0.0041329 | 0.0010349 | -0.0041306 | -0.0010352 | 2.3413e-06 | -2.9425e-07 | 0.0062817 | 0.0062821 | 0.0062821 | 0.97896 | -0.14762 | 0.97839 | -0.15171 | 2.3267

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23795 | 0.060022

## res_load
| p_mw | q_mvar
0 | 0.00023347 | 5.8513e-05
1 | 0.0039842 | 0.00099854
2 | 0.0015357 | 0.00038488
3 | 0.0031187 | 0.00078163
4 | 0.0036244 | 0.00090836
5 | 0.0023203 | 0.00058151
6 | 0.0029259 | 0.00073331
7 | 0.002687 | 0.00067342
8 | 0.0016313 | 0.00040885
9 | 0.001286 | 0.00032229
10 | 0.0022368 | 0.0005606
11 | 0.0034287 | 0.0008593
12 | 0.0053955 | 0.0013522
13 | 0.0016505 | 0.00041365
14 | 0.0017684 | 0.00044319
15 | 0.0017185 | 0.00043071
16 | 0.0030481 | 0.00076392
17 | 0.0039622 | 0.00099303
18 | 0.0032146 | 0.00080566
19 | 0.0032719 | 0.00082001
20 | 0.0030398 | 0.00076185
21 | 0.0031005 | 0.00077707
22 | 0.0038871 | 0.00097419
23 | 0.0013887 | 0.00034803
24 | 0.0021827 | 0.00054703
25 | 0.0026409 | 0.00066186
26 | 0.0028994 | 0.00072666
27 | 0.0042959 | 0.0010766
28 | 0.0023666 | 0.00059314
29 | 0.0042919 | 0.0010757
30 | 0.0036631 | 0.00091805
31 | 0.0020007 | 0.00050143
32 | 0.0029798 | 0.00074682
33 | 0.0054799 | 0.0013734
34 | 0.0018243 | 0.00045722
35 | 0.0036251 | 0.00090854
36 | 0.0042103 | 0.0010552
37 | 0.0051165 | 0.0012823
38 | 0.00063992 | 0.00016038
39 | 0.0001691 | 4.2381e-05
40 | 0.00011966 | 2.9989e-05
41 | 0.00034059 | 8.536e-05
42 | 0.001068 | 0.00026766
43 | 0.0011336 | 0.00028411
44 | 0.00081821 | 0.00020506
45 | 0.0008845 | 0.00022168
46 | 0.0001884 | 4.7217e-05
47 | 0.00050523 | 0.00012662
48 | 0.0001493 | 3.7417e-05
49 | 0.0001965 | 4.9248e-05
50 | 0.0012067 | 0.00030244
51 | 0.00082062 | 0.00020567
52 | 0.0004069 | 0.00010198
53 | 0.00015281 | 3.8299e-05
54 | 0.00076353 | 0.00019136
55 | 0.00027662 | 6.9327e-05
56 | 0.0004628 | 0.00011599
57 | 0.00015713 | 3.9381e-05
58 | 0.00046298 | 0.00011603
59 | 0.00053244 | 0.00013344
60 | 0.0068249 | 0.0017105
61 | 0.0028697 | 0.00071922
62 | 0.0035989 | 0.00090198
63 | 0.0033083 | 0.00082915
64 | 0.0031379 | 0.00078643
65 | 0.003517 | 0.00088144
66 | 0.0046825 | 0.0011735
67 | 0.0011751 | 0.0002945
68 | 0.00089151 | 0.00022343
69 | 0.0013121 | 0.00032885
70 | 0.0011723 | 0.0002938
71 | 0.00033766 | 8.4626e-05
72 | 0.00349 | 0.00087468
73 | 0.0026023 | 0.0006522
74 | 0.0025748 | 0.0006453
75 | 0.0008687 | 0.00021772
76 | 0.0030934 | 0.00077528
77 | 0.00051195 | 0.00012831
78 | 0.0024508 | 0.00061422
79 | 0.0007664 | 0.00019208
80 | 0.0015022 | 0.00037649
81 | 0.003803 | 0.00095313
82 | 0.0019463 | 0.00048778
83 | 0.0024522 | 0.00061458
84 | 0.0013669 | 0.00034257
85 | 0.0060678 | 0.0015207
86 | 0.0037118 | 0.00093027
87 | 0.0012318 | 0.00030871
88 | 0.0069484 | 0.0017414
89 | 0.0011604 | 0.00029081
90 | 0.0012762 | 0.00031985
91 | 0.0015801 | 0.000396
92 | 0.00084368 | 0.00021145
93 | 0.0021386 | 0.00053598
94 | 0.0015487 | 0.00038815
95 | 0.0011653 | 0.00029205
96 | 0.0080026 | 0.0020056
97 | 0.0018841 | 0.00047221
98 | 0.0067471 | 0.001691
99 | 0.0041306 | 0.0010352

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1