## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2113-5_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2113-5_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2113-5_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2113-5_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2113-5_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2113-5_0_6_node_50 | 0.4 | n |  | TRUE
6 | bus_LV_2113-5_0_6_node_48 | 0.4 | n |  | TRUE
7 | bus_LV_2113-5_0_6_node_105 | 0.4 | n |  | TRUE
8 | bus_LV_2113-5_0_6_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2113-5_0_6_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2113-5_0_6_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2113-5_0_6_node_73 | 0.4 | n |  | TRUE
12 | bus_LV_2113-5_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2113-5_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2113-5_0_6_node_80 | 0.4 | n |  | TRUE
15 | bus_LV_2113-5_0_6_node_64 | 0.4 | n |  | TRUE
16 | bus_LV_2113-5_0_6_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2113-5_0_6_node_68 | 0.4 | n |  | TRUE
18 | bus_LV_2113-5_0_6_node_62 | 0.4 | n |  | TRUE
19 | bus_LV_2113-5_0_6_node_79 | 0.4 | n |  | TRUE
20 | bus_LV_2113-5_0_6_node_66 | 0.4 | n |  | TRUE
21 | bus_LV_2113-5_0_6_node_127 | 0.4 | n |  | TRUE
22 | bus_LV_2113-5_0_6_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_2113-5_0_6_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_2113-5_0_6_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_2113-5_0_6_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2113-5_0_6_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_2113-5_0_6_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_2113-5_0_6_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_2113-5_0_6_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_2113-5_0_6_node_52 | 0.4 | n |  | TRUE
31 | bus_LV_2113-5_0_6_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_2113-5_0_6_node_69 | 0.4 | n |  | TRUE
33 | bus_LV_2113-5_0_6_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_2113-5_0_6_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2113-5_0_6_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_2113-5_0_6_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_2113-5_0_6_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_2113-5_0_6_node_54 | 0.4 | n |  | TRUE
39 | bus_LV_2113-5_0_6_node_55 | 0.4 | n |  | TRUE
40 | bus_LV_2113-5_0_6_node_53 | 0.4 | n |  | TRUE
41 | bus_LV_2113-5_0_6_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_2113-5_0_6_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2113-5_0_6_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_2113-5_0_6_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_2113-5_0_6_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_2113-5_0_6_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_2113-5_0_6_node_31 | 0.4 | n |  | TRUE
48 | bus_LV_2113-5_0_6_node_74 | 0.4 | n |  | TRUE
49 | bus_LV_2113-5_0_6_node_70 | 0.4 | n |  | TRUE
50 | bus_LV_2113-5_0_6_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_2113-5_0_6_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_2113-5_0_6_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_2113-5_0_6_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_2113-5_0_6_node_75 | 0.4 | n |  | TRUE
55 | bus_LV_2113-5_0_6_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_2113-5_0_6_node_76 | 0.4 | n |  | TRUE
57 | bus_LV_2113-5_0_6_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_2113-5_0_6_node_32 | 0.4 | n |  | TRUE
59 | bus_LV_2113-5_0_6_node_33 | 0.4 | n |  | TRUE
60 | bus_LV_2113-5_0_6_node_34 | 0.4 | n |  | TRUE
61 | bus_LV_2113-5_0_6_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_2113-5_0_6_node_38 | 0.4 | n |  | TRUE
63 | bus_LV_2113-5_0_6_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_2113-5_0_6_node_71 | 0.4 | n |  | TRUE
65 | bus_LV_2113-5_0_6_node_72 | 0.4 | n |  | TRUE
66 | bus_LV_2113-5_0_6_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_2113-5_0_6_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_2113-5_0_6_node_41 | 0.4 | n |  | TRUE
69 | bus_LV_2113-5_0_6_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_2113-5_0_6_node_77 | 0.4 | n |  | TRUE
71 | bus_LV_2113-5_0_6_node_78 | 0.4 | n |  | TRUE
72 | bus_LV_2113-5_0_6_node_98 | 0.4 | n |  | TRUE
73 | bus_LV_2113-5_0_6_node_87 | 0.4 | n |  | TRUE
74 | bus_LV_2113-5_0_6_node_88 | 0.4 | n |  | TRUE
75 | bus_LV_2113-5_0_6_node_89 | 0.4 | n |  | TRUE
76 | bus_LV_2113-5_0_6_node_90 | 0.4 | n |  | TRUE
77 | bus_LV_2113-5_0_6_node_91 | 0.4 | n |  | TRUE
78 | bus_LV_2113-5_0_6_node_92 | 0.4 | n |  | TRUE
79 | bus_LV_2113-5_0_6_node_93 | 0.4 | n |  | TRUE
80 | bus_LV_2113-5_0_6_node_96 | 0.4 | n |  | TRUE
81 | bus_LV_2113-5_0_6_node_94 | 0.4 | n |  | TRUE
82 | bus_LV_2113-5_0_6_node_95 | 0.4 | n |  | TRUE
83 | bus_LV_2113-5_0_6_node_99 | 0.4 | n |  | TRUE
84 | bus_LV_2113-5_0_6_node_46 | 0.4 | n |  | TRUE
85 | bus_LV_2113-5_0_6_node_47 | 0.4 | n |  | TRUE
86 | bus_LV_2113-5_0_6_node_49 | 0.4 | n |  | TRUE
87 | bus_LV_2113-5_0_6_node_51 | 0.4 | n |  | TRUE
88 | bus_LV_2113-5_0_6_node_56 | 0.4 | n |  | TRUE
89 | bus_LV_2113-5_0_6_node_84 | 0.4 | n |  | TRUE
90 | bus_LV_2113-5_0_6_node_81 | 0.4 | n |  | TRUE
91 | bus_LV_2113-5_0_6_node_86 | 0.4 | n |  | TRUE
92 | bus_LV_2113-5_0_6_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_2113-5_0_6_node_58 | 0.4 | n |  | TRUE
94 | bus_LV_2113-5_0_6_node_59 | 0.4 | n |  | TRUE
95 | bus_LV_2113-5_0_6_node_60 | 0.4 | n |  | TRUE
96 | bus_LV_2113-5_0_6_node_61 | 0.4 | n |  | TRUE
97 | bus_LV_2113-5_0_6_node_63 | 0.4 | n |  | TRUE
98 | bus_LV_2113-5_0_6_node_101 | 0.4 | n |  | TRUE
99 | bus_LV_2113-5_0_6_node_102 | 0.4 | n |  | TRUE
100 | bus_LV_2113-5_0_6_node_123 | 0.4 | n |  | TRUE
101 | bus_LV_2113-5_0_6_node_65 | 0.4 | n |  | TRUE
102 | bus_LV_2113-5_0_6_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_2113-5_0_6_node_125 | 0.4 | n |  | TRUE
104 | bus_LV_2113-5_0_6_node_83 | 0.4 | n |  | TRUE
105 | bus_LV_2113-5_0_6_node_85 | 0.4 | n |  | TRUE
106 | bus_LV_2113-5_0_6_node_100 | 0.4 | n |  | TRUE
107 | bus_LV_2113-5_0_6_node_104 | 0.4 | n |  | TRUE
108 | bus_LV_2113-5_0_6_node_126 | 0.4 | n |  | TRUE
109 | bus_LV_2113-5_0_6_node_121 | 0.4 | n |  | TRUE
110 | bus_LV_2113-5_0_6_node_122 | 0.4 | n |  | TRUE
111 | bus_LV_2113-5_0_6_node_124 | 0.4 | n |  | TRUE
112 | bus_LV_2113-5_0_6_node_106 | 0.4 | n |  | TRUE
113 | bus_LV_2113-5_0_6_node_107 | 0.4 | n |  | TRUE
114 | bus_LV_2113-5_0_6_node_108 | 0.4 | n |  | TRUE
115 | bus_LV_2113-5_0_6_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_2113-5_0_6_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_2113-5_0_6_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_2113-5_0_6_node_116 | 0.4 | n |  | TRUE
119 | bus_LV_2113-5_0_6_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_2113-5_0_6_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_2113-5_0_6_node_119 | 0.4 | n |  | TRUE
122 | bus_LV_2113-5_0_6_node_120 | 0.4 | n |  | TRUE
123 | bus_LV_2113-5_0_6_node_114 | 0.4 | n |  | TRUE
124 | bus_LV_2113-5_0_6_node_115 | 0.4 | n |  | TRUE
125 | bus_LV_2113-5_0_6_node_117 | 0.4 | n |  | TRUE
126 | bus_MV_33_0_node_163 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2113-5_0_6_load_0 | 0 | 0.003824 | 0.00095839 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2113-5_0_6_load_1 | 1 | 0.00024986 | 6.2621e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2113-5_0_6_load_2 | 2 | 0.0013299 | 0.0003333 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2113-5_0_6_load_3 | 3 | 0.00093586 | 0.00023455 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2113-5_0_6_load_48 | 6 | 0.0016589 | 0.00041576 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2113-5_0_6_load_105 | 7 | 0.0064956 | 0.0016279 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2113-5_0_6_load_5 | 8 | 0.001393 | 0.00034913 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2113-5_0_6_load_6 | 9 | 0.00018382 | 4.6071e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2113-5_0_6_load_8 | 12 | 0.00028718 | 7.1973e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2113-5_0_6_load_80 | 14 | 0.0013929 | 0.00034909 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2113-5_0_6_load_68 | 17 | 0.00077464 | 0.00019414 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2113-5_0_6_load_62 | 18 | 0.00023149 | 5.8016e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2113-5_0_6_load_79 | 19 | 0.0012142 | 0.0003043 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2113-5_0_6_load_66 | 20 | 0.00084538 | 0.00021187 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2113-5_0_6_load_127 | 21 | 0.0015692 | 0.00039327 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2113-5_0_6_load_11 | 22 | 0.0024107 | 0.00060417 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2113-5_0_6_load_12 | 23 | 0.0019977 | 0.00050067 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2113-5_0_6_load_13 | 24 | 0.0028159 | 0.00070572 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2113-5_0_6_load_14 | 25 | 0.0018405 | 0.00046126 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2113-5_0_6_load_15 | 26 | 0.0050748 | 0.0012719 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2113-5_0_6_load_16 | 27 | 0.00078612 | 0.00019702 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2113-5_0_6_load_17 | 28 | 0.0035842 | 0.00089829 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2113-5_0_6_load_37 | 29 | 0.0047106 | 0.0011806 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2113-5_0_6_load_52 | 30 | 0.0022853 | 0.00057274 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2113-5_0_6_load_35 | 31 | 0.0016231 | 0.00040678 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2113-5_0_6_load_69 | 32 | 0.0031002 | 0.00077698 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2113-5_0_6_load_18 | 33 | 0.0044063 | 0.0011043 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2113-5_0_6_load_19 | 34 | 0.00029585 | 7.4146e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2113-5_0_6_load_20 | 35 | 0.00035851 | 8.985e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2113-5_0_6_load_21 | 37 | 0.0024554 | 0.00061537 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2113-5_0_6_load_55 | 39 | 0.0013876 | 0.00034778 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2113-5_0_6_load_53 | 40 | 0.0013397 | 0.00033577 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2113-5_0_6_load_23 | 41 | 0.0017416 | 0.00043648 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2113-5_0_6_load_24 | 42 | 0.001366 | 0.00034236 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2113-5_0_6_load_26 | 44 | 0.00082186 | 0.00020598 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2113-5_0_6_load_27 | 45 | 0.0023817 | 0.00059691 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2113-5_0_6_load_28 | 46 | 0.00054181 | 0.00013579 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2113-5_0_6_load_31 | 47 | 0.0015821 | 0.00039651 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2113-5_0_6_load_74 | 48 | 0.0021589 | 0.00054107 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2113-5_0_6_load_70 | 49 | 0.0036711 | 0.00092006 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2113-5_0_6_load_44 | 50 | 0.0015083 | 0.00037802 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2113-5_0_6_load_29 | 51 | 0.0030457 | 0.00076331 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2113-5_0_6_load_30 | 52 | 0.0043354 | 0.0010866 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2113-5_0_6_load_45 | 53 | 0.0020604 | 0.0005164 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2113-5_0_6_load_75 | 54 | 0.004756 | 0.001192 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2113-5_0_6_load_43 | 55 | 0.00067602 | 0.00016943 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2113-5_0_6_load_76 | 56 | 0.010981 | 0.002752 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2113-5_0_6_load_32 | 58 | 0.00065164 | 0.00016332 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2113-5_0_6_load_33 | 59 | 0.0019107 | 0.00047887 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2113-5_0_6_load_34 | 60 | 0.00050124 | 0.00012562 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2113-5_0_6_load_36 | 61 | 0.00028917 | 7.2472e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2113-5_0_6_load_38 | 62 | 0.0020762 | 0.00052035 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2113-5_0_6_load_71 | 64 | 0.0018298 | 0.00045859 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2113-5_0_6_load_72 | 65 | 0.00043449 | 0.00010889 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2113-5_0_6_load_39 | 66 | 0.0010539 | 0.00026413 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2113-5_0_6_load_40 | 67 | 0.00068304 | 0.00017118 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2113-5_0_6_load_41 | 68 | 0.0011659 | 0.0002922 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2113-5_0_6_load_42 | 69 | 0.0011488 | 0.00028791 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2113-5_0_6_load_77 | 70 | 0.0016588 | 0.00041574 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2113-5_0_6_load_78 | 71 | 0.0030481 | 0.00076392 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2113-5_0_6_load_98 | 72 | 0.0019581 | 0.00049076 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2113-5_0_6_load_87 | 73 | 0.0013221 | 0.00033134 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2113-5_0_6_load_88 | 74 | 0.0010148 | 0.00025432 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2113-5_0_6_load_89 | 75 | 0.0019379 | 0.00048569 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2113-5_0_6_load_90 | 76 | 0.00048995 | 0.00012279 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2113-5_0_6_load_91 | 77 | 0.0012602 | 0.00031584 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2113-5_0_6_load_92 | 78 | 0.0012277 | 0.0003077 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2113-5_0_6_load_93 | 79 | 0.0011928 | 0.00029894 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2113-5_0_6_load_96 | 80 | 0.0015385 | 0.00038558 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2113-5_0_6_load_94 | 81 | 0.0017631 | 0.00044188 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2113-5_0_6_load_95 | 82 | 0.0016972 | 0.00042536 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2113-5_0_6_load_99 | 83 | 0.0010234 | 0.00025649 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2113-5_0_6_load_46 | 84 | 0.0010208 | 0.00025583 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2113-5_0_6_load_47 | 85 | 0.0024776 | 0.00062094 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2113-5_0_6_load_49 | 86 | 0.00082597 | 0.00020701 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2113-5_0_6_load_51 | 87 | 0.001555 | 0.00038973 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2113-5_0_6_load_84 | 89 | 0.0025951 | 0.0006504 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2113-5_0_6_load_81 | 90 | 0.0006273 | 0.00015722 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2113-5_0_6_load_86 | 91 | 0.0021202 | 0.00053137 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2113-5_0_6_load_82 | 92 | 0.00098569 | 0.00024704 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2113-5_0_6_load_58 | 93 | 0.00026022 | 6.5219e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2113-5_0_6_load_59 | 94 | 0.00017981 | 4.5064e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2113-5_0_6_load_60 | 95 | 0.00057658 | 0.00014451 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2113-5_0_6_load_61 | 96 | 0.0028884 | 0.0007239 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2113-5_0_6_load_102 | 99 | 0.00392 | 0.00098245 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2113-5_0_6_load_65 | 101 | 0.0010288 | 0.00025785 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2113-5_0_6_load_97 | 102 | 0.00073837 | 0.00018505 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2113-5_0_6_load_125 | 103 | 0.0002103 | 5.2706e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2113-5_0_6_load_85 | 105 | 0.0017047 | 0.00042724 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2113-5_0_6_load_100 | 106 | 0.00094089 | 0.00023581 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2113-5_0_6_load_104 | 107 | 0.0041068 | 0.0010293 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2113-5_0_6_load_126 | 108 | 0.00054223 | 0.0001359 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2113-5_0_6_load_121 | 109 | 6.6415e-05 | 1.6645e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2113-5_0_6_load_122 | 110 | 0.00073458 | 0.0001841 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2113-5_0_6_load_124 | 111 | 0.0060745 | 0.0015224 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2113-5_0_6_load_106 | 112 | 0.0020645 | 0.00051742 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2113-5_0_6_load_109 | 115 | 0.0039853 | 0.00099882 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2113-5_0_6_load_110 | 116 | 0.00051764 | 0.00012973 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2113-5_0_6_load_111 | 117 | 0.0037702 | 0.00094489 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2113-5_0_6_load_116 | 118 | 0.00061725 | 0.0001547 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2113-5_0_6_load_112 | 119 | 0.0017267 | 0.00043275 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2113-5_0_6_load_119 | 121 | 0.0021632 | 0.00054214 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2113-5_0_6_load_120 | 122 | 0.00018484 | 4.6325e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2113-5_0_6_load_114 | 123 | 0.0010307 | 0.00025831 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2113-5_0_6_load_115 | 124 | 0.0013427 | 0.00033652 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2113-5_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.035626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2113-5_0_6_line_1 | NAYY 4x150 SE | 0 | 2 | 0.026275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2113-5_0_6_line_2 | NAYY 4x150 SE | 1 | 3 | 0.040038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2113-5_0_6_line_3 | NAYY 4x150 SE | 2 | 4 | 0.023111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2113-5_0_6_line_4 | NAYY 4x150 SE | 4 | 7 | 0.10055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2113-5_0_6_line_5 | NAYY 4x150 SE | 4 | 5 | 0.16829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2113-5_0_6_line_6 | NAYY 4x150 SE | 5 | 6 | 0.053628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2113-5_0_6_line_7 | NAYY 4x150 SE | 6 | 84 | 0.027508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2113-5_0_6_line_8 | NAYY 4x150 SE | 8 | 9 | 0.011254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_2113-5_0_6_line_9 | NAYY 4x150 SE | 8 | 10 | 0.023612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_2113-5_0_6_line_10 | NAYY 4x150 SE | 8 | 11 | 0.11989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2113-5_0_6_line_11 | NAYY 4x150 SE | 9 | 12 | 0.0097956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_2113-5_0_6_line_12 | NAYY 4x150 SE | 10 | 13 | 0.056367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_2113-5_0_6_line_13 | NAYY 4x150 SE | 11 | 14 | 0.031535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2113-5_0_6_line_14 | NAYY 4x150 SE | 11 | 15 | 0.025544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2113-5_0_6_line_15 | NAYY 4x150 SE | 12 | 16 | 0.027756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_2113-5_0_6_line_16 | NAYY 4x150 SE | 13 | 17 | 0.13244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_2113-5_0_6_line_17 | NAYY 4x150 SE | 14 | 102 | 0.0073103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2113-5_0_6_line_18 | NAYY 4x150 SE | 15 | 18 | 0.10116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2113-5_0_6_line_19 | NAYY 4x150 SE | 16 | 19 | 0.29017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_2113-5_0_6_line_20 | NAYY 4x150 SE | 17 | 20 | 0.034295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_2113-5_0_6_line_21 | NAYY 4x150 SE | 18 | 95 | 0.043837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2113-5_0_6_line_22 | NAYY 4x150 SE | 19 | 21 | 0.24686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_2113-5_0_6_line_23 | NAYY 4x150 SE | 20 | 101 | 0.036411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_2113-5_0_6_line_24 | NAYY 4x150 SE | 21 | 103 | 0.31165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_2113-5_0_6_line_25 | NAYY 4x150 SE | 22 | 23 | 0.024242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_2113-5_0_6_line_26 | NAYY 4x150 SE | 22 | 24 | 0.030901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_2113-5_0_6_line_27 | NAYY 4x150 SE | 23 | 25 | 0.024531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_2113-5_0_6_line_28 | NAYY 4x150 SE | 24 | 26 | 0.02289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_2113-5_0_6_line_29 | NAYY 4x150 SE | 25 | 27 | 0.029286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_2113-5_0_6_line_30 | NAYY 4x150 SE | 26 | 28 | 0.042213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_2113-5_0_6_line_31 | NAYY 4x150 SE | 27 | 29 | 0.033641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_2113-5_0_6_line_32 | NAYY 4x150 SE | 28 | 30 | 0.019897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_2113-5_0_6_line_33 | NAYY 4x150 SE | 29 | 31 | 0.00094974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_2113-5_0_6_line_34 | NAYY 4x150 SE | 30 | 32 | 0.084459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_2113-5_0_6_line_35 | NAYY 4x150 SE | 31 | 59 | 0.014174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_2113-5_0_6_line_36 | NAYY 4x150 SE | 32 | 57 | 0.010694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_2113-5_0_6_line_37 | NAYY 4x150 SE | 33 | 34 | 0.067906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2113-5_0_6_line_38 | NAYY 4x150 SE | 33 | 35 | 0.16264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2113-5_0_6_line_39 | NAYY 4x150 SE | 34 | 36 | 0.024779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2113-5_0_6_line_40 | NAYY 4x150 SE | 35 | 37 | 0.073736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2113-5_0_6_line_41 | NAYY 4x150 SE | 36 | 38 | 0.12525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2113-5_0_6_line_42 | NAYY 4x150 SE | 38 | 39 | 0.083277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2113-5_0_6_line_43 | NAYY 4x150 SE | 38 | 40 | 0.021937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2113-5_0_6_line_44 | NAYY 4x150 SE | 39 | 88 | 0.034928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2113-5_0_6_line_45 | NAYY 4x150 SE | 41 | 42 | 0.033528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_2113-5_0_6_line_46 | NAYY 4x150 SE | 41 | 43 | 0.047661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_2113-5_0_6_line_47 | NAYY 4x150 SE | 42 | 44 | 0.056158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_2113-5_0_6_line_48 | NAYY 4x150 SE | 43 | 45 | 0.037592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_2113-5_0_6_line_49 | NAYY 4x150 SE | 44 | 46 | 0.014309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_2113-5_0_6_line_50 | NAYY 4x150 SE | 45 | 47 | 0.029369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_2113-5_0_6_line_51 | NAYY 4x150 SE | 46 | 48 | 0.019638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_2113-5_0_6_line_52 | NAYY 4x150 SE | 47 | 49 | 0.048647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_2113-5_0_6_line_53 | NAYY 4x150 SE | 48 | 50 | 0.022359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_2113-5_0_6_line_54 | NAYY 4x150 SE | 49 | 57 | 0.021769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_2113-5_0_6_line_55 | NAYY 4x150 SE | 50 | 69 | 0.0096574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
56 | LV_2113-5_0_6_line_56 | NAYY 4x150 SE | 51 | 52 | 0.0088187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_2113-5_0_6_line_57 | NAYY 4x150 SE | 51 | 53 | 0.26727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
58 | LV_2113-5_0_6_line_58 | NAYY 4x150 SE | 52 | 54 | 0.023253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
59 | LV_2113-5_0_6_line_59 | NAYY 4x150 SE | 53 | 55 | 0.092347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_2113-5_0_6_line_60 | NAYY 4x150 SE | 54 | 56 | 0.018058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_2113-5_0_6_line_61 | NAYY 4x150 SE | 55 | 68 | 0.0009273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_2113-5_0_6_line_62 | NAYY 4x150 SE | 56 | 70 | 0.0072245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_2113-5_0_6_line_63 | NAYY 4x150 SE | 57 | 101 | 0.048077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_2113-5_0_6_line_64 | NAYY 4x150 SE | 58 | 59 | 0.0021283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_2113-5_0_6_line_65 | NAYY 4x150 SE | 58 | 60 | 0.023362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_2113-5_0_6_line_66 | NAYY 4x150 SE | 60 | 61 | 0.014174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_2113-5_0_6_line_67 | NAYY 4x150 SE | 61 | 62 | 0.00052522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_2113-5_0_6_line_68 | NAYY 4x150 SE | 62 | 63 | 0.040346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_2113-5_0_6_line_69 | NAYY 4x150 SE | 63 | 64 | 0.055118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
70 | LV_2113-5_0_6_line_70 | NAYY 4x150 SE | 63 | 65 | 0.025775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
71 | LV_2113-5_0_6_line_71 | NAYY 4x150 SE | 64 | 87 | 0.014988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2113-5_0_6_line_72 | NAYY 4x150 SE | 65 | 91 | 0.041932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_2113-5_0_6_line_73 | NAYY 4x150 SE | 66 | 67 | 0.023693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_2113-5_0_6_line_74 | NAYY 4x150 SE | 66 | 68 | 0.013583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_2113-5_0_6_line_75 | NAYY 4x150 SE | 67 | 69 | 0.0014629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_2113-5_0_6_line_76 | NAYY 4x150 SE | 70 | 71 | 0.015135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_2113-5_0_6_line_77 | NAYY 4x150 SE | 71 | 72 | 0.007594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_2113-5_0_6_line_78 | NAYY 4x150 SE | 72 | 80 | 0.037584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_2113-5_0_6_line_79 | NAYY 4x150 SE | 73 | 74 | 0.0080459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2113-5_0_6_line_80 | NAYY 4x150 SE | 73 | 75 | 0.022813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2113-5_0_6_line_81 | NAYY 4x150 SE | 74 | 76 | 0.021564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2113-5_0_6_line_82 | NAYY 4x150 SE | 75 | 77 | 0.010272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2113-5_0_6_line_83 | NAYY 4x150 SE | 76 | 78 | 0.011435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2113-5_0_6_line_84 | NAYY 4x150 SE | 77 | 79 | 0.023837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2113-5_0_6_line_85 | NAYY 4x150 SE | 78 | 80 | 0.0026181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2113-5_0_6_line_86 | NAYY 4x150 SE | 79 | 81 | 0.016177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2113-5_0_6_line_87 | NAYY 4x150 SE | 81 | 82 | 0.033413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2113-5_0_6_line_88 | NAYY 4x150 SE | 82 | 83 | 0.0049809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2113-5_0_6_line_89 | NAYY 4x150 SE | 84 | 85 | 0.034685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2113-5_0_6_line_90 | NAYY 4x150 SE | 85 | 86 | 0.039157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2113-5_0_6_line_91 | NAYY 4x150 SE | 86 | 87 | 0.00036048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2113-5_0_6_line_92 | NAYY 4x150 SE | 88 | 89 | 0.10262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2113-5_0_6_line_93 | NAYY 4x150 SE | 88 | 90 | 0.061627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2113-5_0_6_line_94 | NAYY 4x150 SE | 89 | 91 | 0.093894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
95 | LV_2113-5_0_6_line_95 | NAYY 4x150 SE | 90 | 92 | 0.074924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2113-5_0_6_line_96 | NAYY 4x150 SE | 92 | 104 | 0.022469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2113-5_0_6_line_97 | NAYY 4x150 SE | 93 | 94 | 0.063211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2113-5_0_6_line_98 | NAYY 4x150 SE | 93 | 95 | 0.019673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2113-5_0_6_line_99 | NAYY 4x150 SE | 94 | 96 | 0.026949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2113-5_0_6_line_100 | NAYY 4x150 SE | 96 | 97 | 0.068994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2113-5_0_6_line_101 | NAYY 4x150 SE | 97 | 98 | 0.086709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2113-5_0_6_line_102 | NAYY 4x150 SE | 98 | 99 | 0.041611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2113-5_0_6_line_103 | NAYY 4x150 SE | 98 | 100 | 0.16375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2113-5_0_6_line_104 | NAYY 4x150 SE | 100 | 111 | 0.027812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2113-5_0_6_line_105 | NAYY 4x150 SE | 100 | 109 | 0.23909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2113-5_0_6_line_106 | NAYY 4x150 SE | 103 | 125 | 0.15704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2113-5_0_6_line_107 | NAYY 4x150 SE | 104 | 105 | 0.033473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2113-5_0_6_line_108 | NAYY 4x150 SE | 105 | 106 | 0.025235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2113-5_0_6_line_109 | NAYY 4x150 SE | 107 | 108 | 0.048358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2113-5_0_6_line_110 | NAYY 4x150 SE | 108 | 111 | 0.01718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2113-5_0_6_line_111 | NAYY 4x150 SE | 109 | 110 | 0.020676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2113-5_0_6_line_112 | NAYY 4x150 SE | 112 | 113 | 0.050646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2113-5_0_6_line_113 | NAYY 4x150 SE | 112 | 114 | 0.066846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2113-5_0_6_line_114 | NAYY 4x150 SE | 113 | 115 | 0.082904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2113-5_0_6_line_115 | NAYY 4x150 SE | 114 | 116 | 0.28182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2113-5_0_6_line_116 | NAYY 4x150 SE | 116 | 117 | 0.048928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2113-5_0_6_line_117 | NAYY 4x150 SE | 117 | 118 | 0.27817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2113-5_0_6_line_118 | NAYY 4x150 SE | 118 | 123 | 0.058978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2113-5_0_6_line_119 | NAYY 4x150 SE | 118 | 121 | 0.15633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2113-5_0_6_line_120 | NAYY 4x150 SE | 119 | 120 | 0.039094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2113-5_0_6_line_121 | NAYY 4x150 SE | 120 | 121 | 0.032213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2113-5_0_6_line_122 | NAYY 4x150 SE | 120 | 122 | 0.025972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2113-5_0_6_line_123 | NAYY 4x150 SE | 123 | 124 | 0.002627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2113-5_0_6_line_124 | NAYY 4x150 SE | 124 | 125 | 0.013361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2113-5_0_6_trafo_68 | 0.25 MVA 20/0.4 kV | 126 | 17 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2561705.8949 | 1164752.1422 | 2561717.6429 | 1164785.7758
1 | 2561705.8949 | 1164752.1422 | 2561701.8496 | 1164740.5608 | 2561698.7437 | 1164726.9016
2 | 2561717.6429 | 1164785.7758 | 2561730.8454 | 1164823.5739
3 | 2561701.6184 | 1164704.388 | 2561697.5711 | 1164721.7451 | 2561698.7437 | 1164726.9016
4 | 2561701.6184 | 1164704.388 | 2561621.1077 | 1164644.1495
5 | 2561820.3144 | 1164585.0916 | 2561701.6184 | 1164704.388
6 | 2561820.3144 | 1164585.0916 | 2561809.2062 | 1164561.6391 | 2561797.3602 | 1164536.6249
7 | 2561797.3602 | 1164536.6249 | 2561792.2527 | 1164525.8398 | 2561785.9572 | 1164512.5508 | 2561785.5888 | 1164511.7627
8 | 2561298.5493 | 1163972.0442 | 2561297.683 | 1163973.5042 | 2561293.4229 | 1163982.058
9 | 2561311.3623 | 1163952.2272 | 2561303.8275 | 1163963.1481 | 2561298.5493 | 1163972.0442
10 | 2561192.3713 | 1163916.3776 | 2561298.5493 | 1163972.0442
11 | 2561289.0559 | 1163990.8263 | 2561293.4229 | 1163982.058
12 | 2561340.7487 | 1163904.6131 | 2561338.2039 | 1163913.7898 | 2561311.3623 | 1163952.2272
13 | 2561192.3713 | 1163916.3776 | 2561189.3458 | 1163918.7095 | 2561170.0007 | 1163938.5561
14 | 2561203.4741 | 1163894.6612 | 2561203.1914 | 1163903.0451 | 2561192.3713 | 1163916.3776
15 | 2561278.4229 | 1164015.2946 | 2561285.8582 | 1164006.7755 | 2561287.2794 | 1163994.3933 | 2561289.0559 | 1163990.8263
16 | 2561468.7884 | 1163938.454 | 2561340.7487 | 1163904.6131
17 | 2561170.0007 | 1163938.5561 | 2561169.0848 | 1163939.4958 | 2561165.5833 | 1163944.3657
18 | 2561203.4741 | 1163894.6612 | 2561171.8472 | 1163893.0206 | 2561148.3071 | 1163891.2055 | 2561111.0987 | 1163886.3219 | 2561102.892 | 1163884.7618
19 | 2561278.4229 | 1164015.2946 | 2561085.0564 | 1164231.6471
20 | 2561468.7884 | 1163938.454 | 2561475.2423 | 1163940.7328 | 2561478.8906 | 1163942.3324 | 2561500.3894 | 1163951.7404
21 | 2561102.892 | 1163884.7618 | 2561081.0154 | 1163880.603 | 2561060.1244 | 1163875.2395
22 | 2561085.0564 | 1164231.6471 | 2560838.3371 | 1164239.9465
23 | 2561533.1473 | 1163967.5527 | 2561520.0503 | 1163960.3441 | 2561500.3894 | 1163951.7404
24 | 2560650.5823 | 1164488.6933 | 2560838.3371 | 1164239.9465
25 | 2561657.4664 | 1164189.4673 | 2561658.041 | 1164190.29 | 2561666.8856 | 1164211.7792
26 | 2561639.7696 | 1164164.1355 | 2561650.5203 | 1164179.5214 | 2561657.4664 | 1164189.4673
27 | 2561666.8856 | 1164211.7792 | 2561674.4012 | 1164230.0392 | 2561676.2236 | 1164234.4633
28 | 2561639.7696 | 1164164.1355 | 2561626.6588 | 1164145.3719
29 | 2561676.2236 | 1164234.4633 | 2561684.9654 | 1164255.685 | 2561687.9745 | 1164261.2585
30 | 2561626.6588 | 1164145.3719 | 2561618.3503 | 1164133.4812 | 2561605.4377 | 1164108.9668
31 | 2561703.9561 | 1164290.8605 | 2561687.9745 | 1164261.2585
32 | 2561598.6998 | 1164090.3714 | 2561601.8288 | 1164102.1153 | 2561605.4377 | 1164108.9668
33 | 2561704.4073 | 1164291.6963 | 2561703.9561 | 1164290.8605
34 | 2561572.9616 | 1164010.0707 | 2561573.7603 | 1164011.4372 | 2561585.0227 | 1164040.7357 | 2561591.3918 | 1164062.9619 | 2561593.0083 | 1164069.0214 | 2561596.2492 | 1164081.1735 | 2561598.6998 | 1164090.3714
35 | 2561704.4073 | 1164291.6963 | 2561711.1408 | 1164304.1685
36 | 2561567.5653 | 1164000.8381 | 2561572.9616 | 1164010.0707
37 | 2562077.9171 | 1164429.8419 | 2562079.2984 | 1164450.045 | 2562083.7189 | 1164491.4718 | 2562084.5962 | 1164497.4008
38 | 2562084.5962 | 1164497.4008 | 2562156.7347 | 1164643.1673
39 | 2562081.6967 | 1164406.6741 | 2562076.8003 | 1164413.5086 | 2562077.9171 | 1164429.8419
40 | 2562193.3341 | 1164706.7503 | 2562187.826 | 1164693.1961 | 2562166.7953 | 1164655.2648 | 2562156.7347 | 1164643.1673
41 | 2562026.755 | 1164294.1193 | 2562081.6967 | 1164406.6741
42 | 2562026.755 | 1164294.1193 | 2562007.257 | 1164267.5958 | 2561976.7484 | 1164227.5316
43 | 2562026.755 | 1164294.1193 | 2562046.4885 | 1164284.5371
44 | 2561952.3698 | 1164205.056 | 2561960.719 | 1164206.4816 | 2561976.7484 | 1164227.5316
45 | 2561582.4858 | 1163834.2801 | 2561596.2176 | 1163819.2608 | 2561603.4369 | 1163808.2365
46 | 2561546.7241 | 1163865.7131 | 2561577.7433 | 1163839.4673 | 2561582.4858 | 1163834.2801
47 | 2561617.4557 | 1163754.3496 | 2561607.739 | 1163801.6668 | 2561603.4369 | 1163808.2365
48 | 2561546.7241 | 1163865.7131 | 2561548.7106 | 1163903.2527
49 | 2561621.3582 | 1163740.5925 | 2561618.0186 | 1163751.6085 | 2561617.4557 | 1163754.3496
50 | 2561550.2626 | 1163932.5804 | 2561550.2626 | 1163932.5804 | 2561548.7106 | 1163903.2527
51 | 2561621.3582 | 1163740.5925 | 2561627.0556 | 1163721.7991
52 | 2561562.2161 | 1163979.736 | 2561550.2626 | 1163932.5804
53 | 2561633.5424 | 1163700.4018 | 2561627.0556 | 1163721.7991
54 | 2561567.5653 | 1164000.8381 | 2561562.2161 | 1163979.736
55 | 2561633.5424 | 1163700.4018 | 2561636.3442 | 1163691.1598
56 | 2561338.4734 | 1163513.6018 | 2561332.2167 | 1163507.3871
57 | 2561598.4553 | 1163575.5724 | 2561338.4734 | 1163513.6018
58 | 2561315.7189 | 1163491 | 2561332.2167 | 1163507.3871
59 | 2561647.0805 | 1163653.1457 | 2561641.9049 | 1163637.5191 | 2561602.8297 | 1163585.2977 | 2561598.4553 | 1163575.5724
60 | 2561315.7189 | 1163491 | 2561302.9072 | 1163478.2743
61 | 2561647.0805 | 1163653.1457 | 2561647.3721 | 1163654.0259 | 2561647.3721 | 1163654.0259
62 | 2561297.7815 | 1163473.183 | 2561302.9072 | 1163478.2743
63 | 2561567.5653 | 1164000.8381 | 2561558.7944 | 1163989.8553 | 2561548.4522 | 1163979.872 | 2561533.1473 | 1163967.5527
64 | 2561712.1519 | 1164306.0412 | 2561711.1408 | 1164304.1685
65 | 2561724.547 | 1164325.811 | 2561716.1213 | 1164313.3935 | 2561712.1519 | 1164306.0412
66 | 2561724.547 | 1164325.811 | 2561732.5053 | 1164337.5396
67 | 2561732.8002 | 1164337.9742 | 2561732.5053 | 1164337.5396
68 | 2561753.4122 | 1164372.5194 | 2561747.1928 | 1164359.1855 | 2561732.8002 | 1164337.9742
69 | 2561753.4122 | 1164372.5194 | 2561757.7561 | 1164385.9653 | 2561760.8811 | 1164426.8337
70 | 2561753.4122 | 1164372.5194 | 2561774.73 | 1164358.0317
71 | 2561762.3809 | 1164441.7333 | 2561761.7417 | 1164438.089 | 2561760.8811 | 1164426.8337
72 | 2561774.73 | 1164358.0317 | 2561805.5923 | 1164337.0573 | 2561809.3557 | 1164334.3828
73 | 2561643.6425 | 1163667.0855 | 2561636.7686 | 1163689.7598
74 | 2561647.3721 | 1163654.0259 | 2561645.0965 | 1163662.2892 | 2561643.6425 | 1163667.0855
75 | 2561636.7686 | 1163689.7598 | 2561636.3442 | 1163691.1598
76 | 2561297.7815 | 1163473.183 | 2561287.0432 | 1163462.5168
77 | 2561281.6554 | 1163457.1651 | 2561287.0432 | 1163462.5168
78 | 2561281.6554 | 1163457.1651 | 2561254.9901 | 1163430.6788
79 | 2561223.4794 | 1163400.4639 | 2561229.3796 | 1163405.9341
80 | 2561223.4794 | 1163400.4639 | 2561206.7497 | 1163384.9537
81 | 2561229.3796 | 1163405.9341 | 2561239.8662 | 1163415.6563 | 2561245.0196 | 1163420.7751
82 | 2561199.2171 | 1163377.9701 | 2561206.7497 | 1163384.9537
83 | 2561245.0196 | 1163420.7751 | 2561253.1326 | 1163428.8337
84 | 2561199.2171 | 1163377.9701 | 2561181.7365 | 1163361.7636
85 | 2561253.1326 | 1163428.8337 | 2561254.9901 | 1163430.6788
86 | 2561181.7365 | 1163361.7636 | 2561169.8734 | 1163350.7652
87 | 2561145.3706 | 1163328.0484 | 2561169.8734 | 1163350.7652
88 | 2561141.718 | 1163324.662 | 2561145.3706 | 1163328.0484
89 | 2561785.5888 | 1164511.7627 | 2561771.9196 | 1164482.5137 | 2561771.3029 | 1164480.1948
90 | 2561762.4432 | 1164442.0883 | 2561764.9127 | 1164456.167 | 2561771.3029 | 1164480.1948
91 | 2561762.3809 | 1164441.7333 | 2561762.4432 | 1164442.0883
92 | 2561952.3698 | 1164205.056 | 2561948.7366 | 1164204.5677 | 2561932.4342 | 1164214.6431 | 2561897.1445 | 1164265.3712 | 2561883.9409 | 1164277.592
93 | 2561952.3698 | 1164205.056 | 2561955.4628 | 1164174.7208 | 2561962.2699 | 1164144.3397
94 | 2561883.9409 | 1164277.592 | 2561866.3168 | 1164293.9041 | 2561831.1628 | 1164318.8851 | 2561809.3557 | 1164334.3828
95 | 2561962.2699 | 1164144.3397 | 2561962.2699 | 1164144.3397 | 2561938.8823 | 1164093.9844 | 2561935.3725 | 1164074.9017
96 | 2561933.4139 | 1164052.9868 | 2561932.0284 | 1164056.7198 | 2561935.3725 | 1164074.9017
97 | 2561041.1819 | 1163869.9447 | 2561022.3866 | 1163864.2309 | 2560988.2949 | 1163852.2353 | 2560981.7464 | 1163848.7339
98 | 2561041.1819 | 1163869.9447 | 2561050.3129 | 1163872.7205 | 2561060.1244 | 1163875.2395
99 | 2560981.7464 | 1163848.7339 | 2560963.8925 | 1163839.1874 | 2560958.6501 | 1163835.0107
100 | 2560907.3018 | 1163789.0079 | 2560919.7472 | 1163800.6439 | 2560940.2403 | 1163820.2205 | 2560955.5467 | 1163832.5383 | 2560958.6501 | 1163835.0107
101 | 2560907.3018 | 1163789.0079 | 2560826.2439 | 1163820.4086
102 | 2560826.2439 | 1163820.4086 | 2560837.2902 | 1163832.4205 | 2560851.7372 | 1163847.9786 | 2560854.4914 | 1163851.0289
103 | 2560826.2439 | 1163820.4086 | 2560666.0982 | 1163786.2392
104 | 2560666.0982 | 1163786.2392 | 2560666.59 | 1163777.1424 | 2560656.7972 | 1163761.2092
105 | 2560666.0982 | 1163786.2392 | 2560501.4353 | 1163959.5848
106 | 2560707.5541 | 1164635.0398 | 2560650.5823 | 1164488.6933
107 | 2561933.4139 | 1164052.9868 | 2561923.8474 | 1164039.6073 | 2561915.0974 | 1164025.0026
108 | 2561902.1283 | 1164003.3558 | 2561915.0974 | 1164025.0026
109 | 2560655.7182 | 1163744.8277 | 2560657.7696 | 1163727.4079 | 2560658.7715 | 1163700.3429 | 2560659.0276 | 1163696.6175
110 | 2560656.7972 | 1163761.2092 | 2560654.2728 | 1163757.1018 | 2560655.7182 | 1163744.8277
111 | 2560516.5547 | 1163973.6881 | 2560501.4353 | 1163959.5848
112 | 2561240.3648 | 1164930.3579 | 2561204.4718 | 1164894.6271
113 | 2561153.4597 | 1164853.8141 | 2561172.466 | 1164862.0508 | 2561186.8746 | 1164872.196 | 2561204.4718 | 1164894.6271
114 | 2561240.3648 | 1164930.3579 | 2561250.3377 | 1164928.3924 | 2561266.7341 | 1164926.2409 | 2561277.2651 | 1164922.9489 | 2561281.6247 | 1164916.2062 | 2561283.04 | 1164908.8932 | 2561280.6383 | 1164899.8485 | 2561270.8934 | 1164888.5167 | 2561267.4361 | 1164884.3857
115 | 2561153.4597 | 1164853.8141 | 2561062.9112 | 1164586.9412
116 | 2561045.4147 | 1164567.2669 | 2561036.1042 | 1164576.9546 | 2561036.7038 | 1164584.3656 | 2561044.1596 | 1164586.2404 | 2561056.2681 | 1164582.86 | 2561062.9112 | 1164586.9412
117 | 2560778.271 | 1164644.8041 | 2561045.4147 | 1164567.2669
118 | 2560778.271 | 1164644.8041 | 2560754.2661 | 1164649.9305 | 2560738.139 | 1164650.0361 | 2560722.6193 | 1164640.3316
119 | 2560778.271 | 1164644.8041 | 2560823.1861 | 1164794.5451
120 | 2560850.3492 | 1164811.397 | 2560885.0929 | 1164829.3203
121 | 2560850.3492 | 1164811.397 | 2560829.995 | 1164800.8912 | 2560823.1861 | 1164794.5451
122 | 2560850.3492 | 1164811.397 | 2560844.9199 | 1164821.949 | 2560834.1976 | 1164831.1127
123 | 2560720.2092 | 1164639.3244 | 2560721.9525 | 1164639.9147 | 2560722.6193 | 1164640.3316
124 | 2560707.5541 | 1164635.0398 | 2560720.2092 | 1164639.3244

## bus_geodata
| x | y | coords
0 | 2561705.8949 | 1164752.1422
1 | 2561717.6429 | 1164785.7758
2 | 2561698.7437 | 1164726.9016
3 | 2561730.8454 | 1164823.5739
4 | 2561701.6184 | 1164704.388
5 | 2561820.3144 | 1164585.0916
6 | 2561797.3602 | 1164536.6249
7 | 2561621.1077 | 1164644.1495
8 | 2561298.5493 | 1163972.0442
9 | 2561293.4229 | 1163982.058
10 | 2561311.3623 | 1163952.2272
11 | 2561192.3713 | 1163916.3776
12 | 2561289.0559 | 1163990.8263
13 | 2561340.7487 | 1163904.6131
14 | 2561170.0007 | 1163938.5561
15 | 2561203.4741 | 1163894.6612
16 | 2561278.4229 | 1164015.2946
17 | 2561468.7884 | 1163938.454
18 | 2561102.892 | 1163884.7618
19 | 2561085.0564 | 1164231.6471
20 | 2561500.3894 | 1163951.7404
21 | 2560838.3371 | 1164239.9465
22 | 2561657.4664 | 1164189.4673
23 | 2561666.8856 | 1164211.7792
24 | 2561639.7696 | 1164164.1355
25 | 2561676.2236 | 1164234.4633
26 | 2561626.6588 | 1164145.3719
27 | 2561687.9745 | 1164261.2585
28 | 2561605.4377 | 1164108.9668
29 | 2561703.9561 | 1164290.8605
30 | 2561598.6998 | 1164090.3714
31 | 2561704.4073 | 1164291.6963
32 | 2561572.9616 | 1164010.0707
33 | 2562084.5962 | 1164497.4008
34 | 2562077.9171 | 1164429.8419
35 | 2562156.7347 | 1164643.1673
36 | 2562081.6967 | 1164406.6741
37 | 2562193.3341 | 1164706.7503
38 | 2562026.755 | 1164294.1193
39 | 2561976.7484 | 1164227.5316
40 | 2562046.4885 | 1164284.5371
41 | 2561582.4858 | 1163834.2801
42 | 2561603.4369 | 1163808.2365
43 | 2561546.7241 | 1163865.7131
44 | 2561617.4557 | 1163754.3496
45 | 2561548.7106 | 1163903.2527
46 | 2561621.3582 | 1163740.5925
47 | 2561550.2626 | 1163932.5804
48 | 2561627.0556 | 1163721.7991
49 | 2561562.2161 | 1163979.736
50 | 2561633.5424 | 1163700.4018
51 | 2561338.4734 | 1163513.6018
52 | 2561332.2167 | 1163507.3871
53 | 2561598.4553 | 1163575.5724
54 | 2561315.7189 | 1163491
55 | 2561647.0805 | 1163653.1457
56 | 2561302.9072 | 1163478.2743
57 | 2561567.5653 | 1164000.8381
58 | 2561712.1519 | 1164306.0412
59 | 2561711.1408 | 1164304.1685
60 | 2561724.547 | 1164325.811
61 | 2561732.5053 | 1164337.5396
62 | 2561732.8002 | 1164337.9742
63 | 2561753.4122 | 1164372.5194
64 | 2561760.8811 | 1164426.8337
65 | 2561774.73 | 1164358.0317
66 | 2561643.6425 | 1163667.0855
67 | 2561636.7686 | 1163689.7598
68 | 2561647.3721 | 1163654.0259
69 | 2561636.3442 | 1163691.1598
70 | 2561297.7815 | 1163473.183
71 | 2561287.0432 | 1163462.5168
72 | 2561281.6554 | 1163457.1651
73 | 2561223.4794 | 1163400.4639
74 | 2561229.3796 | 1163405.9341
75 | 2561206.7497 | 1163384.9537
76 | 2561245.0196 | 1163420.7751
77 | 2561199.2171 | 1163377.9701
78 | 2561253.1326 | 1163428.8337
79 | 2561181.7365 | 1163361.7636
80 | 2561254.9901 | 1163430.6788
81 | 2561169.8734 | 1163350.7652
82 | 2561145.3706 | 1163328.0484
83 | 2561141.718 | 1163324.662
84 | 2561785.5888 | 1164511.7627
85 | 2561771.3029 | 1164480.1948
86 | 2561762.4432 | 1164442.0883
87 | 2561762.3809 | 1164441.7333
88 | 2561952.3698 | 1164205.056
89 | 2561883.9409 | 1164277.592
90 | 2561962.2699 | 1164144.3397
91 | 2561809.3557 | 1164334.3828
92 | 2561935.3725 | 1164074.9017
93 | 2561041.1819 | 1163869.9447
94 | 2560981.7464 | 1163848.7339
95 | 2561060.1244 | 1163875.2395
96 | 2560958.6501 | 1163835.0107
97 | 2560907.3018 | 1163789.0079
98 | 2560826.2439 | 1163820.4086
99 | 2560854.4914 | 1163851.0289
100 | 2560666.0982 | 1163786.2392
101 | 2561533.1473 | 1163967.5527
102 | 2561165.5833 | 1163944.3657
103 | 2560650.5823 | 1164488.6933
104 | 2561933.4139 | 1164052.9868
105 | 2561915.0974 | 1164025.0026
106 | 2561902.1283 | 1164003.3558
107 | 2560659.0276 | 1163696.6175
108 | 2560655.7182 | 1163744.8277
109 | 2560501.4353 | 1163959.5848
110 | 2560516.5547 | 1163973.6881
111 | 2560656.7972 | 1163761.2092
112 | 2561204.4718 | 1164894.6271
113 | 2561240.3648 | 1164930.3579
114 | 2561153.4597 | 1164853.8141
115 | 2561267.4361 | 1164884.3857
116 | 2561062.9112 | 1164586.9412
117 | 2561045.4147 | 1164567.2669
118 | 2560778.271 | 1164644.8041
119 | 2560885.0929 | 1164829.3203
120 | 2560850.3492 | 1164811.397
121 | 2560823.1861 | 1164794.5451
122 | 2560834.1976 | 1164831.1127
123 | 2560722.6193 | 1164640.3316
124 | 2560720.2092 | 1164639.3244
125 | 2560707.5541 | 1164635.0398
126 | 2561567.5653 | 1164000.8381

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97103 | -0.20448 | 0.003824 | 0.00095839
1 | 0.97097 | -0.20493 | 0.00024986 | 6.2621e-05
2 | 0.97122 | -0.20309 | 0.0013299 | 0.0003333
3 | 0.97091 | -0.20533 | 0.00093586 | 0.00023455
4 | 0.97144 | -0.20154 | 0 | 0
5 | 0.97461 | -0.17872 | 0 | 0
6 | 0.97562 | -0.17147 | 0.0016589 | 0.00041576
7 | 0.97048 | -0.20846 | 0.0064956 | 0.0016279
8 | 0.99547 | -0.031563 | 0.001393 | 0.00034913
9 | 0.99536 | -0.032365 | 0.00018382 | 4.6071e-05
10 | 0.99598 | -0.028043 | 0 | 0
11 | 0.99169 | -0.058004 | 0 | 0
12 | 0.99526 | -0.033057 | 0.00028718 | 7.1973e-05
13 | 0.99718 | -0.019651 | 0 | 0
14 | 0.99159 | -0.058687 | 0.0013929 | 0.00034909
15 | 0.99096 | -0.063108 | 0 | 0
16 | 0.99499 | -0.03499 | 0 | 0
17 | 1 | 0 | -0.19506 | -0.049084
18 | 0.98808 | -0.083387 | 0.00023149 | 5.8016e-05
19 | 0.99211 | -0.055224 | 0.0012142 | 0.0003043
20 | 0.99756 | -0.016788 | 0.00084538 | 0.00021187
21 | 0.98981 | -0.071447 | 0.0015692 | 0.00039327
22 | 0.98444 | -0.10861 | 0.0024107 | 0.00060417
23 | 0.98375 | -0.11348 | 0.0019977 | 0.00050067
24 | 0.98535 | -0.10216 | 0.0028159 | 0.00070572
25 | 0.98308 | -0.11825 | 0.0018405 | 0.00046126
26 | 0.98606 | -0.097166 | 0.0050748 | 0.0012719
27 | 0.98231 | -0.12376 | 0.00078612 | 0.00019702
28 | 0.98747 | -0.087242 | 0.0035842 | 0.00089829
29 | 0.98143 | -0.13001 | 0.0047106 | 0.0011806
30 | 0.98816 | -0.08233 | 0.0022853 | 0.00057274
31 | 0.98141 | -0.13017 | 0.0016231 | 0.00040678
32 | 0.99122 | -0.060901 | 0.0031002 | 0.00077698
33 | 0.97141 | -0.20198 | 0.0044063 | 0.0011043
34 | 0.97213 | -0.19678 | 0.00029585 | 7.4146e-05
35 | 0.97073 | -0.20684 | 0.00035851 | 8.985e-05
36 | 0.9724 | -0.1948 | 0 | 0
37 | 0.97047 | -0.20876 | 0.0024554 | 0.00061537
38 | 0.97378 | -0.18483 | 0 | 0
39 | 0.97486 | -0.17704 | 0.0013876 | 0.00034778
40 | 0.97374 | -0.18514 | 0.0013397 | 0.00033577
41 | 0.98607 | -0.096944 | 0.0017416 | 0.00043648
42 | 0.98513 | -0.10356 | 0.001366 | 0.00034236
43 | 0.98745 | -0.087273 | 0 | 0
44 | 0.9836 | -0.11441 | 0.00082186 | 0.00020598
45 | 0.98853 | -0.079663 | 0.0023817 | 0.00059691
46 | 0.98321 | -0.11714 | 0.00054181 | 0.00013579
47 | 0.98941 | -0.073491 | 0.0015821 | 0.00039651
48 | 0.98269 | -0.12085 | 0.0021589 | 0.00054107
49 | 0.99091 | -0.063028 | 0.0036711 | 0.00092006
50 | 0.98212 | -0.12491 | 0.0015083 | 0.00037802
51 | 0.97306 | -0.18957 | 0.0030457 | 0.00076331
52 | 0.97288 | -0.19085 | 0.0043354 | 0.0010866
53 | 0.97884 | -0.14819 | 0.0020604 | 0.0005164
54 | 0.97246 | -0.19387 | 0.004756 | 0.001192
55 | 0.98093 | -0.13332 | 0.00067602 | 0.00016943
56 | 0.97218 | -0.19591 | 0.010981 | 0.002752
57 | 0.99162 | -0.058085 | 0 | 0
58 | 0.98103 | -0.13283 | 0.00065164 | 0.00016332
59 | 0.98108 | -0.1325 | 0.0019107 | 0.00047887
60 | 0.98052 | -0.13646 | 0.00050124 | 0.00012562
61 | 0.98022 | -0.13864 | 0.00028917 | 7.2472e-05
62 | 0.98021 | -0.13872 | 0.0020762 | 0.00052035
63 | 0.97938 | -0.1446 | 0 | 0
64 | 0.97849 | -0.15099 | 0.0018298 | 0.00045859
65 | 0.97913 | -0.14637 | 0.00043449 | 0.00010889
66 | 0.98127 | -0.13091 | 0.0010539 | 0.00026413
67 | 0.98184 | -0.12687 | 0.00068304 | 0.00017118
68 | 0.98095 | -0.13317 | 0.0011659 | 0.0002922
69 | 0.98187 | -0.12661 | 0.0011488 | 0.00028791
70 | 0.9721 | -0.19645 | 0.0016588 | 0.00041574
71 | 0.97196 | -0.19749 | 0.0030481 | 0.00076392
72 | 0.9719 | -0.19793 | 0.0019581 | 0.00049076
73 | 0.97091 | -0.20505 | 0.0013221 | 0.00033134
74 | 0.97103 | -0.20418 | 0.0010148 | 0.00025432
75 | 0.97061 | -0.2072 | 0.0019379 | 0.00048569
76 | 0.97138 | -0.20162 | 0.00048995 | 0.00012279
77 | 0.97051 | -0.20795 | 0.0012602 | 0.00031584
78 | 0.97158 | -0.20021 | 0.0012277 | 0.0003077
79 | 0.97031 | -0.20939 | 0.0011928 | 0.00029894
80 | 0.97163 | -0.19985 | 0.0015385 | 0.00038558
81 | 0.9702 | -0.21016 | 0.0017631 | 0.00044188
82 | 0.97007 | -0.21112 | 0.0016972 | 0.00042536
83 | 0.97006 | -0.21118 | 0.0010234 | 0.00025649
84 | 0.97621 | -0.16728 | 0.0010208 | 0.00025583
85 | 0.977 | -0.16163 | 0.0024776 | 0.00062094
86 | 0.97803 | -0.15425 | 0.00082597 | 0.00020701
87 | 0.97804 | -0.15418 | 0.001555 | 0.00038973
88 | 0.97539 | -0.17326 | 0 | 0
89 | 0.97757 | -0.1576 | 0.0025951 | 0.0006504
90 | 0.975 | -0.17603 | 0.0006273 | 0.00015722
91 | 0.97874 | -0.14918 | 0.0021202 | 0.00053137
92 | 0.9746 | -0.17889 | 0.00098569 | 0.00024704
93 | 0.98631 | -0.095907 | 0.00026022 | 6.5219e-05
94 | 0.9846 | -0.10798 | 0.00017981 | 4.5064e-05
95 | 0.98684 | -0.092105 | 0.00057658 | 0.00014451
96 | 0.98388 | -0.11309 | 0.0028884 | 0.0007239
97 | 0.98233 | -0.12414 | 0 | 0
98 | 0.98038 | -0.13807 | 0 | 0
99 | 0.98014 | -0.13976 | 0.00392 | 0.00098245
100 | 0.97763 | -0.15779 | 0 | 0
101 | 0.99499 | -0.034597 | 0.0010288 | 0.00025785
102 | 0.99158 | -0.058742 | 0.00073837 | 0.00018505
103 | 0.98581 | -0.099759 | 0.0002103 | 5.2706e-05
104 | 0.97452 | -0.17952 | 0 | 0
105 | 0.97439 | -0.18045 | 0.0017047 | 0.00042724
106 | 0.97435 | -0.1807 | 0.00094089 | 0.00023581
107 | 0.97678 | -0.16382 | 0.0041068 | 0.0010293
108 | 0.97707 | -0.16174 | 0.00054223 | 0.0001359
109 | 0.97735 | -0.15982 | 6.6415e-05 | 1.6645e-05
110 | 0.97732 | -0.15998 | 0.00073458 | 0.0001841
111 | 0.97719 | -0.16091 | 0.0060745 | 0.0015224
112 | 0.97235 | -0.19613 | 0.0020645 | 0.00051742
113 | 0.97205 | -0.19826 | 0 | 0
114 | 0.97294 | -0.19185 | 0 | 0
115 | 0.97156 | -0.20176 | 0.0039853 | 0.00099882
116 | 0.97544 | -0.17383 | 0.00051764 | 0.00012973
117 | 0.97591 | -0.17043 | 0.0037702 | 0.00094489
118 | 0.98012 | -0.14025 | 0.00061725 | 0.0001547
119 | 0.979 | -0.14825 | 0.0017267 | 0.00043275
120 | 0.9791 | -0.14754 | 0 | 0
121 | 0.97919 | -0.1469 | 0.0021632 | 0.00054214
122 | 0.9791 | -0.14759 | 0.00018484 | 4.6325e-05
123 | 0.98141 | -0.13099 | 0.0010307 | 0.00025831
124 | 0.98148 | -0.13055 | 0.0013427 | 0.00033652
125 | 0.98182 | -0.12813 | 0 | 0
126 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0011859 | 0.00029628 | -0.0011858 | -0.0002967 | 7.3391e-08 | -4.1245e-07 | 0.0018169 | 0.001817 | 0.001817 | 0.97103 | -0.20448 | 0.97097 | -0.20493 | 0.67298
1 | -0.0050099 | -0.0012547 | 0.0050108 | 0.0012547 | 9.6626e-07 | 4.6541e-08 | 0.0076768 | 0.0076767 | 0.0076768 | 0.97103 | -0.20448 | 0.97122 | -0.20309 | 2.8433
2 | 0.00093591 | 0.00023407 | -0.00093586 | -0.00023455 | 5.139e-08 | -4.7542e-07 | 0.0014341 | 0.0014343 | 0.0014343 | 0.97097 | -0.20493 | 0.97091 | -0.20533 | 0.53122
3 | -0.0063407 | -0.001588 | 0.0063421 | 0.0015883 | 1.3609e-06 | 2.3735e-07 | 0.0097143 | 0.0097142 | 0.0097143 | 0.97122 | -0.20309 | 0.97144 | -0.20154 | 3.5979
4 | 0.0065018 | 0.0016291 | -0.0064956 | -0.0016279 | 6.2235e-06 | 1.15e-06 | 0.0099591 | 0.0099595 | 0.0099595 | 0.97144 | -0.20154 | 0.97048 | -0.20846 | 3.6887
5 | -0.012844 | -0.0032174 | 0.012885 | 0.0032309 | 4.0641e-05 | 1.3541e-05 | 0.019673 | 0.019672 | 0.019673 | 0.97144 | -0.20154 | 0.97461 | -0.17872 | 7.2864
6 | -0.012885 | -0.0032309 | 0.012897 | 0.0032352 | 1.295e-05 | 4.312e-06 | 0.019672 | 0.019672 | 0.019672 | 0.97461 | -0.17872 | 0.97562 | -0.17147 | 7.2861
7 | -0.014556 | -0.003651 | 0.014565 | 0.0036539 | 8.4614e-06 | 2.9107e-06 | 0.022202 | 0.022202 | 0.022202 | 0.97562 | -0.17147 | 0.97621 | -0.16728 | 8.2231
8 | 0.021217 | 0.0053173 | -0.021214 | -0.0053168 | 2.3544e-06 | 4.6666e-07 | 0.031715 | 0.031715 | 0.031715 | 0.99547 | -0.031563 | 0.99536 | -0.032365 | 3.9154
9 | -0.044644 | -0.011217 | 0.044666 | 0.011225 | 2.1878e-05 | 7.4933e-06 | 0.066743 | 0.066743 | 0.066743 | 0.99547 | -0.031563 | 0.99598 | -0.028043 | 8.2399
10 | 0.022034 | 0.0055508 | -0.021953 | -0.0055211 | 8.1204e-05 | 2.968e-05 | 0.032947 | 0.032947 | 0.032947 | 0.99547 | -0.031563 | 0.99169 | -0.058004 | 12.2026
11 | 0.021031 | 0.0052708 | -0.021029 | -0.0052704 | 2.014e-06 | 3.9269e-07 | 0.03144 | 0.03144 | 0.03144 | 0.99536 | -0.032365 | 0.99526 | -0.033057 | 3.8815
12 | -0.044666 | -0.011225 | 0.044718 | 0.011243 | 5.2227e-05 | 1.7884e-05 | 0.066743 | 0.066742 | 0.066743 | 0.99598 | -0.028043 | 0.99718 | -0.019651 | 8.2399
13 | 0.0021315 | 0.00053372 | -0.0021313 | -0.00053405 | 2.0127e-07 | -3.2942e-07 | 0.0031981 | 0.0031982 | 0.0031982 | 0.99169 | -0.058004 | 0.99159 | -0.058687 | 1.1845
14 | 0.019822 | 0.0049874 | -0.019807 | -0.0049823 | 1.4107e-05 | 5.0963e-06 | 0.029749 | 0.029749 | 0.029749 | 0.99169 | -0.058004 | 0.99096 | -0.063108 | 11.0182
15 | 0.020741 | 0.0051984 | -0.020736 | -0.0051973 | 5.5519e-06 | 1.0536e-06 | 0.031011 | 0.031011 | 0.031011 | 0.99526 | -0.033057 | 0.99499 | -0.03499 | 3.8285
16 | -0.044718 | -0.011243 | 0.044841 | 0.011285 | 0.0001227 | 4.1996e-05 | 0.066742 | 0.06674 | 0.066742 | 0.99718 | -0.019651 | 1 | 0 | 8.2398
17 | 0.00073837 | 0.00018496 | -0.00073837 | -0.00018505 | 5.6002e-09 | -9.2145e-08 | 0.001108 | 0.001108 | 0.001108 | 0.99159 | -0.058687 | 0.99158 | -0.058742 | 0.41038
18 | 0.019807 | 0.0049823 | -0.019752 | -0.0049621 | 5.5866e-05 | 2.0188e-05 | 0.029749 | 0.02975 | 0.02975 | 0.99096 | -0.063108 | 0.98808 | -0.083387 | 11.0184
19 | 0.020736 | 0.0051973 | -0.020678 | -0.0051863 | 5.805e-05 | 1.1053e-05 | 0.031011 | 0.031015 | 0.031015 | 0.99499 | -0.03499 | 0.99211 | -0.055224 | 3.829
20 | 0.14942 | 0.037799 | -0.14906 | -0.037665 | 0.00035302 | 0.00013443 | 0.22246 | 0.22246 | 0.22246 | 1 | 0 | 0.99756 | -0.016788 | 27.4642
21 | 0.01952 | 0.0049041 | -0.019496 | -0.0048956 | 2.3646e-05 | 8.5337e-06 | 0.029401 | 0.029401 | 0.029401 | 0.98808 | -0.083387 | 0.98684 | -0.092105 | 10.8893
22 | 0.019464 | 0.004882 | -0.01942 | -0.0048747 | 4.3767e-05 | 7.2925e-06 | 0.029194 | 0.029197 | 0.029197 | 0.99211 | -0.055224 | 0.98981 | -0.071447 | 3.6046
23 | 0.14822 | 0.037453 | -0.14785 | -0.037312 | 0.00037056 | 0.0001411 | 0.2212 | 0.2212 | 0.2212 | 0.99756 | -0.016788 | 0.99499 | -0.034597 | 27.3086
24 | 0.017851 | 0.0044814 | -0.017781 | -0.0044625 | 7.0046e-05 | 1.8962e-05 | 0.026838 | 0.026841 | 0.026841 | 0.98981 | -0.071447 | 0.98581 | -0.099759 | 4.9706
25 | 0.058731 | 0.014752 | -0.058691 | -0.014738 | 3.9747e-05 | 1.4363e-05 | 0.088785 | 0.088785 | 0.088785 | 0.98444 | -0.10861 | 0.98375 | -0.11348 | 10.9612
26 | -0.061141 | -0.015356 | 0.061196 | 0.015376 | 5.491e-05 | 1.9939e-05 | 0.092429 | 0.092428 | 0.092429 | 0.98444 | -0.10861 | 0.98535 | -0.10216 | 11.411
27 | 0.056693 | 0.014237 | -0.056656 | -0.014224 | 3.7531e-05 | 1.3501e-05 | 0.085764 | 0.085764 | 0.085764 | 0.98375 | -0.11348 | 0.98308 | -0.11825 | 10.5882
28 | -0.064012 | -0.016082 | 0.064057 | 0.016098 | 4.4504e-05 | 1.6241e-05 | 0.096681 | 0.09668 | 0.096681 | 0.98535 | -0.10216 | 0.98606 | -0.097166 | 11.9359
29 | 0.054815 | 0.013762 | -0.054773 | -0.013747 | 4.1942e-05 | 1.5018e-05 | 0.082978 | 0.082979 | 0.082979 | 0.98308 | -0.11825 | 0.98231 | -0.12376 | 10.2443
30 | -0.069131 | -0.01737 | 0.069227 | 0.017405 | 9.5587e-05 | 3.5146e-05 | 0.10434 | 0.10434 | 0.10434 | 0.98606 | -0.097166 | 0.98747 | -0.087242 | 12.8813
31 | 0.053987 | 0.01355 | -0.05394 | -0.013534 | 4.6807e-05 | 1.6726e-05 | 0.081788 | 0.081788 | 0.081788 | 0.98231 | -0.12376 | 0.98143 | -0.13001 | 10.0973
32 | -0.072811 | -0.018304 | 0.072861 | 0.018322 | 4.984e-05 | 1.8405e-05 | 0.10974 | 0.10974 | 0.10974 | 0.98747 | -0.087242 | 0.98816 | -0.08233 | 13.548
33 | 0.04923 | 0.012353 | -0.049229 | -0.012353 | 1.1007e-06 | 3.8736e-07 | 0.074646 | 0.074646 | 0.074646 | 0.98143 | -0.13001 | 0.98141 | -0.13017 | 9.2156
34 | -0.075146 | -0.018895 | 0.075371 | 0.018978 | 0.00022503 | 8.3295e-05 | 0.11318 | 0.11318 | 0.11318 | 0.98816 | -0.08233 | 0.99122 | -0.060901 | 13.9728
35 | 0.047606 | 0.011946 | -0.04759 | -0.011941 | 1.5362e-05 | 5.3713e-06 | 0.072185 | 0.072185 | 0.072185 | 0.98141 | -0.13017 | 0.98108 | -0.1325 | 8.9118
36 | -0.078472 | -0.019755 | 0.078502 | 0.019766 | 3.0884e-05 | 1.1465e-05 | 0.11783 | 0.11783 | 0.11783 | 0.99122 | -0.060901 | 0.99162 | -0.058085 | 14.5473
37 | -0.0072227 | -0.0018076 | 0.0072279 | 0.0018087 | 5.1858e-06 | 1.1533e-06 | 0.011063 | 0.011063 | 0.011063 | 0.97141 | -0.20198 | 0.97213 | -0.19678 | 4.0974
38 | 0.0028164 | 0.00070327 | -0.0028145 | -0.00070456 | 1.8884e-06 | -1.2857e-06 | 0.0043133 | 0.004314 | 0.004314 | 0.97141 | -0.20198 | 0.97073 | -0.20684 | 1.5978
39 | -0.0075237 | -0.0018829 | 0.0075258 | 0.0018834 | 2.0503e-06 | 4.8129e-07 | 0.011515 | 0.011515 | 0.011515 | 0.97213 | -0.19678 | 0.9724 | -0.1948 | 4.265
40 | 0.002456 | 0.00061471 | -0.0024554 | -0.00061537 | 6.5209e-07 | -6.6052e-07 | 0.0037645 | 0.0037648 | 0.0037648 | 0.97073 | -0.20684 | 0.97047 | -0.20876 | 1.3944
41 | -0.0075258 | -0.0018834 | 0.0075361 | 0.0018858 | 1.0363e-05 | 2.4299e-06 | 0.011515 | 0.011515 | 0.011515 | 0.9724 | -0.1948 | 0.97378 | -0.18483 | 4.2649
42 | -0.0088759 | -0.0022213 | 0.0088855 | 0.002224 | 9.5575e-06 | 2.6388e-06 | 0.013562 | 0.013562 | 0.013562 | 0.97378 | -0.18483 | 0.97486 | -0.17704 | 5.023
43 | 0.0013398 | 0.00033552 | -0.0013397 | -0.00033577 | 5.7374e-08 | -2.5082e-07 | 0.0020472 | 0.0020473 | 0.0020473 | 0.97378 | -0.18483 | 0.97374 | -0.18514 | 0.75827
44 | -0.010273 | -0.0025717 | 0.010278 | 0.0025734 | 5.3584e-06 | 1.6252e-06 | 0.01568 | 0.01568 | 0.01568 | 0.97486 | -0.17704 | 0.97539 | -0.17326 | 5.8073
45 | 0.058119 | 0.01463 | -0.058065 | -0.014611 | 5.367e-05 | 1.9361e-05 | 0.087726 | 0.087727 | 0.087727 | 0.98607 | -0.096944 | 0.98513 | -0.10356 | 10.8304
46 | -0.05986 | -0.015067 | 0.059941 | 0.015096 | 8.0932e-05 | 2.9301e-05 | 0.090354 | 0.090354 | 0.090354 | 0.98607 | -0.096944 | 0.98745 | -0.087273 | 11.1548
47 | 0.056699 | 0.014269 | -0.056613 | -0.014238 | 8.5716e-05 | 3.0826e-05 | 0.085663 | 0.085664 | 0.085664 | 0.98513 | -0.10356 | 0.9836 | -0.11441 | 10.5758
48 | -0.059941 | -0.015096 | 0.060005 | 0.015119 | 6.3834e-05 | 2.3107e-05 | 0.090354 | 0.090353 | 0.090354 | 0.98745 | -0.087273 | 0.98853 | -0.079663 | 11.1548
49 | 0.055792 | 0.014032 | -0.05577 | -0.014024 | 2.1212e-05 | 7.6138e-06 | 0.084421 | 0.084421 | 0.084421 | 0.9836 | -0.11441 | 0.98321 | -0.11714 | 10.4223
50 | -0.062387 | -0.015716 | 0.062441 | 0.015736 | 5.3905e-05 | 1.9602e-05 | 0.093938 | 0.093938 | 0.093938 | 0.98853 | -0.079663 | 0.98941 | -0.073491 | 11.5973
51 | 0.055229 | 0.013888 | -0.0552 | -0.013878 | 2.8549e-05 | 1.0233e-05 | 0.083601 | 0.083601 | 0.083601 | 0.98321 | -0.11714 | 0.98269 | -0.12085 | 10.3211
52 | -0.064023 | -0.016132 | 0.064117 | 0.016166 | 9.3869e-05 | 3.4226e-05 | 0.096317 | 0.096316 | 0.096317 | 0.98941 | -0.073491 | 0.99091 | -0.063028 | 11.891
53 | 0.053041 | 0.013337 | -0.053011 | -0.013326 | 3.0012e-05 | 1.0694e-05 | 0.080332 | 0.080332 | 0.080332 | 0.98269 | -0.12085 | 0.98212 | -0.12491 | 9.9176
54 | -0.067788 | -0.017087 | 0.067835 | 0.017104 | 4.6952e-05 | 1.7217e-05 | 0.10183 | 0.10183 | 0.10183 | 0.99091 | -0.063028 | 0.99162 | -0.058085 | 12.5715
55 | 0.051503 | 0.012948 | -0.051491 | -0.012944 | 1.2236e-05 | 4.3396e-06 | 0.078047 | 0.078047 | 0.078047 | 0.98212 | -0.12491 | 0.98187 | -0.12661 | 9.6355
56 | 0.041259 | 0.010342 | -0.041252 | -0.010339 | 7.3022e-06 | 2.4799e-06 | 0.063095 | 0.063095 | 0.063095 | 0.97306 | -0.18957 | 0.97288 | -0.19085 | 7.7895
57 | -0.044305 | -0.011105 | 0.04456 | 0.011193 | 0.00025517 | 8.8123e-05 | 0.067752 | 0.067748 | 0.067752 | 0.97306 | -0.18957 | 0.97884 | -0.14819 | 8.3645
58 | 0.036916 | 0.0092525 | -0.036901 | -0.0092474 | 1.542e-05 | 5.065e-06 | 0.056464 | 0.056464 | 0.056464 | 0.97288 | -0.19085 | 0.97246 | -0.19387 | 6.9709
59 | -0.04662 | -0.011709 | 0.046717 | 0.011743 | 9.6502e-05 | 3.3626e-05 | 0.070881 | 0.070879 | 0.070881 | 0.97884 | -0.14819 | 0.98093 | -0.13332 | 8.7507
60 | 0.032145 | 0.0080555 | -0.032136 | -0.0080526 | 9.0871e-06 | 2.8231e-06 | 0.049187 | 0.049187 | 0.049187 | 0.97246 | -0.19387 | 0.97218 | -0.19591 | 6.0725
61 | -0.047393 | -0.011912 | 0.047394 | 0.011913 | 9.9724e-07 | 3.4843e-07 | 0.071905 | 0.071905 | 0.071905 | 0.98093 | -0.13332 | 0.98095 | -0.13317 | 8.8772
62 | 0.021155 | 0.0053007 | -0.021154 | -0.0053003 | 1.5755e-06 | 3.3726e-07 | 0.03238 | 0.03238 | 0.03238 | 0.97218 | -0.19591 | 0.9721 | -0.19645 | 3.9976
63 | -0.14634 | -0.03687 | 0.14682 | 0.037054 | 0.00048251 | 0.00018371 | 0.21966 | 0.21966 | 0.21966 | 0.99162 | -0.058085 | 0.99499 | -0.034597 | 27.1187
64 | -0.045677 | -0.011461 | 0.045679 | 0.011462 | 2.1252e-06 | 7.3676e-07 | 0.069287 | 0.069287 | 0.069287 | 0.98103 | -0.13283 | 0.98108 | -0.1325 | 8.554
65 | 0.045026 | 0.011298 | -0.045003 | -0.01129 | 2.2667e-05 | 7.8337e-06 | 0.068299 | 0.068299 | 0.068299 | 0.98103 | -0.13283 | 0.98052 | -0.13646 | 8.432
66 | 0.044502 | 0.011164 | -0.044488 | -0.01116 | 1.3448e-05 | 4.6361e-06 | 0.067539 | 0.067539 | 0.067539 | 0.98052 | -0.13646 | 0.98022 | -0.13864 | 8.3381
67 | 0.044199 | 0.011087 | -0.044199 | -0.011087 | 4.9187e-07 | 1.6932e-07 | 0.0671 | 0.0671 | 0.0671 | 0.98022 | -0.13864 | 0.98021 | -0.13872 | 8.2839
68 | 0.042122 | 0.010567 | -0.042088 | -0.010555 | 3.4318e-05 | 1.1675e-05 | 0.063948 | 0.063949 | 0.063949 | 0.98021 | -0.13872 | 0.97938 | -0.1446 | 7.8949
69 | 0.022334 | 0.0056065 | -0.022314 | -0.0056002 | 1.9805e-05 | 6.2314e-06 | 0.033936 | 0.033936 | 0.033936 | 0.97938 | -0.1446 | 0.97849 | -0.15099 | 6.2845
70 | 0.019754 | 0.0049484 | -0.01975 | -0.0049475 | 4.8292e-06 | 8.8459e-07 | 0.030013 | 0.030013 | 0.030013 | 0.97938 | -0.1446 | 0.97913 | -0.14637 | 3.7053
71 | 0.020484 | 0.0051416 | -0.020475 | -0.0051383 | 9.0772e-06 | 3.3031e-06 | 0.031154 | 0.031154 | 0.031154 | 0.97849 | -0.15099 | 0.97804 | -0.15418 | 11.5385
72 | 0.019315 | 0.0048386 | -0.019308 | -0.0048373 | 7.5148e-06 | 1.3087e-06 | 0.029353 | 0.029353 | 0.029353 | 0.97913 | -0.14637 | 0.97874 | -0.14918 | 3.6239
73 | -0.049629 | -0.012474 | 0.049657 | 0.012484 | 2.7922e-05 | 9.8408e-06 | 0.075271 | 0.075271 | 0.075271 | 0.98127 | -0.13091 | 0.98184 | -0.12687 | 9.2928
74 | 0.048575 | 0.01221 | -0.04856 | -0.012205 | 1.5335e-05 | 5.3833e-06 | 0.073673 | 0.073673 | 0.073673 | 0.98127 | -0.13091 | 0.98095 | -0.13317 | 9.0955
75 | -0.05034 | -0.012655 | 0.050342 | 0.012656 | 1.7718e-06 | 6.2594e-07 | 0.076306 | 0.076306 | 0.076306 | 0.98184 | -0.12687 | 0.98187 | -0.12661 | 9.4205
76 | 0.019495 | 0.0048846 | -0.019492 | -0.0048841 | 2.8034e-06 | 5.1539e-07 | 0.029841 | 0.029841 | 0.029841 | 0.9721 | -0.19645 | 0.97196 | -0.19749 | 3.6841
77 | 0.016444 | 0.0041202 | -0.016443 | -0.00412 | 1.0011e-06 | 1.0269e-07 | 0.025175 | 0.025175 | 0.025175 | 0.97196 | -0.19749 | 0.9719 | -0.19793 | 3.108
78 | 0.014485 | 0.0036293 | -0.014481 | -0.0036292 | 3.8448e-06 | 8.1907e-08 | 0.022177 | 0.022177 | 0.022177 | 0.9719 | -0.19793 | 0.97163 | -0.19985 | 2.7379
79 | -0.010202 | -0.0025562 | 0.010203 | 0.0025566 | 1.2274e-06 | 3.7256e-07 | 0.015636 | 0.015635 | 0.015636 | 0.97091 | -0.20505 | 0.97103 | -0.20418 | 5.7909
80 | 0.00888 | 0.0022249 | -0.0088774 | -0.0022241 | 2.6366e-06 | 7.3204e-07 | 0.013609 | 0.013609 | 0.013609 | 0.97091 | -0.20505 | 0.97061 | -0.2072 | 5.0405
81 | -0.011218 | -0.0028109 | 0.011222 | 0.0028122 | 3.9763e-06 | 1.2625e-06 | 0.01719 | 0.01719 | 0.01719 | 0.97103 | -0.20418 | 0.97138 | -0.20162 | 6.3669
82 | 0.0069395 | 0.0017385 | -0.0069387 | -0.0017383 | 7.2542e-07 | 1.5207e-07 | 0.010638 | 0.010638 | 0.010638 | 0.97061 | -0.2072 | 0.97051 | -0.20795 | 3.9402
83 | -0.011712 | -0.002935 | 0.011714 | 0.0029357 | 2.2967e-06 | 7.4178e-07 | 0.017941 | 0.017941 | 0.017941 | 0.97138 | -0.20162 | 0.97158 | -0.20021 | 6.6448
84 | 0.0056785 | 0.0014225 | -0.0056774 | -0.0014223 | 1.1275e-06 | 1.3915e-07 | 0.0087062 | 0.0087063 | 0.0087063 | 0.97051 | -0.20795 | 0.97031 | -0.20939 | 3.2246
85 | -0.012942 | -0.0032434 | 0.012943 | 0.0032436 | 6.4185e-07 | 2.1444e-07 | 0.019821 | 0.019821 | 0.019821 | 0.97158 | -0.20021 | 0.97163 | -0.19985 | 7.3412
86 | 0.0044846 | 0.0011234 | -0.0044841 | -0.0011234 | 4.7743e-07 | -1.6169e-08 | 0.0068771 | 0.0068772 | 0.0068772 | 0.97031 | -0.20939 | 0.9702 | -0.21016 | 2.5471
87 | 0.002721 | 0.00068152 | -0.0027206 | -0.0006818 | 3.6311e-07 | -2.7291e-07 | 0.0041731 | 0.0041733 | 0.0041733 | 0.9702 | -0.21016 | 0.97007 | -0.21112 | 1.5456
88 | 0.0010234 | 0.00025644 | -0.0010234 | -0.00025649 | 7.6598e-09 | -5.8546e-08 | 0.0015698 | 0.0015699 | 0.0015699 | 0.97007 | -0.21112 | 0.97006 | -0.21118 | 0.58143
89 | -0.015586 | -0.0039097 | 0.015598 | 0.003914 | 1.2217e-05 | 4.2647e-06 | 0.023758 | 0.023758 | 0.023758 | 0.97621 | -0.16728 | 0.977 | -0.16163 | 8.7993
90 | -0.018075 | -0.0045349 | 0.018094 | 0.0045415 | 1.852e-05 | 6.6323e-06 | 0.027532 | 0.027531 | 0.027532 | 0.977 | -0.16163 | 0.97803 | -0.15425 | 10.1969
91 | -0.01892 | -0.0047485 | 0.01892 | 0.0047486 | 1.8642e-07 | 6.7176e-08 | 0.028788 | 0.028788 | 0.028788 | 0.97803 | -0.15425 | 0.97804 | -0.15418 | 10.6622
92 | -0.014541 | -0.0036394 | 0.014572 | 0.0036502 | 3.1504e-05 | 1.0833e-05 | 0.022181 | 0.022181 | 0.022181 | 0.97539 | -0.17326 | 0.97757 | -0.1576 | 8.2152
93 | 0.0042622 | 0.001066 | -0.0042606 | -0.0010661 | 1.6256e-06 | -1.4367e-07 | 0.0065015 | 0.0065018 | 0.0065018 | 0.97539 | -0.17326 | 0.975 | -0.17603 | 2.4081
94 | -0.017167 | -0.0043006 | 0.017187 | 0.0043059 | 2.0002e-05 | 5.3361e-06 | 0.026131 | 0.02613 | 0.026131 | 0.97757 | -0.1576 | 0.97874 | -0.14918 | 4.839
95 | 0.0036333 | 0.00090892 | -0.0036319 | -0.0009093 | 1.4373e-06 | -3.8123e-07 | 0.0055444 | 0.0055448 | 0.0055448 | 0.975 | -0.17603 | 0.9746 | -0.17889 | 2.0536
96 | 0.0026462 | 0.00066227 | -0.002646 | -0.00066246 | 2.2882e-07 | -1.9196e-07 | 0.0040398 | 0.0040399 | 0.0040399 | 0.9746 | -0.17889 | 0.97452 | -0.17952 | 1.4963
97 | 0.01865 | 0.0046823 | -0.018618 | -0.0046711 | 3.1232e-05 | 1.1207e-05 | 0.028139 | 0.02814 | 0.02814 | 0.98631 | -0.095907 | 0.9846 | -0.10798 | 10.422
98 | -0.01891 | -0.0047475 | 0.01892 | 0.0047511 | 9.9936e-06 | 3.5925e-06 | 0.028532 | 0.028532 | 0.028532 | 0.98631 | -0.095907 | 0.98684 | -0.092105 | 10.5673
99 | 0.018439 | 0.004626 | -0.018426 | -0.0046213 | 1.306e-05 | 4.6804e-06 | 0.027868 | 0.027868 | 0.027868 | 0.9846 | -0.10798 | 0.98388 | -0.11309 | 10.3214
100 | 0.015537 | 0.0038974 | -0.015513 | -0.0038891 | 2.3775e-05 | 8.2694e-06 | 0.0235 | 0.0235 | 0.0235 | 0.98388 | -0.11309 | 0.98233 | -0.12414 | 8.7036
101 | 0.015513 | 0.0038891 | -0.015484 | -0.0038788 | 2.988e-05 | 1.0397e-05 | 0.0235 | 0.0235 | 0.0235 | 0.98233 | -0.12414 | 0.98038 | -0.13807 | 8.7038
102 | 0.0039209 | 0.00098228 | -0.00392 | -0.00098245 | 9.1959e-07 | -1.7088e-07 | 0.0059511 | 0.0059513 | 0.0059513 | 0.98038 | -0.13807 | 0.98014 | -0.13976 | 2.2042
103 | 0.011563 | 0.0028965 | -0.011531 | -0.0028864 | 3.147e-05 | 1.0045e-05 | 0.017549 | 0.01755 | 0.01755 | 0.98038 | -0.13807 | 0.97763 | -0.15779 | 6.5
104 | 0.01073 | 0.0026888 | -0.010725 | -0.0026874 | 4.6289e-06 | 1.4318e-06 | 0.016332 | 0.016332 | 0.016332 | 0.97763 | -0.15779 | 0.97719 | -0.16091 | 6.0488
105 | 0.00080124 | 0.00019758 | -0.00080102 | -0.0002005 | 2.2166e-07 | -2.9117e-06 | 0.0012184 | 0.0012195 | 0.0012195 | 0.97763 | -0.15779 | 0.97735 | -0.15982 | 0.45165
106 | 0.01757 | 0.0044098 | -0.017501 | -0.0043852 | 6.8943e-05 | 2.4522e-05 | 0.026524 | 0.026524 | 0.026524 | 0.98581 | -0.099759 | 0.98182 | -0.12813 | 9.8239
107 | 0.002646 | 0.00066246 | -0.0026456 | -0.00066275 | 3.4092e-07 | -2.8587e-07 | 0.0040399 | 0.0040401 | 0.0040401 | 0.97452 | -0.17952 | 0.97439 | -0.18045 | 1.4963
108 | 0.00094093 | 0.00023551 | -0.00094089 | -0.00023581 | 3.2509e-08 | -3.018e-07 | 0.0014368 | 0.0014369 | 0.0014369 | 0.97439 | -0.18045 | 0.97435 | -0.1807 | 0.53219
109 | -0.0041068 | -0.0010293 | 0.004108 | 0.0010291 | 1.1811e-06 | -1.5124e-07 | 0.0062563 | 0.0062561 | 0.0062563 | 0.97678 | -0.16382 | 0.97707 | -0.16174 | 2.3171
110 | -0.0046502 | -0.001165 | 0.0046508 | 0.001165 | 5.3764e-07 | -8.4129e-09 | 0.0070818 | 0.0070818 | 0.0070818 | 0.97707 | -0.16174 | 0.97719 | -0.16091 | 2.6229
111 | 0.0007346 | 0.00018385 | -0.00073458 | -0.0001841 | 1.6138e-08 | -2.5289e-07 | 0.0011183 | 0.0011184 | 0.0011184 | 0.97735 | -0.15982 | 0.97732 | -0.15998 | 0.41424
112 | 0.0039884 | 0.00099836 | -0.0039873 | -0.00099853 | 1.1772e-06 | -1.7523e-07 | 0.0061032 | 0.0061034 | 0.0061034 | 0.97235 | -0.19613 | 0.97205 | -0.19826 | 2.2605
113 | -0.006053 | -0.0015158 | 0.0060565 | 0.0015163 | 3.5786e-06 | 5.4674e-07 | 0.0092626 | 0.0092623 | 0.0092626 | 0.97235 | -0.19613 | 0.97294 | -0.19185 | 3.4306
114 | 0.0039873 | 0.00099853 | -0.0039853 | -0.00099882 | 1.9272e-06 | -2.8594e-07 | 0.0061034 | 0.0061038 | 0.0061038 | 0.97205 | -0.19826 | 0.97156 | -0.20176 | 2.2607
115 | -0.0060565 | -0.0015163 | 0.0060716 | 0.0015186 | 1.5084e-05 | 2.2929e-06 | 0.0092623 | 0.009261 | 0.0092623 | 0.97294 | -0.19185 | 0.97544 | -0.17383 | 3.4305
116 | -0.0065893 | -0.0016483 | 0.0065923 | 0.0016489 | 3.0841e-06 | 5.7513e-07 | 0.010051 | 0.01005 | 0.010051 | 0.97544 | -0.17383 | 0.97591 | -0.17043 | 3.7225
117 | -0.010362 | -0.0025938 | 0.010406 | 0.002607 | 4.3323e-05 | 1.3172e-05 | 0.015799 | 0.015798 | 0.015799 | 0.97591 | -0.17043 | 0.98012 | -0.14025 | 5.8515
118 | -0.015102 | -0.0037813 | 0.015121 | 0.003788 | 1.9344e-05 | 6.6956e-06 | 0.022926 | 0.022926 | 0.022926 | 0.98012 | -0.14025 | 0.98141 | -0.13099 | 8.4912
119 | 0.0040788 | 0.0010196 | -0.0040751 | -0.0010201 | 3.74e-06 | -5.299e-07 | 0.0061915 | 0.0061922 | 0.0061922 | 0.98012 | -0.14025 | 0.97919 | -0.1469 | 2.2934
120 | -0.0017267 | -0.00043275 | 0.0017269 | 0.00043233 | 1.6802e-07 | -4.2701e-07 | 0.0026245 | 0.0026243 | 0.0026245 | 0.979 | -0.14825 | 0.9791 | -0.14754 | 0.97202
121 | -0.0019117 | -0.00047832 | 0.0019119 | 0.00047798 | 1.6964e-07 | -3.3993e-07 | 0.0029051 | 0.0029049 | 0.0029051 | 0.9791 | -0.14754 | 0.97919 | -0.1469 | 1.076
122 | 0.00018484 | 4.5999e-05 | -0.00018484 | -4.6325e-05 | 1.2784e-09 | -3.2614e-07 | 0.0002808 | 0.00028092 | 0.00028092 | 0.9791 | -0.14754 | 0.9791 | -0.14759 | 0.10404
123 | -0.016152 | -0.0040463 | 0.016153 | 0.0040466 | 9.8305e-07 | 3.449e-07 | 0.024489 | 0.024489 | 0.024489 | 0.98141 | -0.13099 | 0.98148 | -0.13055 | 9.0699
124 | -0.017496 | -0.0043832 | 0.017501 | 0.0043852 | 5.8656e-06 | 2.0871e-06 | 0.026525 | 0.026524 | 0.026525 | 0.98148 | -0.13055 | 0.98182 | -0.12813 | 9.8239

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19583 | 0.049278

## res_load
| p_mw | q_mvar
0 | 0.003824 | 0.00095839
1 | 0.00024986 | 6.2621e-05
2 | 0.0013299 | 0.0003333
3 | 0.00093586 | 0.00023455
4 | 0.0016589 | 0.00041576
5 | 0.0064956 | 0.0016279
6 | 0.001393 | 0.00034913
7 | 0.00018382 | 4.6071e-05
8 | 0.00028718 | 7.1973e-05
9 | 0.0013929 | 0.00034909
10 | 0.00077464 | 0.00019414
11 | 0.00023149 | 5.8016e-05
12 | 0.0012142 | 0.0003043
13 | 0.00084538 | 0.00021187
14 | 0.0015692 | 0.00039327
15 | 0.0024107 | 0.00060417
16 | 0.0019977 | 0.00050067
17 | 0.0028159 | 0.00070572
18 | 0.0018405 | 0.00046126
19 | 0.0050748 | 0.0012719
20 | 0.00078612 | 0.00019702
21 | 0.0035842 | 0.00089829
22 | 0.0047106 | 0.0011806
23 | 0.0022853 | 0.00057274
24 | 0.0016231 | 0.00040678
25 | 0.0031002 | 0.00077698
26 | 0.0044063 | 0.0011043
27 | 0.00029585 | 7.4146e-05
28 | 0.00035851 | 8.985e-05
29 | 0.0024554 | 0.00061537
30 | 0.0013876 | 0.00034778
31 | 0.0013397 | 0.00033577
32 | 0.0017416 | 0.00043648
33 | 0.001366 | 0.00034236
34 | 0.00082186 | 0.00020598
35 | 0.0023817 | 0.00059691
36 | 0.00054181 | 0.00013579
37 | 0.0015821 | 0.00039651
38 | 0.0021589 | 0.00054107
39 | 0.0036711 | 0.00092006
40 | 0.0015083 | 0.00037802
41 | 0.0030457 | 0.00076331
42 | 0.0043354 | 0.0010866
43 | 0.0020604 | 0.0005164
44 | 0.004756 | 0.001192
45 | 0.00067602 | 0.00016943
46 | 0.010981 | 0.002752
47 | 0.00065164 | 0.00016332
48 | 0.0019107 | 0.00047887
49 | 0.00050124 | 0.00012562
50 | 0.00028917 | 7.2472e-05
51 | 0.0020762 | 0.00052035
52 | 0.0018298 | 0.00045859
53 | 0.00043449 | 0.00010889
54 | 0.0010539 | 0.00026413
55 | 0.00068304 | 0.00017118
56 | 0.0011659 | 0.0002922
57 | 0.0011488 | 0.00028791
58 | 0.0016588 | 0.00041574
59 | 0.0030481 | 0.00076392
60 | 0.0019581 | 0.00049076
61 | 0.0013221 | 0.00033134
62 | 0.0010148 | 0.00025432
63 | 0.0019379 | 0.00048569
64 | 0.00048995 | 0.00012279
65 | 0.0012602 | 0.00031584
66 | 0.0012277 | 0.0003077
67 | 0.0011928 | 0.00029894
68 | 0.0015385 | 0.00038558
69 | 0.0017631 | 0.00044188
70 | 0.0016972 | 0.00042536
71 | 0.0010234 | 0.00025649
72 | 0.0010208 | 0.00025583
73 | 0.0024776 | 0.00062094
74 | 0.00082597 | 0.00020701
75 | 0.001555 | 0.00038973
76 | 0.0025951 | 0.0006504
77 | 0.0006273 | 0.00015722
78 | 0.0021202 | 0.00053137
79 | 0.00098569 | 0.00024704
80 | 0.00026022 | 6.5219e-05
81 | 0.00017981 | 4.5064e-05
82 | 0.00057658 | 0.00014451
83 | 0.0028884 | 0.0007239
84 | 0.00392 | 0.00098245
85 | 0.0010288 | 0.00025785
86 | 0.00073837 | 0.00018505
87 | 0.0002103 | 5.2706e-05
88 | 0.0017047 | 0.00042724
89 | 0.00094089 | 0.00023581
90 | 0.0041068 | 0.0010293
91 | 0.00054223 | 0.0001359
92 | 6.6415e-05 | 1.6645e-05
93 | 0.00073458 | 0.0001841
94 | 0.0060745 | 0.0015224
95 | 0.0020645 | 0.00051742
96 | 0.0039853 | 0.00099882
97 | 0.00051764 | 0.00012973
98 | 0.0037702 | 0.00094489
99 | 0.00061725 | 0.0001547
100 | 0.0017267 | 0.00043275
101 | 0.0021632 | 0.00054214
102 | 0.00018484 | 4.6325e-05
103 | 0.0010307 | 0.00025831
104 | 0.0013427 | 0.00033652

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1