## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2113-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2113-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2113-7_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2113-7_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2113-7_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2113-7_0_3_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2113-7_0_3_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_2113-7_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2113-7_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2113-7_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2113-7_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2113-7_0_3_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_2113-7_0_3_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_2113-7_0_3_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_2113-7_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2113-7_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2113-7_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2113-7_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2113-7_0_3_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_2113-7_0_3_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_2113-7_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_2113-7_0_3_node_113 | 0.4 | n |  | TRUE
22 | bus_LV_2113-7_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_2113-7_0_3_node_112 | 0.4 | n |  | TRUE
24 | bus_LV_2113-7_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2113-7_0_3_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_2113-7_0_3_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_2113-7_0_3_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_2113-7_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_2113-7_0_3_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_2113-7_0_3_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_2113-7_0_3_node_73 | 0.4 | n |  | TRUE
32 | bus_LV_2113-7_0_3_node_72 | 0.4 | n |  | TRUE
33 | bus_LV_2113-7_0_3_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_2113-7_0_3_node_114 | 0.4 | n |  | TRUE
35 | bus_LV_2113-7_0_3_node_115 | 0.4 | n |  | TRUE
36 | bus_LV_2113-7_0_3_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_2113-7_0_3_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_2113-7_0_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2113-7_0_3_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_2113-7_0_3_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_2113-7_0_3_node_76 | 0.4 | n |  | TRUE
42 | bus_LV_2113-7_0_3_node_78 | 0.4 | n |  | TRUE
43 | bus_LV_2113-7_0_3_node_75 | 0.4 | n |  | TRUE
44 | bus_LV_2113-7_0_3_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_2113-7_0_3_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_2113-7_0_3_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_2113-7_0_3_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_2113-7_0_3_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_2113-7_0_3_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_2113-7_0_3_node_69 | 0.4 | n |  | TRUE
51 | bus_LV_2113-7_0_3_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_2113-7_0_3_node_68 | 0.4 | n |  | TRUE
53 | bus_LV_2113-7_0_3_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_2113-7_0_3_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_2113-7_0_3_node_44 | 0.4 | n |  | TRUE
56 | bus_LV_2113-7_0_3_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_2113-7_0_3_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_2113-7_0_3_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_2113-7_0_3_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_2113-7_0_3_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_2113-7_0_3_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_2113-7_0_3_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_2113-7_0_3_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_2113-7_0_3_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_2113-7_0_3_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_2113-7_0_3_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_2113-7_0_3_node_56 | 0.4 | n |  | TRUE
68 | bus_LV_2113-7_0_3_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_2113-7_0_3_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_2113-7_0_3_node_59 | 0.4 | n |  | TRUE
71 | bus_LV_2113-7_0_3_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_2113-7_0_3_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_2113-7_0_3_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_2113-7_0_3_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_2113-7_0_3_node_64 | 0.4 | n |  | TRUE
76 | bus_LV_2113-7_0_3_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_2113-7_0_3_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_2113-7_0_3_node_84 | 0.4 | n |  | TRUE
79 | bus_LV_2113-7_0_3_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_2113-7_0_3_node_85 | 0.4 | n |  | TRUE
81 | bus_LV_2113-7_0_3_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_2113-7_0_3_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_2113-7_0_3_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_2113-7_0_3_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_2113-7_0_3_node_77 | 0.4 | n |  | TRUE
86 | bus_LV_2113-7_0_3_node_103 | 0.4 | n |  | TRUE
87 | bus_LV_2113-7_0_3_node_94 | 0.4 | n |  | TRUE
88 | bus_LV_2113-7_0_3_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_2113-7_0_3_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_2113-7_0_3_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_2113-7_0_3_node_83 | 0.4 | n |  | TRUE
92 | bus_LV_2113-7_0_3_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_2113-7_0_3_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_2113-7_0_3_node_87 | 0.4 | n |  | TRUE
95 | bus_LV_2113-7_0_3_node_96 | 0.4 | n |  | TRUE
96 | bus_LV_2113-7_0_3_node_88 | 0.4 | n |  | TRUE
97 | bus_LV_2113-7_0_3_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_2113-7_0_3_node_97 | 0.4 | n |  | TRUE
99 | bus_LV_2113-7_0_3_node_98 | 0.4 | n |  | TRUE
100 | bus_LV_2113-7_0_3_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_2113-7_0_3_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_2113-7_0_3_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_2113-7_0_3_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_2113-7_0_3_node_111 | 0.4 | n |  | TRUE
105 | bus_LV_2113-7_0_3_node_108 | 0.4 | n |  | TRUE
106 | bus_LV_2113-7_0_3_node_109 | 0.4 | n |  | TRUE
107 | bus_LV_2113-7_0_3_node_107 | 0.4 | n |  | TRUE
108 | bus_LV_2113-7_0_3_node_99 | 0.4 | n |  | TRUE
109 | bus_LV_2113-7_0_3_node_102 | 0.4 | n |  | TRUE
110 | bus_LV_2113-7_0_3_node_100 | 0.4 | n |  | TRUE
111 | bus_LV_2113-7_0_3_node_101 | 0.4 | n |  | TRUE
112 | bus_LV_2113-7_0_3_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_2113-7_0_3_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_2113-7_0_3_node_110 | 0.4 | n |  | TRUE
115 | bus_LV_2113-7_0_3_node_116 | 0.4 | n |  | TRUE
116 | bus_MV_33_0_node_166 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2113-7_0_3_load_0 | 0 | 0.0012945 | 0.00032443 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2113-7_0_3_load_1 | 1 | 0.00061398 | 0.00015388 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2113-7_0_3_load_3 | 3 | 0.00032224 | 8.0762e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2113-7_0_3_load_9 | 5 | 0.0010489 | 0.00026288 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2113-7_0_3_load_6 | 7 | 0.00074781 | 0.00018742 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2113-7_0_3_load_5 | 8 | 0.00024673 | 6.1837e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2113-7_0_3_load_25 | 11 | 0.00010201 | 2.5567e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2113-7_0_3_load_18 | 12 | 0.00024921 | 6.2457e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2113-7_0_3_load_11 | 14 | 0.00020742 | 5.1985e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2113-7_0_3_load_13 | 16 | 0.00035003 | 8.7726e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2113-7_0_3_load_26 | 18 | 0.0037311 | 0.00093509 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2113-7_0_3_load_27 | 19 | 0.0027758 | 0.00069568 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2113-7_0_3_load_16 | 20 | 0.0011749 | 0.00029446 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2113-7_0_3_load_113 | 21 | 0.00095107 | 0.00023836 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2113-7_0_3_load_112 | 23 | 0.00085596 | 0.00021452 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2113-7_0_3_load_20 | 25 | 0.0001641 | 4.1126e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2113-7_0_3_load_17 | 26 | 0.00017418 | 4.3654e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2113-7_0_3_load_21 | 27 | 0.00012627 | 3.1647e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2113-7_0_3_load_22 | 28 | 0.0013792 | 0.00034566 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2113-7_0_3_load_24 | 29 | 0.0006967 | 0.00017461 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2113-7_0_3_load_28 | 30 | 0.0023029 | 0.00057716 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2113-7_0_3_load_73 | 31 | 0.0020878 | 0.00052324 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2113-7_0_3_load_72 | 32 | 0.0016323 | 0.0004091 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2113-7_0_3_load_114 | 34 | 0.0059942 | 0.0015023 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2113-7_0_3_load_115 | 35 | 0.0036523 | 0.00091535 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2113-7_0_3_load_30 | 36 | 0.0017419 | 0.00043656 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2113-7_0_3_load_31 | 37 | 0.0045941 | 0.0011514 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2113-7_0_3_load_32 | 38 | 0.0055369 | 0.0013877 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2113-7_0_3_load_34 | 40 | 0.0030543 | 0.00076547 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2113-7_0_3_load_78 | 42 | 0.0014719 | 0.0003689 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2113-7_0_3_load_75 | 43 | 0.0026883 | 0.00067375 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2113-7_0_3_load_35 | 44 | 0.0029786 | 0.00074651 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2113-7_0_3_load_36 | 45 | 0.0019227 | 0.00048186 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2113-7_0_3_load_37 | 46 | 0.001654 | 0.00041454 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2113-7_0_3_load_38 | 47 | 0.0054574 | 0.0013678 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2113-7_0_3_load_39 | 48 | 0.0016266 | 0.00040767 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2113-7_0_3_load_43 | 49 | 0.0032947 | 0.00082573 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2113-7_0_3_load_69 | 50 | 0.0026233 | 0.00065745 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2113-7_0_3_load_41 | 51 | 0.0034964 | 0.00087629 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2113-7_0_3_load_68 | 52 | 0.0034646 | 0.0008683 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2113-7_0_3_load_40 | 53 | 0.0031166 | 0.0007811 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2113-7_0_3_load_42 | 54 | 0.0034222 | 0.00085768 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2113-7_0_3_load_44 | 55 | 0.004429 | 0.00111 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2113-7_0_3_load_45 | 56 | 0.0021443 | 0.00053741 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2113-7_0_3_load_46 | 57 | 0.0029456 | 0.00073823 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2113-7_0_3_load_47 | 58 | 0.0022004 | 0.00055147 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2113-7_0_3_load_48 | 59 | 0.0027753 | 0.00069555 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2113-7_0_3_load_49 | 60 | 0.0030692 | 0.00076921 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2113-7_0_3_load_50 | 61 | 0.0031107 | 0.00077962 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2113-7_0_3_load_51 | 62 | 0.0017719 | 0.00044408 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2113-7_0_3_load_53 | 64 | 0.0028983 | 0.00072639 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2113-7_0_3_load_54 | 65 | 0.002236 | 0.00056039 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2113-7_0_3_load_55 | 66 | 0.0026681 | 0.00066868 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2113-7_0_3_load_56 | 67 | 0.0036255 | 0.00090863 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2113-7_0_3_load_57 | 68 | 0.0027873 | 0.00069856 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2113-7_0_3_load_58 | 69 | 0.003616 | 0.00090624 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2113-7_0_3_load_59 | 70 | 0.0023354 | 0.00058531 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2113-7_0_3_load_60 | 71 | 0.0030483 | 0.00076396 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2113-7_0_3_load_61 | 72 | 0.0049026 | 0.0012287 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2113-7_0_3_load_62 | 73 | 0.0037362 | 0.00093637 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2113-7_0_3_load_64 | 75 | 0.0037944 | 0.00095096 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2113-7_0_3_load_65 | 76 | 0.0046819 | 0.0011734 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2113-7_0_3_load_66 | 77 | 0.0020485 | 0.0005134 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2113-7_0_3_load_84 | 78 | 0.0021972 | 0.00055068 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2113-7_0_3_load_67 | 79 | 0.0022676 | 0.00056832 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2113-7_0_3_load_85 | 80 | 0.0043273 | 0.0010845 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2113-7_0_3_load_71 | 82 | 0.0031468 | 0.00078866 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2113-7_0_3_load_74 | 83 | 0.013504 | 0.0033844 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2113-7_0_3_load_79 | 84 | 0.0027646 | 0.00069288 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2113-7_0_3_load_77 | 85 | 0.006194 | 0.0015524 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2113-7_0_3_load_103 | 86 | 0.0017238 | 0.00043203 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2113-7_0_3_load_94 | 87 | 0.002858 | 0.00071627 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2113-7_0_3_load_80 | 88 | 0.0021988 | 0.00055107 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2113-7_0_3_load_83 | 91 | 0.0016707 | 0.0004187 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2113-7_0_3_load_86 | 92 | 0.0018216 | 0.00045653 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2113-7_0_3_load_95 | 93 | 0.0031933 | 0.00080033 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2113-7_0_3_load_87 | 94 | 0.0044603 | 0.0011179 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2113-7_0_3_load_96 | 95 | 0.0011691 | 0.00029299 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2113-7_0_3_load_88 | 96 | 0.0013071 | 0.00032759 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2113-7_0_3_load_89 | 97 | 0.0017692 | 0.00044341 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2113-7_0_3_load_97 | 98 | 0.0016443 | 0.00041211 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2113-7_0_3_load_98 | 99 | 0.0014302 | 0.00035844 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2113-7_0_3_load_90 | 100 | 0.0014612 | 0.00036622 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2113-7_0_3_load_91 | 101 | 0.0015803 | 0.00039605 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2113-7_0_3_load_92 | 102 | 0.0012618 | 0.00031624 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2113-7_0_3_load_93 | 103 | 0.0010282 | 0.0002577 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2113-7_0_3_load_111 | 104 | 0.0013838 | 0.00034682 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2113-7_0_3_load_108 | 105 | 0.0011957 | 0.00029966 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2113-7_0_3_load_109 | 106 | 0.0011693 | 0.00029306 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2113-7_0_3_load_99 | 108 | 0.0059265 | 0.0014853 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2113-7_0_3_load_100 | 110 | 0.0014797 | 0.00037085 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2113-7_0_3_load_101 | 111 | 0.0014015 | 0.00035125 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2113-7_0_3_load_105 | 112 | 0.00077668 | 0.00019466 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2113-7_0_3_load_106 | 113 | 0.00078945 | 0.00019785 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2113-7_0_3_load_110 | 114 | 0.0021098 | 0.00052877 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2113-7_0_3_load_116 | 115 | 0.0023798 | 0.00059642 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 76 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2113-7_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2113-7_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.043789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2113-7_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.058968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2113-7_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.006187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2113-7_0_3_line_4 | NAYY 4x150 SE | 4 | 7 | 0.0017182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2113-7_0_3_line_5 | NAYY 4x150 SE | 4 | 8 | 0.033081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2113-7_0_3_line_6 | NAYY 4x150 SE | 5 | 6 | 0.019168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2113-7_0_3_line_7 | NAYY 4x150 SE | 5 | 7 | 0.11887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2113-7_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.0090507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2113-7_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.016278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2113-7_0_3_line_10 | NAYY 4x150 SE | 10 | 11 | 0.04314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2113-7_0_3_line_11 | NAYY 4x150 SE | 11 | 12 | 0.076922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2113-7_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.042087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2113-7_0_3_line_13 | NAYY 4x150 SE | 12 | 25 | 0.014865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2113-7_0_3_line_14 | NAYY 4x150 SE | 13 | 29 | 0.036231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2113-7_0_3_line_15 | NAYY 4x150 SE | 13 | 27 | 0.0087398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2113-7_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.027274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2113-7_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.013221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2113-7_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.036459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2113-7_0_3_line_19 | NAYY 4x150 SE | 16 | 20 | 0.042719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2113-7_0_3_line_20 | NAYY 4x150 SE | 17 | 21 | 0.025516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2113-7_0_3_line_21 | NAYY 4x150 SE | 17 | 22 | 0.06276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2113-7_0_3_line_22 | NAYY 4x150 SE | 17 | 23 | 0.0062943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2113-7_0_3_line_23 | NAYY 4x150 SE | 18 | 19 | 0.055305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2113-7_0_3_line_24 | NAYY 4x150 SE | 18 | 20 | 0.1377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2113-7_0_3_line_25 | NAYY 4x150 SE | 19 | 30 | 0.011806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2113-7_0_3_line_26 | NAYY 4x150 SE | 22 | 24 | 0.00363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2113-7_0_3_line_27 | NAYY 4x150 SE | 22 | 25 | 0.025876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2113-7_0_3_line_28 | NAYY 4x150 SE | 24 | 26 | 0.021768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2113-7_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.01065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2113-7_0_3_line_30 | NAYY 4x150 SE | 30 | 33 | 0.015308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2113-7_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.016321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2113-7_0_3_line_32 | NAYY 4x150 SE | 32 | 82 | 0.00036505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2113-7_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.027985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2113-7_0_3_line_34 | NAYY 4x150 SE | 34 | 35 | 0.0082904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2113-7_0_3_line_35 | NAYY 4x150 SE | 35 | 37 | 0.059146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2113-7_0_3_line_36 | NAYY 4x150 SE | 36 | 37 | 0.0067834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2113-7_0_3_line_37 | NAYY 4x150 SE | 36 | 38 | 0.0024106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2113-7_0_3_line_38 | NAYY 4x150 SE | 38 | 39 | 0.028731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2113-7_0_3_line_39 | NAYY 4x150 SE | 39 | 40 | 0.027315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2113-7_0_3_line_40 | NAYY 4x150 SE | 40 | 41 | 0.0018482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2113-7_0_3_line_41 | NAYY 4x150 SE | 41 | 42 | 0.026852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2113-7_0_3_line_42 | NAYY 4x150 SE | 41 | 43 | 0.022285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2113-7_0_3_line_43 | NAYY 4x150 SE | 42 | 84 | 0.024749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2113-7_0_3_line_44 | NAYY 4x150 SE | 43 | 83 | 0.015527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2113-7_0_3_line_45 | NAYY 4x150 SE | 44 | 45 | 0.012008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2113-7_0_3_line_46 | NAYY 4x150 SE | 44 | 46 | 0.01949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2113-7_0_3_line_47 | NAYY 4x150 SE | 45 | 47 | 0.0071019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2113-7_0_3_line_48 | NAYY 4x150 SE | 46 | 48 | 0.0026155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2113-7_0_3_line_49 | NAYY 4x150 SE | 47 | 49 | 0.02092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2113-7_0_3_line_50 | NAYY 4x150 SE | 48 | 50 | 0.01854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2113-7_0_3_line_51 | NAYY 4x150 SE | 49 | 51 | 0.011079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2113-7_0_3_line_52 | NAYY 4x150 SE | 50 | 52 | 0.0089113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2113-7_0_3_line_53 | NAYY 4x150 SE | 51 | 53 | 0.011254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2113-7_0_3_line_54 | NAYY 4x150 SE | 52 | 81 | 0.0063476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2113-7_0_3_line_55 | NAYY 4x150 SE | 53 | 54 | 0.019929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2113-7_0_3_line_56 | NAYY 4x150 SE | 54 | 55 | 8.625e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2113-7_0_3_line_57 | NAYY 4x150 SE | 55 | 56 | 0.021833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2113-7_0_3_line_58 | NAYY 4x150 SE | 56 | 57 | 0.023081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2113-7_0_3_line_59 | NAYY 4x150 SE | 57 | 58 | 0.00092357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2113-7_0_3_line_60 | NAYY 4x150 SE | 58 | 59 | 0.026429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2113-7_0_3_line_61 | NAYY 4x150 SE | 59 | 60 | 0.0090323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2113-7_0_3_line_62 | NAYY 4x150 SE | 60 | 61 | 0.019582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2113-7_0_3_line_63 | NAYY 4x150 SE | 61 | 62 | 0.0066259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2113-7_0_3_line_64 | NAYY 4x150 SE | 63 | 64 | 0.017499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2113-7_0_3_line_65 | NAYY 4x150 SE | 63 | 65 | 0.025807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2113-7_0_3_line_66 | NAYY 4x150 SE | 64 | 66 | 0.019976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2113-7_0_3_line_67 | NAYY 4x150 SE | 66 | 67 | 0.0052372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2113-7_0_3_line_68 | NAYY 4x150 SE | 67 | 68 | 0.010632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2113-7_0_3_line_69 | NAYY 4x150 SE | 68 | 69 | 0.011043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2113-7_0_3_line_70 | NAYY 4x150 SE | 69 | 70 | 0.020713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2113-7_0_3_line_71 | NAYY 4x150 SE | 70 | 71 | 0.010291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2113-7_0_3_line_72 | NAYY 4x150 SE | 71 | 72 | 0.02043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2113-7_0_3_line_73 | NAYY 4x150 SE | 72 | 73 | 0.022956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2113-7_0_3_line_74 | NAYY 4x150 SE | 73 | 74 | 0.023934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2113-7_0_3_line_75 | NAYY 4x150 SE | 74 | 75 | 0.0079664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2113-7_0_3_line_76 | NAYY 4x150 SE | 74 | 76 | 0.013602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2113-7_0_3_line_77 | NAYY 4x150 SE | 75 | 77 | 0.03082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2113-7_0_3_line_78 | NAYY 4x150 SE | 76 | 78 | 0.011923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
79 | LV_2113-7_0_3_line_79 | NAYY 4x150 SE | 77 | 79 | 0.010361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2113-7_0_3_line_80 | NAYY 4x150 SE | 78 | 80 | 0.026427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
81 | LV_2113-7_0_3_line_81 | NAYY 4x150 SE | 79 | 81 | 0.023411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2113-7_0_3_line_82 | NAYY 4x150 SE | 80 | 90 | 0.016124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
83 | LV_2113-7_0_3_line_83 | NAYY 4x150 SE | 81 | 82 | 0.026292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2113-7_0_3_line_84 | NAYY 4x150 SE | 84 | 88 | 0.031079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
85 | LV_2113-7_0_3_line_85 | NAYY 4x150 SE | 85 | 86 | 0.15903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2113-7_0_3_line_86 | NAYY 4x150 SE | 86 | 87 | 0.024262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2113-7_0_3_line_87 | NAYY 4x150 SE | 87 | 102 | 0.0041155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2113-7_0_3_line_88 | NAYY 4x150 SE | 88 | 89 | 0.016991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
89 | LV_2113-7_0_3_line_89 | NAYY 4x150 SE | 89 | 90 | 0.012112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_2113-7_0_3_line_90 | NAYY 4x150 SE | 89 | 91 | 0.017157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2113-7_0_3_line_91 | NAYY 4x150 SE | 90 | 92 | 0.030049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2113-7_0_3_line_92 | NAYY 4x150 SE | 91 | 93 | 0.0077534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2113-7_0_3_line_93 | NAYY 4x150 SE | 92 | 94 | 0.014191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2113-7_0_3_line_94 | NAYY 4x150 SE | 93 | 95 | 0.018963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2113-7_0_3_line_95 | NAYY 4x150 SE | 94 | 96 | 0.01417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2113-7_0_3_line_96 | NAYY 4x150 SE | 95 | 106 | 0.013818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2113-7_0_3_line_97 | NAYY 4x150 SE | 96 | 97 | 0.011373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2113-7_0_3_line_98 | NAYY 4x150 SE | 97 | 98 | 0.02126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2113-7_0_3_line_99 | NAYY 4x150 SE | 98 | 99 | 0.0029585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2113-7_0_3_line_100 | NAYY 4x150 SE | 99 | 108 | 0.02441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2113-7_0_3_line_101 | NAYY 4x150 SE | 100 | 101 | 0.00088158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2113-7_0_3_line_102 | NAYY 4x150 SE | 100 | 102 | 0.022043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2113-7_0_3_line_103 | NAYY 4x150 SE | 101 | 103 | 0.0025895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2113-7_0_3_line_104 | NAYY 4x150 SE | 103 | 104 | 0.020547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2113-7_0_3_line_105 | NAYY 4x150 SE | 104 | 105 | 0.00058328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2113-7_0_3_line_106 | NAYY 4x150 SE | 105 | 107 | 0.035029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2113-7_0_3_line_107 | NAYY 4x150 SE | 106 | 107 | 0.012376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2113-7_0_3_line_108 | NAYY 4x150 SE | 107 | 114 | 0.020785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2113-7_0_3_line_109 | NAYY 4x150 SE | 107 | 113 | 0.013887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2113-7_0_3_line_110 | NAYY 4x150 SE | 108 | 109 | 0.033512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2113-7_0_3_line_111 | NAYY 4x150 SE | 109 | 110 | 0.031894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2113-7_0_3_line_112 | NAYY 4x150 SE | 110 | 111 | 0.026354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2113-7_0_3_line_113 | NAYY 4x150 SE | 112 | 113 | 0.015506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2113-7_0_3_line_114 | NAYY 4x150 SE | 114 | 115 | 0.014522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2113-7_0_3_trafo_65 | 0.25 MVA 20/0.4 kV | 116 | 76 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2561387.5566 | 1166393.1747 | 2561382.2754 | 1166376.6766
1 | 2561400.9065 | 1166434.8785 | 2561387.5566 | 1166393.1747
2 | 2561364.2976 | 1166320.5156 | 2561382.2754 | 1166376.6766
3 | 2561402.7971 | 1166440.7694 | 2561400.9065 | 1166434.8785
4 | 2561402.7971 | 1166440.7694 | 2561401.8608 | 1166442.2101
5 | 2561402.7971 | 1166440.7694 | 2561412.7352 | 1166425.4753 | 2561421.3492 | 1166413.3896
6 | 2561321.7597 | 1166536.5637 | 2561312.0251 | 1166520.0512
7 | 2561312.0251 | 1166520.0512 | 2561401.8608 | 1166442.2101
8 | 2561325.228 | 1166544.9234 | 2561321.7597 | 1166536.5637
9 | 2561325.228 | 1166544.9234 | 2561330.8387 | 1166560.2062
10 | 2561330.8387 | 1166560.2062 | 2561300.0478 | 1166573.2117 | 2561297.1903 | 1166575.2757 | 2561297.2114 | 1166578.5439 | 2561298.2239 | 1166581.285
11 | 2561298.2239 | 1166581.285 | 2561222.598 | 1166567.2211
12 | 2561311.2285 | 1166621.1755 | 2561309.9588 | 1166613.0573 | 2561298.2239 | 1166581.285
13 | 2561222.598 | 1166567.2211 | 2561218.8895 | 1166552.8257 | 2561218.8895 | 1166552.8257
14 | 2561311.2285 | 1166621.1755 | 2561311.4601 | 1166622.6637 | 2561308.6532 | 1166633.7431 | 2561305.4154 | 1166640.9232 | 2561296.2298 | 1166649.3758 | 2561293.754 | 1166650.9541
15 | 2561311.2285 | 1166621.1755 | 2561319.4025 | 1166618.082
16 | 2561143.8145 | 1166581.6602 | 2561117.6993 | 1166589.5251
17 | 2561143.8145 | 1166581.6602 | 2561147.6737 | 1166594.305
18 | 2561143.8145 | 1166581.6602 | 2561141.3271 | 1166573.5054 | 2561151.2501 | 1166570.1727 | 2561146.3184 | 1166553.4182
19 | 2561131.1681 | 1166619.5912 | 2561153.3805 | 1166613.0033 | 2561147.6737 | 1166594.305
20 | 2561146.3184 | 1166553.4182 | 2561122.0464 | 1166561.2889
21 | 2561194.1886 | 1166555.7537 | 2561151.2501 | 1166570.1727 | 2561146.3184 | 1166553.4182
22 | 2561146.3184 | 1166553.4182 | 2561144.5399 | 1166547.3804
23 | 2561019.9458 | 1166700.7735 | 2561014.2242 | 1166703.2425 | 2561006.7145 | 1166703.2914 | 2560977.1137 | 1166704.8626 | 2560976.413 | 1166707.7576 | 2560967.5117 | 1166708.6207
24 | 2561019.9458 | 1166700.7735 | 2561131.1681 | 1166619.5912
25 | 2560967.5117 | 1166708.6207 | 2560955.7611 | 1166709.7601
26 | 2561194.1886 | 1166555.7537 | 2561195.2064 | 1166559.2378
27 | 2561194.1886 | 1166555.7537 | 2561214.8255 | 1166550.6397 | 2561218.8895 | 1166552.8257
28 | 2561195.2064 | 1166559.2378 | 2561199.4551 | 1166558.0319 | 2561202.8684 | 1166560.2332 | 2561206.5148 | 1166573.0128
29 | 2561319.4025 | 1166618.082 | 2561329.3629 | 1166614.3125
30 | 2560940.5242 | 1166711.2376 | 2560955.7611 | 1166709.7601
31 | 2560935.1953 | 1166643.378 | 2560934.2269 | 1166634.2276 | 2560932.0661 | 1166627.4437
32 | 2560932.0661 | 1166627.4437 | 2560931.9553 | 1166627.0958
33 | 2560940.5242 | 1166711.2376 | 2560945.1545 | 1166738.8368
34 | 2560945.1545 | 1166738.8368 | 2560946.5262 | 1166747.0129
35 | 2560889.6286 | 1166763.1646 | 2560946.5262 | 1166747.0129
36 | 2560886.75 | 1166757.0223 | 2560889.6286 | 1166763.1646
37 | 2560886.75 | 1166757.0223 | 2560885.727 | 1166754.8396
38 | 2560873.4786 | 1166728.8507 | 2560878.0969 | 1166738.5589 | 2560885.727 | 1166754.8396
39 | 2560873.4786 | 1166728.8507 | 2560861.7376 | 1166704.1877
40 | 2560860.9432 | 1166702.5189 | 2560861.7376 | 1166704.1877
41 | 2560860.9432 | 1166702.5189 | 2560849.4045 | 1166678.2723
42 | 2560860.9432 | 1166702.5189 | 2560839.7681 | 1166705.9923 | 2560839.0729 | 1166706.4409
43 | 2560849.4045 | 1166678.2723 | 2560838.9611 | 1166656.3274 | 2560838.7812 | 1166655.919
44 | 2560826.0175 | 1166714.8458 | 2560827.0449 | 1166714.2019 | 2560839.0729 | 1166706.4409
45 | 2560930.3139 | 1166548.4735 | 2560929.7887 | 1166536.477
46 | 2560930.3139 | 1166548.4735 | 2560930.3957 | 1166550.3424 | 2560929.5681 | 1166566.6562 | 2560929.3591 | 1166567.924
47 | 2560929.7887 | 1166536.477 | 2560929.4781 | 1166529.3819
48 | 2560929.3591 | 1166567.924 | 2560928.9337 | 1166570.5047
49 | 2560929.4781 | 1166529.3819 | 2560929.4781 | 1166529.3819 | 2560924.2583 | 1166509.124
50 | 2560925.5509 | 1166588.7142 | 2560926.4162 | 1166585.7756 | 2560928.9337 | 1166570.5047
51 | 2560920.2363 | 1166498.8027 | 2560924.2078 | 1166508.9279 | 2560924.2583 | 1166509.124
52 | 2560923.0338 | 1166597.2626 | 2560925.5509 | 1166588.7142
53 | 2560916.1268 | 1166488.3254 | 2560920.2363 | 1166498.8027
54 | 2560921.2409 | 1166603.3518 | 2560923.0338 | 1166597.2626
55 | 2560916.1268 | 1166488.3254 | 2560916.1268 | 1166488.3254 | 2560906.1467 | 1166471.0758
56 | 2560906.1467 | 1166471.0758 | 2560906.1035 | 1166471.0012
57 | 2560906.1035 | 1166471.0012 | 2560904.311 | 1166467.903 | 2560892.2871 | 1166454.1693
58 | 2560892.2871 | 1166454.1693 | 2560888.7689 | 1166450.1508 | 2560875.6054 | 1166438.2591
59 | 2560875.6054 | 1166438.2591 | 2560874.92 | 1166437.64
60 | 2560874.92 | 1166437.64 | 2560855.3087 | 1166419.9235
61 | 2560848.6064 | 1166413.8687 | 2560855.3087 | 1166419.9235
62 | 2560848.6064 | 1166413.8687 | 2560834.0757 | 1166400.742
63 | 2560829.159 | 1166396.3003 | 2560834.0757 | 1166400.742
64 | 2560777.851 | 1166448.697 | 2560790.8378 | 1166457.3054 | 2560792.5492 | 1166458.1728
65 | 2560777.851 | 1166448.697 | 2560772.3628 | 1166447.6768 | 2560764.3957 | 1166443.3823 | 2560760.5124 | 1166445.431 | 2560756.1354 | 1166440.2492
66 | 2560792.5492 | 1166458.1728 | 2560810.3672 | 1166467.2037
67 | 2560815.0386 | 1166469.5715 | 2560810.3672 | 1166467.2037
68 | 2560815.0386 | 1166469.5715 | 2560818.9663 | 1166471.5622 | 2560824.0476 | 1166475.164
69 | 2560832.1105 | 1166482.5117 | 2560829.6111 | 1166479.1076 | 2560824.0476 | 1166475.164
70 | 2560832.1105 | 1166482.5117 | 2560838.5715 | 1166491.311 | 2560843.0474 | 1166500.0249
71 | 2560843.0474 | 1166500.0249 | 2560847.7495 | 1166509.1791
72 | 2560847.7495 | 1166509.1791 | 2560857.0842 | 1166527.3522
73 | 2560866.1075 | 1166548.4492 | 2560858.7636 | 1166530.6217 | 2560857.0842 | 1166527.3522
74 | 2560875.2239 | 1166570.5794 | 2560866.1075 | 1166548.4492
75 | 2560875.2239 | 1166570.5794 | 2560878.6689 | 1166577.7624
76 | 2560875.2239 | 1166570.5794 | 2560869.0138 | 1166573.8772 | 2560863.4397 | 1166577.3561
77 | 2560878.6689 | 1166577.7624 | 2560885.1738 | 1166591.3252 | 2560892.591 | 1166605.2507
78 | 2560853.3254 | 1166583.6686 | 2560863.4397 | 1166577.3561
79 | 2560901.0359 | 1166611.2543 | 2560901.0359 | 1166611.2543 | 2560892.591 | 1166605.2507 | 2560892.591 | 1166605.2507
80 | 2560853.3254 | 1166583.6686 | 2560846.3691 | 1166588.0102 | 2560829.4624 | 1166594.8217
81 | 2560921.2409 | 1166603.3518 | 2560911.1688 | 1166611.9664 | 2560901.0359 | 1166611.2543
82 | 2560814.5065 | 1166600.8473 | 2560829.4624 | 1166594.8217
83 | 2560921.2409 | 1166603.3518 | 2560927.3258 | 1166612.5613 | 2560931.9553 | 1166627.0958
84 | 2560838.7812 | 1166655.919 | 2560826.2469 | 1166627.4801
85 | 2560693.5166 | 1166549.8973 | 2560566.2006 | 1166645.1988
86 | 2560693.5166 | 1166549.8973 | 2560695.4785 | 1166551.8456 | 2560708.6879 | 1166568.805
87 | 2560708.6879 | 1166568.805 | 2560711.2168 | 1166572.0518
88 | 2560819.3944 | 1166611.9322 | 2560826.2469 | 1166627.4801
89 | 2560814.5065 | 1166600.8473 | 2560819.3944 | 1166611.9322
90 | 2560819.3944 | 1166611.9322 | 2560803.7217 | 1166618.9137
91 | 2560814.5065 | 1166600.8473 | 2560813.2554 | 1166598.0096 | 2560801.8498 | 1166573.5946
92 | 2560803.7217 | 1166618.9137 | 2560796.6392 | 1166622.0686
93 | 2560795.8433 | 1166560.737 | 2560801.8498 | 1166573.5946
94 | 2560779.317 | 1166629.7849 | 2560796.6392 | 1166622.0686
95 | 2560795.8433 | 1166560.737 | 2560792.8974 | 1166554.4312 | 2560789.3033 | 1166548.1809
96 | 2560766.6946 | 1166635.4077 | 2560779.317 | 1166629.7849
97 | 2560789.3033 | 1166548.1809 | 2560783.634 | 1166538.3221
98 | 2560772.1514 | 1166520.4658 | 2560777.9055 | 1166528.3602 | 2560783.634 | 1166538.3221
99 | 2560772.1514 | 1166520.4658 | 2560770.4088 | 1166518.075
100 | 2560770.4088 | 1166518.075 | 2560764.5103 | 1166509.9828 | 2560755.4038 | 1166498.8328
101 | 2560725.3035 | 1166590.1374 | 2560724.7618 | 1166589.4419
102 | 2560724.7618 | 1166589.4419 | 2560711.2168 | 1166572.0518
103 | 2560726.8947 | 1166592.1804 | 2560725.3035 | 1166590.1374
104 | 2560738.2458 | 1166609.2298 | 2560733.6335 | 1166600.8321 | 2560726.8947 | 1166592.1804
105 | 2560738.5266 | 1166609.741 | 2560738.2458 | 1166609.2298
106 | 2560755.3897 | 1166640.4435 | 2560738.5266 | 1166609.741
107 | 2560755.3897 | 1166640.4435 | 2560766.6946 | 1166635.4077
108 | 2560755.3897 | 1166640.4435 | 2560765.0465 | 1166658.8488
109 | 2560755.3897 | 1166640.4435 | 2560742.8472 | 1166646.4038
110 | 2560732.2478 | 1166474.6868 | 2560748.0102 | 1166489.7803 | 2560755.4038 | 1166498.8328
111 | 2560732.2478 | 1166474.6868 | 2560712.4997 | 1166499.7311
112 | 2560712.4997 | 1166499.7311 | 2560696.1818 | 1166520.4252
113 | 2560728.8422 | 1166653.0591 | 2560742.8472 | 1166646.4038
114 | 2560771.7934 | 1166671.7079 | 2560765.0465 | 1166658.8488

## bus_geodata
| x | y | coords
0 | 2561387.5566 | 1166393.1747
1 | 2561382.2754 | 1166376.6766
2 | 2561400.9065 | 1166434.8785
3 | 2561364.2976 | 1166320.5156
4 | 2561402.7971 | 1166440.7694
5 | 2561312.0251 | 1166520.0512
6 | 2561321.7597 | 1166536.5637
7 | 2561401.8608 | 1166442.2101
8 | 2561421.3492 | 1166413.3896
9 | 2561325.228 | 1166544.9234
10 | 2561330.8387 | 1166560.2062
11 | 2561298.2239 | 1166581.285
12 | 2561222.598 | 1166567.2211
13 | 2561311.2285 | 1166621.1755
14 | 2561117.6993 | 1166589.5251
15 | 2561143.8145 | 1166581.6602
16 | 2561147.6737 | 1166594.305
17 | 2561146.3184 | 1166553.4182
18 | 2561019.9458 | 1166700.7735
19 | 2560967.5117 | 1166708.6207
20 | 2561131.1681 | 1166619.5912
21 | 2561122.0464 | 1166561.2889
22 | 2561194.1886 | 1166555.7537
23 | 2561144.5399 | 1166547.3804
24 | 2561195.2064 | 1166559.2378
25 | 2561218.8895 | 1166552.8257
26 | 2561206.5148 | 1166573.0128
27 | 2561319.4025 | 1166618.082
28 | 2561329.3629 | 1166614.3125
29 | 2561293.754 | 1166650.9541
30 | 2560955.7611 | 1166709.7601
31 | 2560935.1953 | 1166643.378
32 | 2560932.0661 | 1166627.4437
33 | 2560940.5242 | 1166711.2376
34 | 2560945.1545 | 1166738.8368
35 | 2560946.5262 | 1166747.0129
36 | 2560886.75 | 1166757.0223
37 | 2560889.6286 | 1166763.1646
38 | 2560885.727 | 1166754.8396
39 | 2560873.4786 | 1166728.8507
40 | 2560861.7376 | 1166704.1877
41 | 2560860.9432 | 1166702.5189
42 | 2560849.4045 | 1166678.2723
43 | 2560839.0728 | 1166706.4409
44 | 2560930.3139 | 1166548.4735
45 | 2560929.7887 | 1166536.477
46 | 2560929.3591 | 1166567.924
47 | 2560929.4781 | 1166529.3819
48 | 2560928.9337 | 1166570.5047
49 | 2560924.2583 | 1166509.124
50 | 2560925.5509 | 1166588.7142
51 | 2560920.2363 | 1166498.8027
52 | 2560923.0338 | 1166597.2626
53 | 2560916.1268 | 1166488.3254
54 | 2560906.1467 | 1166471.0758
55 | 2560906.1035 | 1166471.0012
56 | 2560892.2871 | 1166454.1693
57 | 2560875.6054 | 1166438.2591
58 | 2560874.92 | 1166437.64
59 | 2560855.3087 | 1166419.9235
60 | 2560848.6064 | 1166413.8687
61 | 2560834.0757 | 1166400.742
62 | 2560829.159 | 1166396.3003
63 | 2560777.851 | 1166448.697
64 | 2560792.5492 | 1166458.1728
65 | 2560756.1354 | 1166440.2492
66 | 2560810.3672 | 1166467.2037
67 | 2560815.0386 | 1166469.5715
68 | 2560824.0476 | 1166475.164
69 | 2560832.1105 | 1166482.5117
70 | 2560843.0474 | 1166500.0249
71 | 2560847.7495 | 1166509.1791
72 | 2560857.0842 | 1166527.3522
73 | 2560866.1075 | 1166548.4492
74 | 2560875.2239 | 1166570.5794
75 | 2560878.6689 | 1166577.7624
76 | 2560863.4397 | 1166577.3561
77 | 2560892.591 | 1166605.2507
78 | 2560853.3254 | 1166583.6686
79 | 2560901.0359 | 1166611.2543
80 | 2560829.4624 | 1166594.8217
81 | 2560921.2409 | 1166603.3518
82 | 2560931.9553 | 1166627.0958
83 | 2560826.0175 | 1166714.8458
84 | 2560838.7812 | 1166655.919
85 | 2560566.2006 | 1166645.1988
86 | 2560693.5166 | 1166549.8973
87 | 2560708.6879 | 1166568.805
88 | 2560826.2469 | 1166627.4801
89 | 2560819.3944 | 1166611.9322
90 | 2560814.5065 | 1166600.8473
91 | 2560803.7217 | 1166618.9137
92 | 2560801.8498 | 1166573.5946
93 | 2560796.6392 | 1166622.0686
94 | 2560795.8433 | 1166560.737
95 | 2560779.317 | 1166629.7849
96 | 2560789.3033 | 1166548.1809
97 | 2560783.634 | 1166538.3221
98 | 2560772.1514 | 1166520.4658
99 | 2560770.4088 | 1166518.075
100 | 2560724.7618 | 1166589.4419
101 | 2560725.3035 | 1166590.1374
102 | 2560711.2168 | 1166572.0518
103 | 2560726.8947 | 1166592.1804
104 | 2560738.2458 | 1166609.2298
105 | 2560738.5266 | 1166609.741
106 | 2560766.6946 | 1166635.4077
107 | 2560755.3897 | 1166640.4435
108 | 2560755.4038 | 1166498.8328
109 | 2560732.2478 | 1166474.6868
110 | 2560712.4997 | 1166499.7311
111 | 2560696.1818 | 1166520.4252
112 | 2560728.8422 | 1166653.0591
113 | 2560742.8472 | 1166646.4038
114 | 2560765.0465 | 1166658.8488
115 | 2560771.7934 | 1166671.7079
116 | 2560863.4397 | 1166577.3561

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97148 | -0.20205 | 0.0012945 | 0.00032443
1 | 0.97145 | -0.20223 | 0.00061398 | 0.00015388
2 | 0.97162 | -0.20102 | 0 | 0
3 | 0.97143 | -0.20243 | 0.00032224 | 8.0762e-05
4 | 0.97164 | -0.20087 | 0 | 0
5 | 0.97221 | -0.19675 | 0.0010489 | 0.00026288
6 | 0.97233 | -0.19588 | 0 | 0
7 | 0.97165 | -0.20083 | 0.00074781 | 0.00018742
8 | 0.97163 | -0.20096 | 0.00024673 | 6.1837e-05
9 | 0.97239 | -0.19547 | 0 | 0
10 | 0.97249 | -0.19473 | 0 | 0
11 | 0.97276 | -0.19277 | 0.00010201 | 2.5567e-05
12 | 0.9735 | -0.1874 | 0.00024921 | 6.2457e-05
13 | 0.97262 | -0.19375 | 0 | 0
14 | 0.97505 | -0.17623 | 0.00020742 | 5.1985e-05
15 | 0.97505 | -0.17617 | 0 | 0
16 | 0.97523 | -0.17489 | 0.00035003 | 8.7726e-05
17 | 0.97457 | -0.17964 | 0 | 0
18 | 0.97799 | -0.15505 | 0.0037311 | 0.00093509
19 | 0.97915 | -0.14668 | 0.0027758 | 0.00069568
20 | 0.97583 | -0.17059 | 0.0011749 | 0.00029446
21 | 0.97454 | -0.17989 | 0.00095107 | 0.00023836
22 | 0.97392 | -0.1844 | 0 | 0
23 | 0.97457 | -0.17969 | 0.00085596 | 0.00021452
24 | 0.97391 | -0.18441 | 0 | 0
25 | 0.97365 | -0.18632 | 0.0001641 | 4.1126e-05
26 | 0.97391 | -0.18445 | 0.00017418 | 4.3654e-05
27 | 0.9726 | -0.19389 | 0.00012627 | 3.1647e-05
28 | 0.97258 | -0.19404 | 0.0013792 | 0.00034566
29 | 0.97259 | -0.19402 | 0.0006967 | 0.00017461
30 | 0.97945 | -0.14455 | 0.0023029 | 0.00057716
31 | 0.99082 | -0.064039 | 0.0020878 | 0.00052324
32 | 0.99087 | -0.063693 | 0.0016323 | 0.0004091
33 | 0.97989 | -0.14143 | 0 | 0
34 | 0.98069 | -0.13573 | 0.0059942 | 0.0015023
35 | 0.98099 | -0.13353 | 0.0036523 | 0.00091535
36 | 0.98384 | -0.11325 | 0.0017419 | 0.00043656
37 | 0.98351 | -0.11562 | 0.0045941 | 0.0011514
38 | 0.98397 | -0.11237 | 0.0055369 | 0.0013877
39 | 0.98568 | -0.10021 | 0 | 0
40 | 0.98731 | -0.088679 | 0.0030543 | 0.00076547
41 | 0.98743 | -0.087843 | 0 | 0
42 | 0.98978 | -0.071282 | 0.0014719 | 0.0003689
43 | 0.98691 | -0.091539 | 0.0026883 | 0.00067375
44 | 0.98714 | -0.089973 | 0.0029786 | 0.00074651
45 | 0.98639 | -0.095287 | 0.0019227 | 0.00048186
46 | 0.98844 | -0.080771 | 0.001654 | 0.00041454
47 | 0.98596 | -0.098293 | 0.0054574 | 0.0013678
48 | 0.98862 | -0.079494 | 0.0016266 | 0.00040767
49 | 0.98488 | -0.10599 | 0.0032947 | 0.00082573
50 | 0.98995 | -0.070147 | 0.0026233 | 0.00065745
51 | 0.98435 | -0.10969 | 0.0034964 | 0.00087629
52 | 0.99062 | -0.065426 | 0.0034646 | 0.0008683
53 | 0.98388 | -0.11306 | 0.0031166 | 0.0007811
54 | 0.98313 | -0.11838 | 0.0034222 | 0.00085768
55 | 0.98313 | -0.1184 | 0.004429 | 0.00111
56 | 0.98256 | -0.12247 | 0.0021443 | 0.00053741
57 | 0.98203 | -0.12626 | 0.0029456 | 0.00073823
58 | 0.98201 | -0.12638 | 0.0022004 | 0.00055147
59 | 0.9816 | -0.12932 | 0.0027753 | 0.00069555
60 | 0.98149 | -0.13006 | 0.0030692 | 0.00076921
61 | 0.98135 | -0.13105 | 0.0031107 | 0.00077962
62 | 0.98134 | -0.13117 | 0.0017719 | 0.00044408
63 | 0.99381 | -0.043328 | 0 | 0
64 | 0.99386 | -0.042932 | 0.0028983 | 0.00072639
65 | 0.99373 | -0.043911 | 0.002236 | 0.00056039
66 | 0.99401 | -0.041895 | 0.0026681 | 0.00066868
67 | 0.99407 | -0.041482 | 0.0036255 | 0.00090863
68 | 0.99424 | -0.040254 | 0.0027873 | 0.00069856
69 | 0.99447 | -0.038669 | 0.003616 | 0.00090624
70 | 0.995 | -0.034941 | 0.0023354 | 0.00058531
71 | 0.9953 | -0.032849 | 0.0030483 | 0.00076396
72 | 0.99598 | -0.028071 | 0.0049026 | 0.0012287
73 | 0.9969 | -0.021579 | 0.0037362 | 0.00093637
74 | 0.99799 | -0.013927 | 0 | 0
75 | 0.99718 | -0.019561 | 0.0037944 | 0.00095096
76 | 1 | 0 | -0.23226 | -0.058338
77 | 0.99421 | -0.040261 | 0.0020485 | 0.0005134
78 | 0.99891 | -0.0075419 | 0.0021972 | 0.00055068
79 | 0.99324 | -0.047033 | 0.0022676 | 0.00056832
80 | 0.99654 | -0.024026 | 0.0043273 | 0.0010845
81 | 0.99113 | -0.061843 | 0 | 0
82 | 0.99087 | -0.063679 | 0.0031468 | 0.00078866
83 | 0.98661 | -0.093689 | 0.013504 | 0.0033844
84 | 0.992 | -0.055717 | 0.0027646 | 0.00069288
85 | 0.9878 | -0.085535 | 0.006194 | 0.0015524
86 | 0.98922 | -0.075462 | 0.0017238 | 0.00043203
87 | 0.9895 | -0.073499 | 0.002858 | 0.00071627
88 | 0.99346 | -0.045544 | 0.0021988 | 0.00055107
89 | 0.99428 | -0.039807 | 0 | 0
90 | 0.99514 | -0.033769 | 0 | 0
91 | 0.99349 | -0.045351 | 0.0016707 | 0.0004187
92 | 0.99423 | -0.040213 | 0.0018216 | 0.00045653
93 | 0.99315 | -0.047728 | 0.0031933 | 0.00080033
94 | 0.99383 | -0.042999 | 0.0044603 | 0.0011179
95 | 0.99241 | -0.052935 | 0.0011691 | 0.00029299
96 | 0.99353 | -0.045144 | 0.0013071 | 0.00032759
97 | 0.99331 | -0.046716 | 0.0017692 | 0.00044341
98 | 0.99294 | -0.049275 | 0.0016443 | 0.00041211
99 | 0.9929 | -0.049582 | 0.0014302 | 0.00035844
100 | 0.98995 | -0.070339 | 0.0014612 | 0.00036622
101 | 0.98997 | -0.070217 | 0.0015803 | 0.00039605
102 | 0.98957 | -0.073046 | 0.0012618 | 0.00031624
103 | 0.99002 | -0.069819 | 0.0010282 | 0.0002577
104 | 0.9905 | -0.066446 | 0.0013838 | 0.00034682
105 | 0.99051 | -0.066342 | 0.0011957 | 0.00029966
106 | 0.9919 | -0.05657 | 0.0011693 | 0.00029306
107 | 0.99146 | -0.059681 | 0 | 0
108 | 0.99259 | -0.051761 | 0.0059265 | 0.0014853
109 | 0.99245 | -0.052742 | 0 | 0
110 | 0.99232 | -0.053674 | 0.0014797 | 0.00037085
111 | 0.99227 | -0.054049 | 0.0014015 | 0.00035125
112 | 0.99141 | -0.060025 | 0.00077668 | 0.00019466
113 | 0.99143 | -0.059903 | 0.00078945 | 0.00019785
114 | 0.99132 | -0.060629 | 0.0021098 | 0.00052877
115 | 0.99127 | -0.060981 | 0.0023798 | 0.00059642
116 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00093626 | 0.00023371 | -0.00093623 | -0.00023391 | 2.2221e-08 | -2.0593e-07 | 0.0014337 | 0.0014338 | 0.0014338 | 0.97148 | -0.20205 | 0.97145 | -0.20223 | 0.53104
1 | -0.0022307 | -0.00055814 | 0.0022311 | 0.00055772 | 3.1892e-07 | -4.1959e-07 | 0.0034165 | 0.0034163 | 0.0034165 | 0.97148 | -0.20205 | 0.97162 | -0.20102 | 1.2654
2 | 0.00032225 | 8.0036e-05 | -0.00032224 | -8.0762e-05 | 8.9606e-09 | -7.2662e-07 | 0.00049335 | 0.00049361 | 0.00049361 | 0.97145 | -0.20223 | 0.97143 | -0.20243 | 0.18282
3 | -0.0022311 | -0.00055772 | 0.0022311 | 0.00055766 | 4.5058e-08 | -5.9299e-08 | 0.0034163 | 0.0034163 | 0.0034163 | 0.97162 | -0.20102 | 0.97164 | -0.20087 | 1.2653
4 | -0.0024778 | -0.00061909 | 0.0024779 | 0.00061907 | 1.5433e-08 | -1.5345e-08 | 0.003794 | 0.003794 | 0.003794 | 0.97164 | -0.20087 | 0.97165 | -0.20083 | 1.4052
5 | 0.00024673 | 6.1428e-05 | -0.00024673 | -6.1837e-05 | 2.9461e-09 | -4.0859e-07 | 0.00037771 | 0.00037786 | 0.00037786 | 0.97164 | -0.20087 | 0.97163 | -0.20096 | 0.13995
6 | -0.0042764 | -0.0010686 | 0.0042769 | 0.0010686 | 5.1222e-07 | -4.0712e-08 | 0.0065441 | 0.006544 | 0.0065441 | 0.97221 | -0.19675 | 0.97233 | -0.19588 | 2.4237
7 | 0.0032275 | 0.00080571 | -0.0032257 | -0.00080649 | 1.8093e-06 | -7.7725e-07 | 0.0049387 | 0.0049392 | 0.0049392 | 0.97221 | -0.19675 | 0.97165 | -0.20083 | 1.8293
8 | -0.0042769 | -0.0010686 | 0.0042771 | 0.0010685 | 2.4185e-07 | -1.9245e-08 | 0.006544 | 0.006544 | 0.006544 | 0.97233 | -0.19588 | 0.97239 | -0.19547 | 2.4237
9 | -0.0042771 | -0.0010685 | 0.0042776 | 0.0010685 | 4.3497e-07 | -3.4649e-08 | 0.006544 | 0.0065439 | 0.006544 | 0.97239 | -0.19547 | 0.97249 | -0.19473 | 2.4237
10 | -0.0042776 | -0.0010685 | 0.0042787 | 0.0010684 | 1.1527e-06 | -9.205e-08 | 0.0065439 | 0.0065437 | 0.0065439 | 0.97249 | -0.19473 | 0.97276 | -0.19277 | 2.4237
11 | -0.0065833 | -0.0016448 | 0.0065882 | 0.0016457 | 4.8658e-06 | 9.1579e-07 | 0.010069 | 0.010068 | 0.010069 | 0.97276 | -0.19277 | 0.9735 | -0.1874 | 3.7291
12 | 0.0022025 | 0.00055085 | -0.0022022 | -0.00055126 | 2.9806e-07 | -4.0777e-07 | 0.0033688 | 0.003369 | 0.003369 | 0.97276 | -0.19277 | 0.97262 | -0.19375 | 1.2478
13 | -0.0068374 | -0.0017082 | 0.0068384 | 0.0017084 | 1.0128e-06 | 2.0468e-07 | 0.010449 | 0.010449 | 0.010449 | 0.9735 | -0.1874 | 0.97365 | -0.18632 | 3.87
14 | 0.00069673 | 0.00017417 | -0.0006967 | -0.00017461 | 2.5683e-08 | -4.3976e-07 | 0.0010658 | 0.0010659 | 0.0010659 | 0.97262 | -0.19375 | 0.97259 | -0.19402 | 0.39479
15 | 0.0015055 | 0.00037708 | -0.0015055 | -0.00037718 | 2.8931e-08 | -9.7339e-08 | 0.0023032 | 0.0023032 | 0.0023032 | 0.97262 | -0.19375 | 0.9726 | -0.19389 | 0.85305
16 | -0.00020742 | -5.1985e-05 | 0.00020743 | 5.1646e-05 | 1.7047e-09 | -3.3952e-07 | 0.00031655 | 0.00031643 | 0.00031655 | 0.97505 | -0.17623 | 0.97505 | -0.17617 | 0.11724
17 | -0.009202 | -0.0022996 | 0.0092036 | 0.0023001 | 1.6263e-06 | 4.6058e-07 | 0.014041 | 0.014041 | 0.014041 | 0.97505 | -0.17617 | 0.97523 | -0.17489 | 5.2002
18 | 0.0089946 | 0.002248 | -0.0089903 | -0.0022468 | 4.2851e-06 | 1.1936e-06 | 0.013724 | 0.013724 | 0.013724 | 0.97505 | -0.17617 | 0.97457 | -0.17964 | 5.0831
19 | -0.0095536 | -0.0023878 | 0.0095593 | 0.0023895 | 5.6623e-06 | 1.6445e-06 | 0.014575 | 0.014574 | 0.014575 | 0.97523 | -0.17489 | 0.97583 | -0.17059 | 5.398
20 | 0.0009511 | 0.00023806 | -0.00095107 | -0.00023836 | 3.3574e-08 | -3.0502e-07 | 0.0014521 | 0.0014522 | 0.0014522 | 0.97457 | -0.17964 | 0.97454 | -0.17989 | 0.53785
21 | 0.0071832 | 0.0017943 | -0.0071785 | -0.0017933 | 4.709e-06 | 1.0297e-06 | 0.010965 | 0.010966 | 0.010966 | 0.97457 | -0.17964 | 0.97392 | -0.1844 | 4.0614
22 | 0.00085597 | 0.00021445 | -0.00085596 | -0.00021452 | 6.7084e-09 | -7.585e-08 | 0.0013069 | 0.0013069 | 0.0013069 | 0.97457 | -0.17964 | 0.97457 | -0.17969 | 0.48404
23 | -0.014488 | -0.0036261 | 0.014505 | 0.0036319 | 1.6767e-05 | 5.7541e-06 | 0.022042 | 0.022042 | 0.022042 | 0.97799 | -0.15505 | 0.97915 | -0.14668 | 8.1638
24 | 0.010757 | 0.002691 | -0.010734 | -0.0026839 | 2.3014e-05 | 7.1274e-06 | 0.016365 | 0.016366 | 0.016366 | 0.97799 | -0.15505 | 0.97583 | -0.17059 | 6.0615
25 | -0.017281 | -0.0043276 | 0.017286 | 0.0043294 | 5.0802e-06 | 1.8054e-06 | 0.02626 | 0.02626 | 0.02626 | 0.97915 | -0.14668 | 0.97945 | -0.14455 | 9.7261
26 | 0.00017418 | 4.3338e-05 | -0.00017418 | -4.3383e-05 | 1.6032e-10 | -4.5109e-08 | 0.00026601 | 0.00026603 | 0.00026603 | 0.97392 | -0.1844 | 0.97391 | -0.18441 | 0.098529
27 | 0.0070043 | 0.0017499 | -0.0070025 | -0.0017495 | 1.8485e-06 | 3.8906e-07 | 0.0107 | 0.0107 | 0.0107 | 0.97392 | -0.1844 | 0.97365 | -0.18632 | 3.9629
28 | 0.00017418 | 4.3383e-05 | -0.00017418 | -4.3654e-05 | 9.6164e-10 | -2.705e-07 | 0.00026603 | 0.00026613 | 0.00026613 | 0.97391 | -0.18441 | 0.97391 | -0.18445 | 0.098565
29 | 0.0013792 | 0.00034553 | -0.0013792 | -0.00034566 | 2.9588e-08 | -1.2078e-07 | 0.00211 | 0.0021101 | 0.0021101 | 0.9726 | -0.19389 | 0.97258 | -0.19404 | 0.78152
30 | -0.019589 | -0.0049065 | 0.019597 | 0.0049096 | 8.4595e-06 | 3.0609e-06 | 0.029759 | 0.029759 | 0.029759 | 0.97945 | -0.14455 | 0.97989 | -0.14143 | 11.0218
31 | -0.0020878 | -0.00052324 | 0.0020879 | 0.00052307 | 1.0012e-07 | -1.7171e-07 | 0.0031354 | 0.0031353 | 0.0031354 | 0.99082 | -0.064039 | 0.99087 | -0.063693 | 1.1613
32 | -0.0037202 | -0.00093217 | 0.0037202 | 0.00093217 | 7.1095e-09 | -1.9675e-09 | 0.0055866 | 0.0055866 | 0.0055866 | 0.99087 | -0.063693 | 0.99087 | -0.063679 | 2.0691
33 | -0.019597 | -0.0049096 | 0.019613 | 0.0049152 | 1.5465e-05 | 5.5951e-06 | 0.029759 | 0.029759 | 0.029759 | 0.97989 | -0.14143 | 0.98069 | -0.13573 | 11.0218
34 | -0.025607 | -0.0064175 | 0.025615 | 0.0064204 | 7.8096e-06 | 2.899e-06 | 0.038854 | 0.038854 | 0.038854 | 0.98069 | -0.13573 | 0.98099 | -0.13353 | 14.3903
35 | -0.029267 | -0.0073357 | 0.02934 | 0.0073629 | 7.2736e-05 | 2.7227e-05 | 0.044394 | 0.044394 | 0.044394 | 0.98099 | -0.13353 | 0.98351 | -0.11562 | 16.4421
36 | 0.033945 | 0.0085185 | -0.033934 | -0.0085143 | 1.1159e-05 | 4.2057e-06 | 0.051344 | 0.051344 | 0.051344 | 0.98384 | -0.11325 | 0.98351 | -0.11562 | 19.0164
37 | -0.035687 | -0.0089551 | 0.035691 | 0.0089567 | 4.3828e-06 | 1.6551e-06 | 0.053979 | 0.053979 | 0.053979 | 0.98384 | -0.11325 | 0.98397 | -0.11237 | 19.9921
38 | -0.041228 | -0.010344 | 0.041298 | 0.010371 | 6.97e-05 | 2.6442e-05 | 0.062352 | 0.062352 | 0.062352 | 0.98397 | -0.11237 | 0.98568 | -0.10021 | 23.0933
39 | -0.041298 | -0.010371 | 0.041364 | 0.010396 | 6.6265e-05 | 2.5138e-05 | 0.062352 | 0.062352 | 0.062352 | 0.98568 | -0.10021 | 0.98731 | -0.088679 | 23.0933
40 | -0.044418 | -0.011161 | 0.044424 | 0.011163 | 5.1702e-06 | 1.9649e-06 | 0.066955 | 0.066955 | 0.066955 | 0.98731 | -0.088679 | 0.98743 | -0.087843 | 24.7981
41 | -0.060628 | -0.015226 | 0.060768 | 0.015279 | 0.0001399 | 5.3463e-05 | 0.091375 | 0.091375 | 0.091375 | 0.98743 | -0.087843 | 0.98978 | -0.071282 | 33.8425
42 | 0.016204 | 0.0040624 | -0.016196 | -0.0040595 | 8.2926e-06 | 2.9046e-06 | 0.02442 | 0.02442 | 0.02442 | 0.98743 | -0.087843 | 0.98691 | -0.091539 | 9.0444
43 | -0.06224 | -0.015648 | 0.062375 | 0.0157 | 0.00013526 | 5.1706e-05 | 0.093587 | 0.093587 | 0.093587 | 0.98978 | -0.071282 | 0.992 | -0.055717 | 34.662
44 | 0.013508 | 0.0033857 | -0.013504 | -0.0033844 | 4.0189e-06 | 1.3474e-06 | 0.020367 | 0.020367 | 0.020367 | 0.98691 | -0.091539 | 0.98661 | -0.093689 | 7.5432
45 | 0.043318 | 0.010876 | -0.043286 | -0.010864 | 3.1955e-05 | 1.2137e-05 | 0.065305 | 0.065305 | 0.065305 | 0.98714 | -0.089973 | 0.98639 | -0.095287 | 24.1869
46 | -0.046297 | -0.011622 | 0.046356 | 0.011645 | 5.9244e-05 | 2.2537e-05 | 0.069795 | 0.069794 | 0.069795 | 0.98714 | -0.089973 | 0.98844 | -0.080771 | 25.8498
47 | 0.041363 | 0.010382 | -0.041346 | -0.010375 | 1.7258e-05 | 6.547e-06 | 0.062404 | 0.062404 | 0.062404 | 0.98639 | -0.095287 | 0.98596 | -0.098293 | 23.1127
48 | -0.04801 | -0.012059 | 0.048018 | 0.012063 | 8.5278e-06 | 3.2464e-06 | 0.072284 | 0.072284 | 0.072284 | 0.98844 | -0.080771 | 0.98862 | -0.079494 | 26.772
49 | 0.035889 | 0.0090074 | -0.03585 | -0.008993 | 3.8302e-05 | 1.4465e-05 | 0.054168 | 0.054168 | 0.054168 | 0.98596 | -0.098293 | 0.98488 | -0.10599 | 20.0622
50 | -0.049645 | -0.01247 | 0.04971 | 0.012495 | 6.4614e-05 | 2.4613e-05 | 0.074733 | 0.074733 | 0.074733 | 0.98862 | -0.079494 | 0.98995 | -0.070147 | 27.6788
51 | 0.032556 | 0.0081672 | -0.032539 | -0.0081609 | 1.6727e-05 | 6.2927e-06 | 0.04919 | 0.04919 | 0.04919 | 0.98488 | -0.10599 | 0.98435 | -0.10969 | 18.2186
52 | -0.052333 | -0.013152 | 0.052367 | 0.013165 | 3.442e-05 | 1.3124e-05 | 0.078676 | 0.078676 | 0.078676 | 0.98995 | -0.070147 | 0.99062 | -0.065426 | 29.1392
53 | 0.029042 | 0.0072847 | -0.029029 | -0.0072796 | 1.3537e-05 | 5.0636e-06 | 0.043905 | 0.043905 | 0.043905 | 0.98435 | -0.10969 | 0.98388 | -0.11306 | 16.261
54 | -0.055832 | -0.014034 | 0.05586 | 0.014044 | 2.7868e-05 | 1.0637e-05 | 0.08388 | 0.08388 | 0.08388 | 0.99062 | -0.065426 | 0.99113 | -0.061843 | 31.0666
55 | 0.025912 | 0.0064985 | -0.025893 | -0.0064914 | 1.91e-05 | 7.0934e-06 | 0.039191 | 0.039191 | 0.039191 | 0.98388 | -0.11306 | 0.98313 | -0.11838 | 14.5153
56 | 0.022471 | 0.0056337 | -0.022471 | -0.0056337 | 6.226e-08 | 2.2852e-08 | 0.034012 | 0.034012 | 0.034012 | 0.98313 | -0.11838 | 0.98313 | -0.1184 | 12.5969
57 | 0.018042 | 0.0045237 | -0.018032 | -0.00452 | 1.016e-05 | 3.6309e-06 | 0.027308 | 0.027308 | 0.027308 | 0.98313 | -0.1184 | 0.98256 | -0.12247 | 10.1141
58 | 0.015887 | 0.0039826 | -0.015879 | -0.0039797 | 8.3379e-06 | 2.9147e-06 | 0.024061 | 0.024061 | 0.024061 | 0.98256 | -0.12247 | 0.98203 | -0.12626 | 8.9115
59 | 0.012934 | 0.0032415 | -0.012933 | -0.0032414 | 2.2134e-07 | 7.3446e-08 | 0.019598 | 0.019598 | 0.019598 | 0.98203 | -0.12626 | 0.98201 | -0.12638 | 7.2584
60 | 0.010733 | 0.0026899 | -0.010729 | -0.0026886 | 4.362e-06 | 1.3435e-06 | 0.016263 | 0.016264 | 0.016264 | 0.98201 | -0.12638 | 0.9816 | -0.12932 | 6.0235
61 | 0.0079533 | 0.001993 | -0.0079525 | -0.0019928 | 8.1926e-07 | 2.0094e-07 | 0.012056 | 0.012056 | 0.012056 | 0.9816 | -0.12932 | 0.98149 | -0.13006 | 4.4654
62 | 0.0048833 | 0.0012236 | -0.0048827 | -0.0012236 | 6.6974e-07 | 1.0148e-08 | 0.0074034 | 0.0074035 | 0.0074035 | 0.98149 | -0.13006 | 0.98135 | -0.13105 | 2.742
63 | 0.0017719 | 0.00044401 | -0.0017719 | -0.00044408 | 2.9846e-08 | -7.2235e-08 | 0.0026867 | 0.0026868 | 0.0026868 | 0.98135 | -0.13105 | 0.98134 | -0.13117 | 0.99509
64 | -0.0022361 | -0.00056012 | 0.0022363 | 0.00055994 | 1.224e-07 | -1.7968e-07 | 0.003348 | 0.003348 | 0.003348 | 0.99381 | -0.043328 | 0.99386 | -0.042932 | 1.24
65 | 0.0022361 | 0.00056012 | -0.002236 | -0.00056039 | 1.8052e-07 | -2.6493e-07 | 0.003348 | 0.0033482 | 0.0033482 | 0.99381 | -0.043328 | 0.99373 | -0.043911 | 1.2401
66 | -0.0051346 | -0.0012863 | 0.0051353 | 0.0012864 | 7.3661e-07 | 2.4409e-08 | 0.0076873 | 0.0076872 | 0.0076873 | 0.99386 | -0.042932 | 0.99401 | -0.041895 | 2.8472
67 | -0.0078034 | -0.001955 | 0.0078038 | 0.0019551 | 4.4593e-07 | 1.0362e-07 | 0.011681 | 0.011681 | 0.011681 | 0.99401 | -0.041895 | 0.99407 | -0.041482 | 4.3264
68 | -0.011429 | -0.0028638 | 0.011431 | 0.0028644 | 1.9418e-06 | 6.0897e-07 | 0.017108 | 0.017108 | 0.017108 | 0.99407 | -0.041482 | 0.99424 | -0.040254 | 6.3364
69 | -0.014219 | -0.0035629 | 0.014222 | 0.003564 | 3.1202e-06 | 1.0568e-06 | 0.02128 | 0.02128 | 0.02128 | 0.99424 | -0.040254 | 0.99447 | -0.038669 | 7.8814
70 | -0.017838 | -0.0044702 | 0.017847 | 0.0044735 | 9.2071e-06 | 3.2723e-06 | 0.02669 | 0.02669 | 0.02669 | 0.99447 | -0.038669 | 0.995 | -0.034941 | 9.8852
71 | -0.020182 | -0.0050588 | 0.020188 | 0.0050609 | 5.8501e-06 | 2.1163e-06 | 0.030183 | 0.030183 | 0.030183 | 0.995 | -0.034941 | 0.9953 | -0.032849 | 11.1788
72 | -0.023236 | -0.0058249 | 0.023252 | 0.0058305 | 1.5386e-05 | 5.6518e-06 | 0.03474 | 0.03474 | 0.03474 | 0.9953 | -0.032849 | 0.99598 | -0.028071 | 12.8666
73 | -0.028154 | -0.0070593 | 0.02818 | 0.0070687 | 2.5347e-05 | 9.4496e-06 | 0.042064 | 0.042064 | 0.042064 | 0.99598 | -0.028071 | 0.9969 | -0.021579 | 15.5794
74 | -0.031916 | -0.0080051 | 0.03195 | 0.0080178 | 3.3898e-05 | 1.2725e-05 | 0.047641 | 0.047641 | 0.047641 | 0.9969 | -0.021579 | 0.99799 | -0.013927 | 17.6448
75 | 0.071281 | 0.017967 | -0.071225 | -0.017946 | 5.6189e-05 | 2.1507e-05 | 0.10632 | 0.10632 | 0.10632 | 0.99799 | -0.013927 | 0.99718 | -0.019561 | 39.3766
76 | -0.10323 | -0.025985 | 0.10343 | 0.026062 | 0.00020118 | 7.72e-05 | 0.15396 | 0.15396 | 0.15396 | 0.99799 | -0.013927 | 1 | 0 | 57.0214
77 | 0.067431 | 0.016995 | -0.067236 | -0.01692 | 0.00019484 | 7.4538e-05 | 0.10065 | 0.10065 | 0.10065 | 0.99718 | -0.019561 | 0.99421 | -0.040261 | 37.2796
78 | 0.12803 | 0.032276 | -0.1279 | -0.032224 | 0.0001351 | 5.1651e-05 | 0.19058 | 0.19058 | 0.19058 | 1 | 0 | 0.99891 | -0.0075419 | 35.2923
79 | 0.065187 | 0.016407 | -0.065126 | -0.016383 | 6.1575e-05 | 2.3549e-05 | 0.097589 | 0.097589 | 0.097589 | 0.99421 | -0.040261 | 0.99324 | -0.047033 | 36.1441
80 | 0.1257 | 0.031673 | -0.12541 | -0.031563 | 0.00028927 | 0.00011057 | 0.18731 | 0.18731 | 0.18731 | 0.99891 | -0.0075419 | 0.99654 | -0.024026 | 34.6862
81 | 0.062858 | 0.015815 | -0.062728 | -0.015766 | 0.00012961 | 4.9548e-05 | 0.094192 | 0.094192 | 0.094192 | 0.99324 | -0.047033 | 0.99113 | -0.061843 | 34.8859
82 | 0.12108 | 0.030478 | -0.12092 | -0.030415 | 0.00016453 | 6.286e-05 | 0.18084 | 0.18084 | 0.18084 | 0.99654 | -0.024026 | 0.99514 | -0.033769 | 33.4897
83 | 0.0068687 | 0.0017212 | -0.006867 | -0.0017208 | 1.7447e-06 | 3.3227e-07 | 0.010312 | 0.010312 | 0.010312 | 0.99113 | -0.061843 | 0.99087 | -0.063679 | 3.8193
84 | -0.06514 | -0.016393 | 0.065232 | 0.016428 | 9.2621e-05 | 3.482e-05 | 0.097734 | 0.097734 | 0.097734 | 0.992 | -0.055717 | 0.99346 | -0.045544 | 18.0989
85 | -0.006194 | -0.0015524 | 0.0062027 | 0.0015537 | 8.639e-06 | 1.2839e-06 | 0.0093306 | 0.0093299 | 0.0093306 | 0.9878 | -0.085535 | 0.98922 | -0.075462 | 3.4558
86 | -0.0079265 | -0.0019857 | 0.0079287 | 0.0019862 | 2.1521e-06 | 5.1618e-07 | 0.011923 | 0.011923 | 0.011923 | 0.98922 | -0.075462 | 0.9895 | -0.073499 | 4.4159
87 | -0.010787 | -0.0027025 | 0.010787 | 0.0027027 | 6.7567e-07 | 2.0701e-07 | 0.016221 | 0.016221 | 0.016221 | 0.9895 | -0.073499 | 0.98957 | -0.073046 | 6.0076
88 | -0.067431 | -0.016979 | 0.067485 | 0.016999 | 5.4107e-05 | 2.037e-05 | 0.10103 | 0.10103 | 0.10103 | 0.99346 | -0.045544 | 0.99428 | -0.039807 | 18.7088
89 | -0.099551 | -0.025047 | 0.099635 | 0.025078 | 8.3919e-05 | 3.1962e-05 | 0.14902 | 0.14902 | 0.14902 | 0.99428 | -0.039807 | 0.99514 | -0.033769 | 27.5963
90 | 0.032066 | 0.0080475 | -0.032041 | -0.0080382 | 2.466e-05 | 9.2622e-06 | 0.047993 | 0.047993 | 0.047993 | 0.99428 | -0.039807 | 0.99349 | -0.045351 | 17.7752
91 | 0.021282 | 0.0053368 | -0.021263 | -0.0053299 | 1.899e-05 | 6.9139e-06 | 0.031824 | 0.031824 | 0.031824 | 0.99514 | -0.033769 | 0.99423 | -0.040213 | 11.7868
92 | 0.030371 | 0.0076195 | -0.030361 | -0.0076157 | 1.0012e-05 | 3.7504e-06 | 0.045491 | 0.045491 | 0.045491 | 0.99349 | -0.045351 | 0.99315 | -0.047728 | 16.8484
93 | 0.019442 | 0.0048734 | -0.019434 | -0.0048707 | 7.4979e-06 | 2.6999e-06 | 0.029098 | 0.029098 | 0.029098 | 0.99423 | -0.040213 | 0.99383 | -0.042999 | 10.7771
94 | 0.027167 | 0.0068154 | -0.027148 | -0.0068081 | 1.9607e-05 | 7.2961e-06 | 0.040706 | 0.040706 | 0.040706 | 0.99315 | -0.047728 | 0.99241 | -0.052935 | 15.0764
95 | 0.014974 | 0.0037528 | -0.01497 | -0.0037513 | 4.4445e-06 | 1.5259e-06 | 0.02242 | 0.02242 | 0.02242 | 0.99383 | -0.042999 | 0.99353 | -0.045144 | 8.3037
96 | 0.025979 | 0.0065151 | -0.025965 | -0.0065103 | 1.3084e-05 | 4.8537e-06 | 0.038953 | 0.038954 | 0.038954 | 0.99241 | -0.052935 | 0.9919 | -0.05657 | 14.4272
97 | 0.013663 | 0.0034237 | -0.01366 | -0.0034227 | 2.9714e-06 | 9.9559e-07 | 0.020462 | 0.020462 | 0.020462 | 0.99353 | -0.045144 | 0.99331 | -0.046716 | 7.5787
98 | 0.01189 | 0.0029793 | -0.011886 | -0.0029779 | 4.2091e-06 | 1.3438e-06 | 0.017812 | 0.017812 | 0.017812 | 0.99331 | -0.046716 | 0.99294 | -0.049275 | 6.5971
99 | 0.010242 | 0.0025658 | -0.010241 | -0.0025657 | 4.3487e-07 | 1.2899e-07 | 0.015348 | 0.015348 | 0.015348 | 0.99294 | -0.049275 | 0.9929 | -0.049582 | 5.6844
100 | 0.0088112 | 0.0022073 | -0.0088085 | -0.0022066 | 2.6559e-06 | 7.0587e-07 | 0.013205 | 0.013205 | 0.013205 | 0.9929 | -0.049582 | 0.99259 | -0.051761 | 4.8906
101 | -0.013515 | -0.0033866 | 0.013515 | 0.0033867 | 2.2701e-07 | 7.5978e-08 | 0.020314 | 0.020314 | 0.020314 | 0.98995 | -0.070339 | 0.98997 | -0.070217 | 7.5238
102 | 0.012054 | 0.0030204 | -0.012049 | -0.0030189 | 4.5151e-06 | 1.4533e-06 | 0.018118 | 0.018118 | 0.018118 | 0.98995 | -0.070339 | 0.98957 | -0.073046 | 6.7104
103 | -0.015095 | -0.0037827 | 0.015096 | 0.003783 | 8.3187e-07 | 2.8665e-07 | 0.02269 | 0.02269 | 0.02269 | 0.98997 | -0.070217 | 0.99002 | -0.069819 | 8.4036
104 | -0.016124 | -0.0040407 | 0.016132 | 0.0040433 | 7.5305e-06 | 2.632e-06 | 0.024235 | 0.024235 | 0.024235 | 0.99002 | -0.069819 | 0.9905 | -0.066446 | 8.9759
105 | -0.017516 | -0.0043902 | 0.017516 | 0.0043902 | 2.5202e-07 | 8.9423e-08 | 0.026314 | 0.026314 | 0.026314 | 0.9905 | -0.066446 | 0.99051 | -0.066342 | 9.7459
106 | -0.018712 | -0.0046899 | 0.018729 | 0.0046961 | 1.7271e-05 | 6.1915e-06 | 0.02811 | 0.02811 | 0.02811 | 0.99051 | -0.066342 | 0.99146 | -0.059681 | 10.4111
107 | 0.024796 | 0.0062172 | -0.024785 | -0.0062133 | 1.0686e-05 | 3.9505e-06 | 0.037199 | 0.037199 | 0.037199 | 0.9919 | -0.05657 | 0.99146 | -0.059681 | 13.7776
108 | 0.0044903 | 0.001125 | -0.0044897 | -0.0011251 | 5.8903e-07 | -4.1458e-08 | 0.0067391 | 0.0067391 | 0.0067391 | 0.99146 | -0.059681 | 0.99132 | -0.060629 | 2.496
109 | 0.0015662 | 0.00039215 | -0.0015661 | -0.00039231 | 4.7874e-08 | -1.6066e-07 | 0.0023505 | 0.0023505 | 0.0023505 | 0.99146 | -0.059681 | 0.99143 | -0.059903 | 0.87057
110 | 0.002882 | 0.00072123 | -0.0028816 | -0.00072151 | 3.9029e-07 | -2.8299e-07 | 0.0043201 | 0.0043203 | 0.0043203 | 0.99259 | -0.051761 | 0.99245 | -0.052742 | 1.6001
111 | 0.0028816 | 0.00072151 | -0.0028813 | -0.00072178 | 3.7147e-07 | -2.692e-07 | 0.0043203 | 0.0043204 | 0.0043204 | 0.99245 | -0.052742 | 0.99232 | -0.053674 | 1.6002
112 | 0.0014016 | 0.00035093 | -0.0014015 | -0.00035125 | 7.2634e-08 | -3.125e-07 | 0.0021016 | 0.0021017 | 0.0021017 | 0.99232 | -0.053674 | 0.99227 | -0.054049 | 0.7784
113 | -0.00077668 | -0.00019466 | 0.0007767 | 0.00019446 | 1.3148e-08 | -1.9489e-07 | 0.0011657 | 0.0011657 | 0.0011657 | 0.99141 | -0.060025 | 0.99143 | -0.059903 | 0.43175
114 | 0.0023799 | 0.00059628 | -0.0023798 | -0.00059642 | 1.1563e-07 | -1.4274e-07 | 0.0035722 | 0.0035723 | 0.0035723 | 0.99132 | -0.060629 | 0.99127 | -0.060981 | 1.3231

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23694 | 0.059511

## res_load
| p_mw | q_mvar
0 | 0.0012945 | 0.00032443
1 | 0.00061398 | 0.00015388
2 | 0.00032224 | 8.0762e-05
3 | 0.0010489 | 0.00026288
4 | 0.00074781 | 0.00018742
5 | 0.00024673 | 6.1837e-05
6 | 0.00010201 | 2.5567e-05
7 | 0.00024921 | 6.2457e-05
8 | 0.00020742 | 5.1985e-05
9 | 0.00035003 | 8.7726e-05
10 | 0.0037311 | 0.00093509
11 | 0.0027758 | 0.00069568
12 | 0.0011749 | 0.00029446
13 | 0.00095107 | 0.00023836
14 | 0.00085596 | 0.00021452
15 | 0.0001641 | 4.1126e-05
16 | 0.00017418 | 4.3654e-05
17 | 0.00012627 | 3.1647e-05
18 | 0.0013792 | 0.00034566
19 | 0.0006967 | 0.00017461
20 | 0.0023029 | 0.00057716
21 | 0.0020878 | 0.00052324
22 | 0.0016323 | 0.0004091
23 | 0.0059942 | 0.0015023
24 | 0.0036523 | 0.00091535
25 | 0.0017419 | 0.00043656
26 | 0.0045941 | 0.0011514
27 | 0.0055369 | 0.0013877
28 | 0.0030543 | 0.00076547
29 | 0.0014719 | 0.0003689
30 | 0.0026883 | 0.00067375
31 | 0.0029786 | 0.00074651
32 | 0.0019227 | 0.00048186
33 | 0.001654 | 0.00041454
34 | 0.0054574 | 0.0013678
35 | 0.0016266 | 0.00040767
36 | 0.0032947 | 0.00082573
37 | 0.0026233 | 0.00065745
38 | 0.0034964 | 0.00087629
39 | 0.0034646 | 0.0008683
40 | 0.0031166 | 0.0007811
41 | 0.0034222 | 0.00085768
42 | 0.004429 | 0.00111
43 | 0.0021443 | 0.00053741
44 | 0.0029456 | 0.00073823
45 | 0.0022004 | 0.00055147
46 | 0.0027753 | 0.00069555
47 | 0.0030692 | 0.00076921
48 | 0.0031107 | 0.00077962
49 | 0.0017719 | 0.00044408
50 | 0.0028983 | 0.00072639
51 | 0.002236 | 0.00056039
52 | 0.0026681 | 0.00066868
53 | 0.0036255 | 0.00090863
54 | 0.0027873 | 0.00069856
55 | 0.003616 | 0.00090624
56 | 0.0023354 | 0.00058531
57 | 0.0030483 | 0.00076396
58 | 0.0049026 | 0.0012287
59 | 0.0037362 | 0.00093637
60 | 0.0037944 | 0.00095096
61 | 0.0046819 | 0.0011734
62 | 0.0020485 | 0.0005134
63 | 0.0021972 | 0.00055068
64 | 0.0022676 | 0.00056832
65 | 0.0043273 | 0.0010845
66 | 0.0031468 | 0.00078866
67 | 0.013504 | 0.0033844
68 | 0.0027646 | 0.00069288
69 | 0.006194 | 0.0015524
70 | 0.0017238 | 0.00043203
71 | 0.002858 | 0.00071627
72 | 0.0021988 | 0.00055107
73 | 0.0016707 | 0.0004187
74 | 0.0018216 | 0.00045653
75 | 0.0031933 | 0.00080033
76 | 0.0044603 | 0.0011179
77 | 0.0011691 | 0.00029299
78 | 0.0013071 | 0.00032759
79 | 0.0017692 | 0.00044341
80 | 0.0016443 | 0.00041211
81 | 0.0014302 | 0.00035844
82 | 0.0014612 | 0.00036622
83 | 0.0015803 | 0.00039605
84 | 0.0012618 | 0.00031624
85 | 0.0010282 | 0.0002577
86 | 0.0013838 | 0.00034682
87 | 0.0011957 | 0.00029966
88 | 0.0011693 | 0.00029306
89 | 0.0059265 | 0.0014853
90 | 0.0014797 | 0.00037085
91 | 0.0014015 | 0.00035125
92 | 0.00077668 | 0.00019466
93 | 0.00078945 | 0.00019785
94 | 0.0021098 | 0.00052877
95 | 0.0023798 | 0.00059642

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1