## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2117-12_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2117-12_0_2_node_12 | 0.4 | n |  | TRUE
2 | bus_LV_2117-12_0_2_node_10 | 0.4 | n |  | TRUE
3 | bus_LV_2117-12_0_2_node_1 | 0.4 | n |  | TRUE
4 | bus_LV_2117-12_0_2_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_2117-12_0_2_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_2117-12_0_2_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2117-12_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2117-12_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2117-12_0_2_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_2117-12_0_2_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_2117-12_0_2_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2117-12_0_2_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_2117-12_0_2_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_2117-12_0_2_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_2117-12_0_2_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2117-12_0_2_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2117-12_0_2_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2117-12_0_2_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2117-12_0_2_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2117-12_0_2_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2117-12_0_2_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2117-12_0_2_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2117-12_0_2_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_2117-12_0_2_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_2117-12_0_2_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_2117-12_0_2_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_2117-12_0_2_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2117-12_0_2_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_2117-12_0_2_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2117-12_0_2_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_2117-12_0_2_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_2117-12_0_2_node_31 | 0.4 | n |  | TRUE
33 | bus_MV_27_2_node_125 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2117-12_0_2_load_0 | 0 | 0.00062467 | 0.00015656 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2117-12_0_2_load_12 | 1 | 0.00091197 | 0.00022856 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2117-12_0_2_load_10 | 2 | 0.00059955 | 0.00015026 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2117-12_0_2_load_1 | 3 | 0.028081 | 0.0070378 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2117-12_0_2_load_5 | 7 | 0.0076449 | 0.001916 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2117-12_0_2_load_6 | 8 | 0.036887 | 0.0092447 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2117-12_0_2_load_29 | 9 | 0.00061678 | 0.00015458 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2117-12_0_2_load_28 | 10 | 0.0019321 | 0.00048423 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2117-12_0_2_load_7 | 11 | 0.03058 | 0.0076642 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2117-12_0_2_load_32 | 13 | 0.00022322 | 5.5944e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2117-12_0_2_load_8 | 15 | 0.035326 | 0.0088536 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2117-12_0_2_load_13 | 16 | 0.0010409 | 0.00026087 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2117-12_0_2_load_9 | 17 | 0.0111 | 0.002782 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2117-12_0_2_load_16 | 19 | 0.00027899 | 6.9922e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2117-12_0_2_load_14 | 20 | 0.00086437 | 0.00021663 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2117-12_0_2_load_17 | 21 | 0.0014547 | 0.00036457 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2117-12_0_2_load_18 | 22 | 0.0051704 | 0.0012958 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2117-12_0_2_load_19 | 23 | 0.00095844 | 0.00024021 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2117-12_0_2_load_21 | 25 | 0.00037315 | 9.3519e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2117-12_0_2_load_22 | 26 | 0.0031339 | 0.00078544 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2117-12_0_2_load_23 | 27 | 0.0016216 | 0.00040642 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2117-12_0_2_load_24 | 28 | 0.00049078 | 0.000123 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2117-12_0_2_load_25 | 29 | 0.039659 | 0.0099395 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2117-12_0_2_load_26 | 30 | 0.0016048 | 0.00040221 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2117-12_0_2_load_30 | 31 | 0.000881 | 0.0002208 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2117-12_0_2_load_31 | 32 | 0.0014586 | 0.00036557 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2117-12_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.12049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2117-12_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.0039844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2117-12_0_2_line_2 | NAYY 4x150 SE | 2 | 17 | 0.026704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2117-12_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.03775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2117-12_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0013151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2117-12_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.067053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2117-12_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.019481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_2117-12_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.065009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2117-12_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.032534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2117-12_0_2_line_9 | NAYY 4x150 SE | 6 | 10 | 0.0081215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2117-12_0_2_line_10 | NAYY 4x150 SE | 7 | 11 | 0.013699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_2117-12_0_2_line_11 | NAYY 4x150 SE | 8 | 12 | 0.0067919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2117-12_0_2_line_12 | NAYY 4x150 SE | 9 | 13 | 0.0012544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2117-12_0_2_line_13 | NAYY 4x150 SE | 10 | 14 | 0.028245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2117-12_0_2_line_14 | NAYY 4x150 SE | 11 | 15 | 0.049954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_2117-12_0_2_line_15 | NAYY 4x150 SE | 12 | 16 | 0.031881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2117-12_0_2_line_16 | NAYY 4x150 SE | 12 | 17 | 0.02032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2117-12_0_2_line_17 | NAYY 4x150 SE | 14 | 31 | 0.04884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2117-12_0_2_line_18 | NAYY 4x150 SE | 14 | 30 | 0.02032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2117-12_0_2_line_19 | NAYY 4x150 SE | 16 | 18 | 0.00092904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2117-12_0_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.037975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2117-12_0_2_line_21 | NAYY 4x150 SE | 18 | 20 | 0.025248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2117-12_0_2_line_22 | NAYY 4x150 SE | 19 | 21 | 0.0019003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2117-12_0_2_line_23 | NAYY 4x150 SE | 21 | 22 | 0.033786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2117-12_0_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.012194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2117-12_0_2_line_25 | NAYY 4x150 SE | 23 | 24 | 0.015526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2117-12_0_2_line_26 | NAYY 4x150 SE | 24 | 25 | 0.0073442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2117-12_0_2_line_27 | NAYY 4x150 SE | 25 | 26 | 0.047109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2117-12_0_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.034323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2117-12_0_2_line_29 | NAYY 4x150 SE | 27 | 29 | 0.026776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2117-12_0_2_line_30 | NAYY 4x150 SE | 28 | 30 | 0.020593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2117-12_0_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.01599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2117-12_0_2_trafo_8 | 0.25 MVA 20/0.4 kV | 33 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2563849.7902 | 1176735.3852 | 2563961.4757 | 1176690.1674
1 | 2563849.7902 | 1176735.3852 | 2563848.1263 | 1176739.0056
2 | 2563848.1263 | 1176739.0056 | 2563843.3859 | 1176749.3201 | 2563834.2904 | 1176761.6875
3 | 2563742.8451 | 1176700.8809 | 2563750.5495 | 1176704.7696 | 2563759.4298 | 1176711.0191 | 2563772.7805 | 1176723.4781
4 | 2563773.6653 | 1176724.4511 | 2563772.7805 | 1176723.4781
5 | 2563742.8451 | 1176700.8809 | 2563741.2202 | 1176703.8924 | 2563739.3023 | 1176706.4831 | 2563735.5887 | 1176710.3743 | 2563730.1989 | 1176713.8644 | 2563705.7327 | 1176727.3309 | 2563687.2113 | 1176736.8261
6 | 2563773.6653 | 1176724.4511 | 2563763.7609 | 1176734.6053 | 2563759.3854 | 1176737.5894
7 | 2563773.6653 | 1176724.4511 | 2563801.7411 | 1176755.5197 | 2563817.2529 | 1176772.6822
8 | 2563687.2113 | 1176736.8261 | 2563665.9874 | 1176727.9281 | 2563658.4296 | 1176722.1393
9 | 2563687.2113 | 1176736.8261 | 2563682.8153 | 1176739.0873 | 2563680.0147 | 1176740.5896
10 | 2563748.0678 | 1176745.3081 | 2563759.3854 | 1176737.5894
11 | 2563821.8071 | 1176777.721 | 2563817.2529 | 1176772.6822
12 | 2563657.4337 | 1176721.3766 | 2563658.4296 | 1176722.1393
13 | 2563655.1249 | 1176753.941 | 2563680.0147 | 1176740.5896
14 | 2563748.0678 | 1176745.3081 | 2563746.7882 | 1176746.1808 | 2563735.2455 | 1176755.8558 | 2563733.4918 | 1176760.3133 | 2563733.3511 | 1176766.0949 | 2563736.2265 | 1176770.1685 | 2563751.1039 | 1176779.9127
15 | 2563821.8071 | 1176777.721 | 2563830.7013 | 1176787.5502 | 2563842.9137 | 1176801.6123
16 | 2563821.8071 | 1176777.721 | 2563834.1305 | 1176761.9049 | 2563834.2904 | 1176761.6875
17 | 2563655.1249 | 1176753.941 | 2563627.427 | 1176768.7949 | 2563611.6497 | 1176776.1583
18 | 2563655.1249 | 1176753.941 | 2563667.1331 | 1176770.3328
19 | 2563843.5229 | 1176802.3138 | 2563842.9137 | 1176801.6123
20 | 2563843.5229 | 1176802.3138 | 2563868.4108 | 1176830.9959
21 | 2563843.5229 | 1176802.3138 | 2563858.9815 | 1176782.3516
22 | 2563868.4108 | 1176830.9959 | 2563869.6562 | 1176832.4312
23 | 2563890.1511 | 1176859.2887 | 2563870.3821 | 1176833.2678 | 2563869.6562 | 1176832.4312
24 | 2563890.1511 | 1176859.2887 | 2563897.5278 | 1176868.9983
25 | 2563906.9205 | 1176881.3614 | 2563897.5278 | 1176868.9983
26 | 2563906.9205 | 1176881.3614 | 2563901.6754 | 1176886.502
27 | 2563860.5303 | 1176901.4186 | 2563866.5892 | 1176896.1237 | 2563891.7409 | 1176896.2385 | 2563901.6754 | 1176886.502
28 | 2563699.5863 | 1176814.6332 | 2563679.3029 | 1176786.9453
29 | 2563699.5863 | 1176814.6332 | 2563715.4101 | 1176836.2334
30 | 2563679.3029 | 1176786.9453 | 2563667.1331 | 1176770.3328
31 | 2563597.1603 | 1176782.9206 | 2563611.6497 | 1176776.1583

## bus_geodata
| x | y | coords
0 | 2563961.4757 | 1176690.1674
1 | 2563849.7902 | 1176735.3852
2 | 2563848.1263 | 1176739.0056
3 | 2563772.7805 | 1176723.4781
4 | 2563742.8451 | 1176700.8809
5 | 2563773.6653 | 1176724.4511
6 | 2563687.2113 | 1176736.8261
7 | 2563759.3854 | 1176737.5894
8 | 2563817.2529 | 1176772.6822
9 | 2563658.4296 | 1176722.1393
10 | 2563680.0147 | 1176740.5896
11 | 2563748.0678 | 1176745.3081
12 | 2563821.8071 | 1176777.721
13 | 2563657.4337 | 1176721.3766
14 | 2563655.1249 | 1176753.941
15 | 2563751.1039 | 1176779.9127
16 | 2563842.9137 | 1176801.6123
17 | 2563834.2904 | 1176761.6875
18 | 2563843.5229 | 1176802.3138
19 | 2563868.4108 | 1176830.9959
20 | 2563858.9815 | 1176782.3516
21 | 2563869.6562 | 1176832.4312
22 | 2563890.1511 | 1176859.2887
23 | 2563897.5278 | 1176868.9983
24 | 2563906.9205 | 1176881.3614
25 | 2563901.6754 | 1176886.502
26 | 2563860.5303 | 1176901.4186
27 | 2563699.5863 | 1176814.6332
28 | 2563679.3029 | 1176786.9453
29 | 2563715.4101 | 1176836.2334
30 | 2563667.1331 | 1176770.3328
31 | 2563611.6497 | 1176776.1583
32 | 2563597.1603 | 1176782.9206
33 | 2563760.8643 | 1176786.3055

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98328 | -0.11715 | 0.00062467 | 0.00015656
1 | 0.98339 | -0.11636 | 0.00091197 | 0.00022856
2 | 0.9834 | -0.1163 | 0.00059955 | 0.00015026
3 | 0.98996 | -0.069858 | 0.028081 | 0.0070378
4 | 0.98728 | -0.088561 | 0 | 0
5 | 0.99011 | -0.068832 | 0 | 0
6 | 0.98253 | -0.12203 | 0 | 0
7 | 0.99209 | -0.054973 | 0.0076449 | 0.001916
8 | 0.98413 | -0.11107 | 0.036887 | 0.0092447
9 | 0.98249 | -0.12231 | 0.00061678 | 0.00015458
10 | 0.98196 | -0.12603 | 0.0019321 | 0.00048423
11 | 0.99355 | -0.04473 | 0.03058 | 0.0076642
12 | 0.98387 | -0.11293 | 0 | 0
13 | 0.98249 | -0.12232 | 0.00022322 | 5.5944e-05
14 | 0.98008 | -0.13943 | 0 | 0
15 | 1 | 0 | -0.18175 | -0.045709
16 | 0.98326 | -0.1173 | 0.0010409 | 0.00026087
17 | 0.98348 | -0.11571 | 0.0111 | 0.002782
18 | 0.98324 | -0.11742 | 0 | 0
19 | 0.98262 | -0.12189 | 0.00027899 | 6.9922e-05
20 | 0.98321 | -0.11765 | 0.00086437 | 0.00021663
21 | 0.98259 | -0.1221 | 0.0014547 | 0.00036457
22 | 0.98211 | -0.12547 | 0.0051704 | 0.0012958
23 | 0.98203 | -0.12604 | 0.00095844 | 0.00024021
24 | 0.98196 | -0.1266 | 0 | 0
25 | 0.98192 | -0.12687 | 0.00037315 | 9.3519e-05
26 | 0.9817 | -0.1284 | 0.0031339 | 0.00078544
27 | 0.97545 | -0.17241 | 0.0016216 | 0.00040642
28 | 0.97753 | -0.15758 | 0.00049078 | 0.000123
29 | 0.9739 | -0.18356 | 0.039659 | 0.0099395
30 | 0.97879 | -0.1486 | 0.0016048 | 0.00040221
31 | 0.97991 | -0.14062 | 0.000881 | 0.0002208
32 | 0.97988 | -0.14086 | 0.0014586 | 0.00036557
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00062467 | -0.00015656 | 0.00062474 | 0.00015506 | 6.7152e-08 | -1.5027e-06 | 0.00094533 | 0.00094479 | 0.00094533 | 0.98328 | -0.11715 | 0.98339 | -0.11636 | 0.35012
1 | -0.0015367 | -0.00038362 | 0.0015367 | 0.00038357 | 1.3436e-08 | -4.5383e-08 | 0.0023247 | 0.0023247 | 0.0023247 | 0.98339 | -0.11636 | 0.9834 | -0.1163 | 0.86101
2 | -0.0021363 | -0.00053383 | 0.0021365 | 0.00053356 | 1.7404e-07 | -2.7189e-07 | 0.0032319 | 0.0032318 | 0.0032319 | 0.9834 | -0.1163 | 0.98348 | -0.11571 | 1.197
3 | 0.049214 | 0.012427 | -0.049085 | -0.012378 | 0.00012902 | 4.9138e-05 | 0.074007 | 0.074007 | 0.074007 | 0.98996 | -0.069858 | 0.98728 | -0.088561 | 27.4101
4 | -0.077295 | -0.019465 | 0.077306 | 0.019469 | 1.1083e-05 | 4.2459e-06 | 0.11622 | 0.11622 | 0.11622 | 0.98996 | -0.069858 | 0.99011 | -0.068832 | 43.043
5 | 0.049085 | 0.012378 | -0.048856 | -0.012291 | 0.00022917 | 8.7288e-05 | 0.074007 | 0.074008 | 0.074008 | 0.98728 | -0.088561 | 0.98253 | -0.12203 | 27.4102
6 | -0.14111 | -0.035509 | 0.14138 | 0.035614 | 0.00027349 | 0.00010469 | 0.21212 | 0.21212 | 0.21212 | 0.99011 | -0.068832 | 0.99209 | -0.054973 | 39.2823
7 | 0.063805 | 0.01604 | -0.063431 | -0.015897 | 0.00037314 | 0.00014268 | 0.095908 | 0.095908 | 0.095908 | 0.99011 | -0.068832 | 0.98413 | -0.11107 | 35.5217
8 | 0.00084004 | 0.00021011 | -0.00084 | -0.00021051 | 3.2854e-08 | -3.9938e-07 | 0.0012721 | 0.0012722 | 0.0012722 | 0.98253 | -0.12203 | 0.98249 | -0.12231 | 0.47119
9 | 0.048016 | 0.012081 | -0.047989 | -0.01207 | 2.6811e-05 | 1.0209e-05 | 0.072735 | 0.072736 | 0.072736 | 0.98253 | -0.12203 | 0.98196 | -0.12603 | 26.9391
10 | -0.14903 | -0.03753 | 0.14924 | 0.037611 | 0.00021368 | 8.1829e-05 | 0.22359 | 0.22359 | 0.22359 | 0.99209 | -0.054973 | 0.99355 | -0.04473 | 41.4057
11 | 0.026545 | 0.0066523 | -0.026538 | -0.0066498 | 6.8272e-06 | 2.5396e-06 | 0.040136 | 0.040136 | 0.040136 | 0.98413 | -0.11107 | 0.98387 | -0.11293 | 14.8651
12 | 0.00022322 | 5.5929e-05 | -0.00022322 | -5.5944e-05 | 8.9507e-11 | -1.5851e-08 | 0.00033807 | 0.00033808 | 0.00033808 | 0.98249 | -0.12231 | 0.98249 | -0.12232 | 0.12521
13 | 0.046057 | 0.011586 | -0.045971 | -0.011554 | 8.5887e-05 | 3.2677e-05 | 0.069808 | 0.069808 | 0.069808 | 0.98196 | -0.12603 | 0.98008 | -0.13943 | 25.8548
14 | -0.17982 | -0.045276 | 0.18095 | 0.045709 | 0.0011311 | 0.00043372 | 0.26939 | 0.26939 | 0.26939 | 0.99355 | -0.04473 | 1 | 0 | 49.887
15 | 0.013296 | 0.0033326 | -0.013288 | -0.0033299 | 8.0449e-06 | 2.6896e-06 | 0.02011 | 0.02011 | 0.02011 | 0.98387 | -0.11293 | 0.98326 | -0.1173 | 7.448
16 | 0.013242 | 0.0033172 | -0.013237 | -0.0033155 | 5.0853e-06 | 1.6979e-06 | 0.020026 | 0.020026 | 0.020026 | 0.98387 | -0.11293 | 0.98348 | -0.11571 | 7.4172
17 | 0.0023401 | 0.00058572 | -0.0023397 | -0.00058618 | 3.8466e-07 | -4.6742e-07 | 0.0035526 | 0.0035528 | 0.0035528 | 0.98008 | -0.13943 | 0.97991 | -0.14062 | 1.3158
18 | 0.043631 | 0.010968 | -0.043575 | -0.010947 | 5.566e-05 | 2.1152e-05 | 0.066255 | 0.066255 | 0.066255 | 0.98008 | -0.13943 | 0.97879 | -0.1486 | 24.539
19 | 0.012247 | 0.003069 | -0.012247 | -0.0030689 | 1.9915e-07 | 6.4812e-08 | 0.018534 | 0.018534 | 0.018534 | 0.98326 | -0.1173 | 0.98324 | -0.11742 | 6.8646
20 | 0.011383 | 0.0028526 | -0.011376 | -0.0028504 | 7.0319e-06 | 2.2232e-06 | 0.017226 | 0.017227 | 0.017227 | 0.98324 | -0.11742 | 0.98262 | -0.12189 | 6.3802
21 | 0.00086439 | 0.00021632 | -0.00086437 | -0.00021663 | 2.6958e-08 | -3.0985e-07 | 0.001308 | 0.0013082 | 0.0013082 | 0.98324 | -0.11742 | 0.98321 | -0.11765 | 0.4845
22 | 0.011097 | 0.0027805 | -0.011096 | -0.0027804 | 3.3484e-07 | 1.0471e-07 | 0.016804 | 0.016804 | 0.016804 | 0.98262 | -0.12189 | 0.98259 | -0.1221 | 6.2237
23 | 0.0096418 | 0.0024158 | -0.0096373 | -0.0024145 | 4.4948e-06 | 1.301e-06 | 0.014601 | 0.014601 | 0.014601 | 0.98259 | -0.1221 | 0.98211 | -0.12547 | 5.4079
24 | 0.0044669 | 0.0011187 | -0.0044666 | -0.0011187 | 3.485e-07 | -2.0253e-08 | 0.0067676 | 0.0067677 | 0.0067677 | 0.98211 | -0.12547 | 0.98203 | -0.12604 | 2.5065
25 | 0.0035081 | 0.00087848 | -0.0035079 | -0.00087857 | 2.7374e-07 | -9.1142e-08 | 0.0053154 | 0.0053155 | 0.0053155 | 0.98203 | -0.12604 | 0.98196 | -0.1266 | 1.9687
26 | 0.0035079 | 0.00087857 | -0.0035077 | -0.00087862 | 1.2948e-07 | -4.31e-08 | 0.0053155 | 0.0053155 | 0.0053155 | 0.98196 | -0.1266 | 0.98192 | -0.12687 | 1.9687
27 | 0.0031346 | 0.0007851 | -0.0031339 | -0.00078544 | 6.6328e-07 | -3.4065e-07 | 0.00475 | 0.0047502 | 0.0047502 | 0.98192 | -0.12687 | 0.9817 | -0.1284 | 1.7594
28 | -0.041342 | -0.010369 | 0.041427 | 0.010402 | 8.5191e-05 | 3.2336e-05 | 0.063069 | 0.063069 | 0.063069 | 0.97545 | -0.17241 | 0.97753 | -0.15758 | 23.3588
29 | 0.039721 | 0.0099628 | -0.039659 | -0.0099395 | 6.1349e-05 | 2.3262e-05 | 0.060595 | 0.060595 | 0.060595 | 0.97545 | -0.17241 | 0.9739 | -0.18356 | 22.4426
30 | -0.041918 | -0.010525 | 0.041971 | 0.010544 | 5.2331e-05 | 1.9869e-05 | 0.063816 | 0.063816 | 0.063816 | 0.97753 | -0.15758 | 0.97879 | -0.1486 | 23.6354
31 | 0.0014587 | 0.00036538 | -0.0014586 | -0.00036557 | 4.8952e-08 | -1.8259e-07 | 0.002215 | 0.002215 | 0.002215 | 0.97991 | -0.14062 | 0.97988 | -0.14086 | 0.82039

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21708 | 0.054563

## res_load
| p_mw | q_mvar
0 | 0.00062467 | 0.00015656
1 | 0.00091197 | 0.00022856
2 | 0.00059955 | 0.00015026
3 | 0.028081 | 0.0070378
4 | 0.0076449 | 0.001916
5 | 0.036887 | 0.0092447
6 | 0.00061678 | 0.00015458
7 | 0.0019321 | 0.00048423
8 | 0.03058 | 0.0076642
9 | 0.00022322 | 5.5944e-05
10 | 0.035326 | 0.0088536
11 | 0.0010409 | 0.00026087
12 | 0.0111 | 0.002782
13 | 0.00027899 | 6.9922e-05
14 | 0.00086437 | 0.00021663
15 | 0.0014547 | 0.00036457
16 | 0.0051704 | 0.0012958
17 | 0.00095844 | 0.00024021
18 | 0.00037315 | 9.3519e-05
19 | 0.0031339 | 0.00078544
20 | 0.0016216 | 0.00040642
21 | 0.00049078 | 0.000123
22 | 0.039659 | 0.0099395
23 | 0.0016048 | 0.00040221
24 | 0.000881 | 0.0002208
25 | 0.0014586 | 0.00036557

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1