## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2117-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2117-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2117-8_0_4_node_28 | 0.4 | n |  | TRUE
3 | bus_LV_2117-8_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2117-8_0_4_node_23 | 0.4 | n |  | TRUE
5 | bus_LV_2117-8_0_4_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_2117-8_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_2117-8_0_4_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_2117-8_0_4_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_2117-8_0_4_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_2117-8_0_4_node_34 | 0.4 | n |  | TRUE
11 | bus_LV_2117-8_0_4_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_2117-8_0_4_node_35 | 0.4 | n |  | TRUE
13 | bus_LV_2117-8_0_4_node_30 | 0.4 | n |  | TRUE
14 | bus_LV_2117-8_0_4_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_2117-8_0_4_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_2117-8_0_4_node_37 | 0.4 | n |  | TRUE
17 | bus_LV_2117-8_0_4_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_2117-8_0_4_node_41 | 0.4 | n |  | TRUE
19 | bus_LV_2117-8_0_4_node_3 | 0.4 | n |  | TRUE
20 | bus_LV_2117-8_0_4_node_4 | 0.4 | n |  | TRUE
21 | bus_LV_2117-8_0_4_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_2117-8_0_4_node_8 | 0.4 | n |  | TRUE
23 | bus_LV_2117-8_0_4_node_39 | 0.4 | n |  | TRUE
24 | bus_LV_2117-8_0_4_node_9 | 0.4 | n |  | TRUE
25 | bus_LV_2117-8_0_4_node_5 | 0.4 | n |  | TRUE
26 | bus_LV_2117-8_0_4_node_6 | 0.4 | n |  | TRUE
27 | bus_LV_2117-8_0_4_node_7 | 0.4 | n |  | TRUE
28 | bus_LV_2117-8_0_4_node_11 | 0.4 | n |  | TRUE
29 | bus_LV_2117-8_0_4_node_10 | 0.4 | n |  | TRUE
30 | bus_LV_2117-8_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_2117-8_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_2117-8_0_4_node_12 | 0.4 | n |  | TRUE
33 | bus_LV_2117-8_0_4_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_2117-8_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_2117-8_0_4_node_13 | 0.4 | n |  | TRUE
36 | bus_LV_2117-8_0_4_node_14 | 0.4 | n |  | TRUE
37 | bus_LV_2117-8_0_4_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_2117-8_0_4_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_2117-8_0_4_node_38 | 0.4 | n |  | TRUE
40 | bus_MV_27_2_node_142 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2117-8_0_4_load_0 | 0 | 0.012178 | 0.0030522 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2117-8_0_4_load_1 | 1 | 0.0093193 | 0.0023356 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2117-8_0_4_load_2 | 3 | 0.0090274 | 0.0022625 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2117-8_0_4_load_23 | 4 | 0.0078949 | 0.0019786 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2117-8_0_4_load_27 | 8 | 0.00043373 | 0.0001087 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2117-8_0_4_load_34 | 10 | 0.0018304 | 0.00045873 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2117-8_0_4_load_35 | 12 | 0.00058074 | 0.00014555 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2117-8_0_4_load_30 | 13 | 0.052286 | 0.013104 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2117-8_0_4_load_31 | 14 | 0.016462 | 0.0041258 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2117-8_0_4_load_33 | 15 | 0.032271 | 0.0080879 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2117-8_0_4_load_37 | 16 | 0.0071313 | 0.0017873 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2117-8_0_4_load_41 | 18 | 0.024098 | 0.0060396 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2117-8_0_4_load_4 | 20 | 0.004553 | 0.0011411 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2117-8_0_4_load_8 | 22 | 0.0061696 | 0.0015463 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2117-8_0_4_load_39 | 23 | 0.0060598 | 0.0015187 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2117-8_0_4_load_5 | 25 | 0.0079161 | 0.001984 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2117-8_0_4_load_6 | 26 | 0.0075972 | 0.001904 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2117-8_0_4_load_11 | 28 | 0.0048556 | 0.0012169 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2117-8_0_4_load_10 | 29 | 0.0035837 | 0.00089817 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2117-8_0_4_load_18 | 31 | 0.0029044 | 0.00072792 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2117-8_0_4_load_12 | 32 | 0.0032601 | 0.00081705 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2117-8_0_4_load_16 | 33 | 0.0024892 | 0.00062385 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2117-8_0_4_load_20 | 34 | 0.0027336 | 0.0006851 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2117-8_0_4_load_13 | 35 | 0.0023908 | 0.00059918 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2117-8_0_4_load_14 | 36 | 0.0037739 | 0.00094583 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2117-8_0_4_load_21 | 37 | 0.003769 | 0.0009446 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2117-8_0_4_load_22 | 38 | 0.0037959 | 0.00095133 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2117-8_0_4_load_38 | 39 | 0.0022176 | 0.00055577 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2117-8_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.029072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_2117-8_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.19254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_2117-8_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.028922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_2117-8_0_4_line_3 | NAYY 4x150 SE | 2 | 6 | 0.015945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_2117-8_0_4_line_4 | NAYY 4x150 SE | 3 | 19 | 0.023032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_2117-8_0_4_line_5 | NAYY 4x150 SE | 4 | 5 | 0.048094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_2117-8_0_4_line_6 | NAYY 4x150 SE | 4 | 6 | 0.047251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_2117-8_0_4_line_7 | NAYY 4x150 SE | 5 | 7 | 0.015534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2117-8_0_4_line_8 | NAYY 4x150 SE | 5 | 8 | 0.061117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_2117-8_0_4_line_9 | NAYY 4x150 SE | 6 | 9 | 0.02745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_2117-8_0_4_line_10 | NAYY 4x150 SE | 7 | 10 | 0.022039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2117-8_0_4_line_11 | NAYY 4x150 SE | 8 | 11 | 0.030023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_2117-8_0_4_line_12 | NAYY 4x150 SE | 9 | 12 | 0.030599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_2117-8_0_4_line_13 | NAYY 4x150 SE | 11 | 13 | 0.079672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_2117-8_0_4_line_14 | NAYY 4x150 SE | 12 | 17 | 0.056959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2117-8_0_4_line_15 | NAYY 4x150 SE | 13 | 14 | 0.13034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_2117-8_0_4_line_16 | NAYY 4x150 SE | 14 | 15 | 0.017837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2117-8_0_4_line_17 | NAYY 4x150 SE | 15 | 16 | 0.00086224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2117-8_0_4_line_18 | NAYY 4x150 SE | 17 | 18 | 0.10416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2117-8_0_4_line_19 | NAYY 4x150 SE | 19 | 20 | 0.021942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2117-8_0_4_line_20 | NAYY 4x150 SE | 19 | 21 | 0.10508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2117-8_0_4_line_21 | NAYY 4x150 SE | 20 | 22 | 0.030126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2117-8_0_4_line_22 | NAYY 4x150 SE | 21 | 23 | 0.033036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2117-8_0_4_line_23 | NAYY 4x150 SE | 22 | 24 | 0.02449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2117-8_0_4_line_24 | NAYY 4x150 SE | 23 | 39 | 0.042795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2117-8_0_4_line_25 | NAYY 4x150 SE | 24 | 30 | 0.052985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2117-8_0_4_line_26 | NAYY 4x150 SE | 24 | 31 | 0.014785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2117-8_0_4_line_27 | NAYY 4x150 SE | 24 | 32 | 0.016531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2117-8_0_4_line_28 | NAYY 4x150 SE | 25 | 26 | 0.0076713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2117-8_0_4_line_29 | NAYY 4x150 SE | 26 | 27 | 0.017655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2117-8_0_4_line_30 | NAYY 4x150 SE | 27 | 28 | 0.012684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2117-8_0_4_line_31 | NAYY 4x150 SE | 28 | 29 | 0.027513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2117-8_0_4_line_32 | NAYY 4x150 SE | 29 | 32 | 0.034382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2117-8_0_4_line_33 | NAYY 4x150 SE | 30 | 33 | 0.023791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2117-8_0_4_line_34 | NAYY 4x150 SE | 31 | 34 | 0.014531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2117-8_0_4_line_35 | NAYY 4x150 SE | 33 | 36 | 0.042156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2117-8_0_4_line_36 | NAYY 4x150 SE | 34 | 37 | 0.01367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2117-8_0_4_line_37 | NAYY 4x150 SE | 35 | 36 | 0.024844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2117-8_0_4_line_38 | NAYY 4x150 SE | 37 | 38 | 0.030871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2117-8_0_4_trafo_35 | 0.25 MVA 20/0.4 kV | 40 | 12 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2563589.9109 | 1174452.2008 | 2563611.5733 | 1174471.589
1 | 2563589.9109 | 1174452.2008 | 2563576.9517 | 1174260.0992
2 | 2563611.5733 | 1174471.589 | 2563633.1246 | 1174490.8776
3 | 2563563.6932 | 1174251.1864 | 2563576.9517 | 1174260.0992
4 | 2563650.2864 | 1174506.2376 | 2563633.1246 | 1174490.8776
5 | 2563485.0642 | 1174197.2596 | 2563524.7261 | 1174224.4612
6 | 2563563.6932 | 1174251.1864 | 2563524.7261 | 1174224.4612
7 | 2563485.0642 | 1174197.2596 | 2563475.828 | 1174209.7669
8 | 2563485.0642 | 1174197.2596 | 2563497.1015 | 1174180.1772 | 2563520.8638 | 1174147.7281
9 | 2563563.6932 | 1174251.1864 | 2563572.2954 | 1174240.0059 | 2563580.0893 | 1174229.1751
10 | 2563475.828 | 1174209.7669 | 2563469.2307 | 1174204.9268 | 2563470.1383 | 1174192.0368 | 2563470.7639 | 1174191.3426
11 | 2563538.6017 | 1174123.5058 | 2563520.8638 | 1174147.7281
12 | 2563580.0893 | 1174229.1751 | 2563598.8736 | 1174205.0198
13 | 2563538.6017 | 1174123.5058 | 2563570.2979 | 1174080.2235 | 2563588.4804 | 1174061.6035
14 | 2563633.8393 | 1174160.0566 | 2563598.8736 | 1174205.0198
15 | 2563588.4804 | 1174061.6035 | 2563604.7196 | 1174044.9735 | 2563634.106 | 1174019.0369 | 2563680.8864 | 1173985.3686 | 2563689.7161 | 1173980.127
16 | 2563705.0545 | 1173971.0216 | 2563689.7161 | 1173980.127
17 | 2563705.7959 | 1173970.5815 | 2563705.0545 | 1173971.0216
18 | 2563633.8393 | 1174160.0566 | 2563732.1741 | 1174194.4001
19 | 2563650.2864 | 1174506.2376 | 2563635.588 | 1174522.5287
20 | 2563650.2864 | 1174506.2376 | 2563741.892 | 1174557.7088
21 | 2563615.9006 | 1174545.312 | 2563621.7549 | 1174537.8608 | 2563635.588 | 1174522.5287
22 | 2563741.892 | 1174557.7088 | 2563760.7449 | 1174584.8374
23 | 2563600.7704 | 1174564.569 | 2563615.9006 | 1174545.312
24 | 2563785.1671 | 1174619.98 | 2563760.7449 | 1174584.8374
25 | 2563600.7704 | 1174564.569 | 2563591.8875 | 1174577.2852 | 2563585.6402 | 1174588.4179 | 2563580.1584 | 1174595.933 | 2563576.055 | 1174600.049 | 2563572.403 | 1174602.9617 | 2563567.9982 | 1174605.2786
26 | 2563600.7704 | 1174564.569 | 2563610.1102 | 1174576.0311
27 | 2563600.7704 | 1174564.569 | 2563590.9636 | 1174553.6229 | 2563589.7761 | 1174552.225
28 | 2563585.1288 | 1174473.8631 | 2563579.4147 | 1174478.9816
29 | 2563565.6368 | 1174489.9549 | 2563571.7358 | 1174485.8601 | 2563579.4147 | 1174478.9816
30 | 2563565.6368 | 1174489.9549 | 2563562.7787 | 1174502.3123
31 | 2563565.6113 | 1174527.851 | 2563563.73 | 1174525.8519 | 2563559.6147 | 1174516.7278 | 2563561.942 | 1174505.9302 | 2563562.7787 | 1174502.3123
32 | 2563589.7761 | 1174552.225 | 2563584.218 | 1174545.682 | 2563573.1335 | 1174535.8443 | 2563565.6113 | 1174527.851
33 | 2563567.9982 | 1174605.2786 | 2563564.1004 | 1174605.4913 | 2563557.6465 | 1174604.0298 | 2563549.6842 | 1174598.4198 | 2563547.5904 | 1174595.5778
34 | 2563618.5043 | 1174587.877 | 2563612.6867 | 1174579.1931 | 2563610.1102 | 1174576.0311
35 | 2563547.5904 | 1174595.5778 | 2563542.7538 | 1174589.0127 | 2563533.935 | 1174573.3471 | 2563527.1889 | 1174559.0807 | 2563527.0782 | 1174558.8645
36 | 2563618.5043 | 1174587.877 | 2563622.8632 | 1174594.3836 | 2563626.2875 | 1174599.112
37 | 2563512.617 | 1174538.9472 | 2563515.2375 | 1174541.2442 | 2563519.1942 | 1174545.6669 | 2563522.7863 | 1174550.4808 | 2563527.0782 | 1174558.8645
38 | 2563644.3943 | 1174624.1151 | 2563626.2875 | 1174599.112

## bus_geodata
| x | y | coords
0 | 2563589.9109 | 1174452.2008
1 | 2563611.5733 | 1174471.589
2 | 2563576.9517 | 1174260.0992
3 | 2563633.1246 | 1174490.8776
4 | 2563524.7261 | 1174224.4612
5 | 2563485.0642 | 1174197.2596
6 | 2563563.6932 | 1174251.1864
7 | 2563475.828 | 1174209.7669
8 | 2563520.8638 | 1174147.7281
9 | 2563580.0893 | 1174229.1751
10 | 2563470.7639 | 1174191.3426
11 | 2563538.6017 | 1174123.5058
12 | 2563598.8736 | 1174205.0198
13 | 2563588.4804 | 1174061.6035
14 | 2563689.7161 | 1173980.127
15 | 2563705.0545 | 1173971.0216
16 | 2563705.7959 | 1173970.5815
17 | 2563633.8393 | 1174160.0566
18 | 2563732.1742 | 1174194.4001
19 | 2563650.2864 | 1174506.2376
20 | 2563635.588 | 1174522.5287
21 | 2563741.892 | 1174557.7088
22 | 2563615.9006 | 1174545.312
23 | 2563760.7449 | 1174584.8374
24 | 2563600.7704 | 1174564.569
25 | 2563585.1287 | 1174473.8631
26 | 2563579.4147 | 1174478.9816
27 | 2563565.6368 | 1174489.9549
28 | 2563562.7787 | 1174502.3123
29 | 2563565.6113 | 1174527.851
30 | 2563567.9982 | 1174605.2786
31 | 2563610.1102 | 1174576.0311
32 | 2563589.7761 | 1174552.225
33 | 2563547.5904 | 1174595.5778
34 | 2563618.5043 | 1174587.877
35 | 2563512.617 | 1174538.9472
36 | 2563527.0782 | 1174558.8645
37 | 2563626.2875 | 1174599.112
38 | 2563644.3943 | 1174624.1151
39 | 2563785.1671 | 1174619.98
40 | 2563616.821 | 1174181.9408

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98388 | -0.1122 | 0.012178 | 0.0030522
1 | 0.98265 | -0.12085 | 0.0093193 | 0.0023356
2 | 0.99311 | -0.047501 | 0 | 0
3 | 0.98157 | -0.12855 | 0.0090274 | 0.0022625
4 | 0.99116 | -0.06109 | 0.0078949 | 0.0019786
5 | 0.98858 | -0.079133 | 0 | 0
6 | 0.99388 | -0.042195 | 0 | 0
7 | 0.98853 | -0.079424 | 0 | 0
8 | 0.98535 | -0.10181 | 0.00043373 | 0.0001087
9 | 0.99677 | -0.022178 | 0 | 0
10 | 0.98848 | -0.079836 | 0.0018304 | 0.00045873
11 | 0.98377 | -0.11296 | 0 | 0
12 | 1 | 0 | -0.24684 | -0.062303
13 | 0.97957 | -0.14272 | 0.052286 | 0.013104
14 | 0.97424 | -0.1808 | 0.016462 | 0.0041258
15 | 0.97321 | -0.1882 | 0.032271 | 0.0080879
16 | 0.9732 | -0.18826 | 0.0071313 | 0.0017873
17 | 0.99803 | -0.013733 | 0 | 0
18 | 0.99443 | -0.03898 | 0.024098 | 0.0060396
19 | 0.98042 | -0.13669 | 0 | 0
20 | 0.9785 | -0.15034 | 0.004553 | 0.0011411
21 | 0.97915 | -0.14574 | 0 | 0
22 | 0.97606 | -0.16774 | 0.0061696 | 0.0015463
23 | 0.97875 | -0.14859 | 0.0060598 | 0.0015187
24 | 0.9743 | -0.18036 | 0 | 0
25 | 0.97083 | -0.20533 | 0.0079161 | 0.001984
26 | 0.97091 | -0.20468 | 0.0075972 | 0.001904
27 | 0.97132 | -0.20179 | 0 | 0
28 | 0.97161 | -0.1997 | 0.0048556 | 0.0012169
29 | 0.97243 | -0.19378 | 0.0035837 | 0.00089817
30 | 0.97363 | -0.1852 | 0 | 0
31 | 0.97401 | -0.18242 | 0.0029044 | 0.00072792
32 | 0.97364 | -0.1851 | 0.0032601 | 0.00081705
33 | 0.97332 | -0.18737 | 0.0024892 | 0.00062385
34 | 0.97379 | -0.18399 | 0.0027336 | 0.0006851
35 | 0.97286 | -0.19073 | 0.0023908 | 0.00059918
36 | 0.97294 | -0.19011 | 0.0037739 | 0.00094583
37 | 0.97364 | -0.18508 | 0.003769 | 0.0009446
38 | 0.97347 | -0.18632 | 0.0037959 | 0.00095133
39 | 0.97862 | -0.14958 | 0.0022176 | 0.00055577
40 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.087125 | 0.02192 | -0.08702 | -0.021881 | 0.00010504 | 3.9294e-05 | 0.1318 | 0.1318 | 0.1318 | 0.98388 | -0.1122 | 0.98265 | -0.12085 | 16.2714
1 | -0.099303 | -0.024972 | 0.10021 | 0.025313 | 0.00090367 | 0.00034016 | 0.15022 | 0.15021 | 0.15022 | 0.98388 | -0.1122 | 0.99311 | -0.047501 | 18.5453
2 | 0.0777 | 0.019545 | -0.077617 | -0.019514 | 8.332e-05 | 3.0948e-05 | 0.11769 | 0.11769 | 0.11769 | 0.98265 | -0.12085 | 0.98157 | -0.12855 | 14.5292
3 | -0.10021 | -0.025313 | 0.10028 | 0.025341 | 7.4836e-05 | 2.8163e-05 | 0.15021 | 0.15021 | 0.15021 | 0.99311 | -0.047501 | 0.99388 | -0.042195 | 18.5449
4 | 0.06859 | 0.017252 | -0.068512 | -0.017223 | 7.7725e-05 | 2.9312e-05 | 0.104 | 0.104 | 0.104 | 0.98157 | -0.12855 | 0.98042 | -0.13669 | 19.2596
5 | 0.112 | 0.028271 | -0.11172 | -0.028164 | 0.00028308 | 0.00010702 | 0.16822 | 0.16822 | 0.16822 | 0.99116 | -0.06109 | 0.98858 | -0.079133 | 20.768
6 | -0.1199 | -0.03025 | 0.12022 | 0.03037 | 0.00031869 | 0.00012074 | 0.18007 | 0.18007 | 0.18007 | 0.99116 | -0.06109 | 0.99388 | -0.042195 | 22.2311
7 | 0.0018305 | 0.00045832 | -0.0018305 | -0.00045849 | 7.3583e-08 | -1.7086e-07 | 0.0027552 | 0.0027552 | 0.0027552 | 0.98858 | -0.079133 | 0.98853 | -0.079424 | 1.0205
8 | 0.10989 | 0.027706 | -0.10954 | -0.027574 | 0.00034805 | 0.00013152 | 0.16547 | 0.16547 | 0.16547 | 0.98858 | -0.079133 | 0.98535 | -0.10181 | 20.4279
9 | -0.2205 | -0.055711 | 0.22112 | 0.05595 | 0.00062286 | 0.00023849 | 0.33029 | 0.33028 | 0.33029 | 0.99388 | -0.042195 | 0.99677 | -0.022178 | 40.776
10 | 0.0018305 | 0.00045849 | -0.0018304 | -0.00045873 | 1.044e-07 | -2.4237e-07 | 0.0027552 | 0.0027553 | 0.0027553 | 0.98853 | -0.079424 | 0.98848 | -0.079836 | 1.0205
11 | 0.10911 | 0.027465 | -0.10894 | -0.027401 | 0.00016962 | 6.4094e-05 | 0.16481 | 0.16481 | 0.16481 | 0.98535 | -0.10181 | 0.98377 | -0.11296 | 20.3471
12 | -0.22112 | -0.05595 | 0.22182 | 0.056216 | 0.00069431 | 0.00026584 | 0.33028 | 0.33028 | 0.33028 | 0.99677 | -0.022178 | 1 | 0 | 40.7759
13 | 0.10894 | 0.027401 | -0.10849 | -0.027231 | 0.00045014 | 0.00017011 | 0.16481 | 0.16481 | 0.16481 | 0.98377 | -0.11296 | 0.97957 | -0.14272 | 20.3472
14 | 0.024229 | 0.0060878 | -0.024183 | -0.0060707 | 4.6213e-05 | 1.7028e-05 | 0.036059 | 0.036059 | 0.036059 | 1 | 0 | 0.99803 | -0.013733 | 13.3551
15 | 0.056202 | 0.014127 | -0.055905 | -0.014016 | 0.00029651 | 0.00011078 | 0.085388 | 0.085389 | 0.085389 | 0.97957 | -0.14272 | 0.97424 | -0.1808 | 15.8127
16 | 0.039443 | 0.0098905 | -0.039403 | -0.0098752 | 4.0398e-05 | 1.5316e-05 | 0.060245 | 0.060245 | 0.060245 | 0.97424 | -0.1808 | 0.97321 | -0.1882 | 22.3131
17 | 0.0071313 | 0.0017873 | -0.0071313 | -0.0017873 | 6.3967e-08 | 1.3889e-08 | 0.010904 | 0.010904 | 0.010904 | 0.97321 | -0.1882 | 0.9732 | -0.18826 | 4.0384
18 | 0.024183 | 0.0060707 | -0.024098 | -0.0060396 | 8.4511e-05 | 3.1148e-05 | 0.036059 | 0.036059 | 0.036059 | 0.99803 | -0.013733 | 0.99443 | -0.03898 | 13.3553
19 | 0.060221 | 0.015145 | -0.060106 | -0.015101 | 0.00011442 | 4.3733e-05 | 0.091418 | 0.091418 | 0.091418 | 0.98042 | -0.13669 | 0.9785 | -0.15034 | 33.8584
20 | 0.0082914 | 0.0020776 | -0.008281 | -0.0020749 | 1.0383e-05 | 2.6702e-06 | 0.012584 | 0.012584 | 0.012584 | 0.98042 | -0.13669 | 0.97915 | -0.14574 | 4.6609
21 | 0.055553 | 0.01396 | -0.055419 | -0.013909 | 0.00013421 | 5.1241e-05 | 0.084494 | 0.084494 | 0.084494 | 0.9785 | -0.15034 | 0.97606 | -0.16774 | 31.2941
22 | 0.008281 | 0.0020749 | -0.0082777 | -0.0020741 | 3.2647e-06 | 8.403e-07 | 0.012584 | 0.012585 | 0.012585 | 0.97915 | -0.14574 | 0.97875 | -0.14859 | 4.661
23 | 0.049249 | 0.012363 | -0.049163 | -0.01233 | 8.6162e-05 | 3.2834e-05 | 0.075088 | 0.075088 | 0.075088 | 0.97606 | -0.16774 | 0.9743 | -0.18036 | 27.8106
24 | 0.0022179 | 0.00055535 | -0.0022176 | -0.00055577 | 3.036e-07 | -4.21e-07 | 0.0033717 | 0.0033719 | 0.0033719 | 0.97875 | -0.14859 | 0.97862 | -0.14958 | 1.2488
25 | 0.0086648 | 0.0021713 | -0.008659 | -0.0021697 | 5.7901e-06 | 1.5676e-06 | 0.013233 | 0.013234 | 0.013234 | 0.9743 | -0.18036 | 0.97363 | -0.1852 | 4.9013
26 | 0.013211 | 0.003311 | -0.013207 | -0.0033098 | 3.7558e-06 | 1.2605e-06 | 0.020176 | 0.020176 | 0.020176 | 0.9743 | -0.18036 | 0.97401 | -0.18242 | 7.4728
27 | 0.027288 | 0.0068475 | -0.02727 | -0.0068408 | 1.7919e-05 | 6.6861e-06 | 0.041679 | 0.041679 | 0.041679 | 0.9743 | -0.18036 | 0.97364 | -0.1851 | 15.4366
28 | -0.0079161 | -0.001984 | 0.0079168 | 0.0019841 | 7.0471e-07 | 1.7618e-07 | 0.012133 | 0.012133 | 0.012133 | 0.97083 | -0.20533 | 0.97091 | -0.20468 | 4.4938
29 | -0.015514 | -0.0038882 | 0.01552 | 0.0038904 | 6.2281e-06 | 2.177e-06 | 0.023777 | 0.023777 | 0.023777 | 0.97091 | -0.20468 | 0.97132 | -0.20179 | 8.8062
30 | -0.01552 | -0.0038904 | 0.015525 | 0.0038919 | 4.4743e-06 | 1.5639e-06 | 0.023777 | 0.023777 | 0.023777 | 0.97132 | -0.20179 | 0.97161 | -0.1997 | 8.8061
31 | -0.02038 | -0.0051088 | 0.020397 | 0.0051149 | 1.6726e-05 | 6.092e-06 | 0.031213 | 0.031213 | 0.031213 | 0.97161 | -0.1997 | 0.97243 | -0.19378 | 11.5603
32 | -0.023981 | -0.0060131 | 0.02401 | 0.0060238 | 2.8891e-05 | 1.0685e-05 | 0.036697 | 0.036696 | 0.036697 | 0.97243 | -0.19378 | 0.97364 | -0.1851 | 13.5913
33 | 0.008659 | 0.0021697 | -0.0086564 | -0.002169 | 2.5999e-06 | 7.0419e-07 | 0.013234 | 0.013234 | 0.013234 | 0.97363 | -0.1852 | 0.97332 | -0.18737 | 4.9014
34 | 0.010302 | 0.0025819 | -0.0103 | -0.0025812 | 2.2463e-06 | 6.8313e-07 | 0.015739 | 0.015739 | 0.015739 | 0.97401 | -0.18242 | 0.97379 | -0.18399 | 5.8294
35 | 0.0061672 | 0.0015452 | -0.0061649 | -0.0015448 | 2.3384e-06 | 3.7564e-07 | 0.0094283 | 0.0094285 | 0.0094285 | 0.97332 | -0.18737 | 0.97294 | -0.19011 | 3.492
36 | 0.0075667 | 0.0018961 | -0.0075655 | -0.0018958 | 1.1403e-06 | 2.6856e-07 | 0.011562 | 0.011562 | 0.011562 | 0.97379 | -0.18399 | 0.97364 | -0.18508 | 4.2823
37 | -0.0023908 | -0.00059918 | 0.002391 | 0.00059895 | 2.0729e-07 | -2.2878e-07 | 0.0036568 | 0.0036567 | 0.0036568 | 0.97286 | -0.19073 | 0.97294 | -0.19011 | 1.3544
38 | 0.0037965 | 0.0009512 | -0.0037959 | -0.00095133 | 6.4851e-07 | -1.3444e-07 | 0.0058021 | 0.0058022 | 0.0058022 | 0.97364 | -0.18508 | 0.97347 | -0.18632 | 2.149

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24742 | 0.062449

## res_load
| p_mw | q_mvar
0 | 0.012178 | 0.0030522
1 | 0.0093193 | 0.0023356
2 | 0.0090274 | 0.0022625
3 | 0.0078949 | 0.0019786
4 | 0.00043373 | 0.0001087
5 | 0.0018304 | 0.00045873
6 | 0.00058074 | 0.00014555
7 | 0.052286 | 0.013104
8 | 0.016462 | 0.0041258
9 | 0.032271 | 0.0080879
10 | 0.0071313 | 0.0017873
11 | 0.024098 | 0.0060396
12 | 0.004553 | 0.0011411
13 | 0.0061696 | 0.0015463
14 | 0.0060598 | 0.0015187
15 | 0.0079161 | 0.001984
16 | 0.0075972 | 0.001904
17 | 0.0048556 | 0.0012169
18 | 0.0035837 | 0.00089817
19 | 0.0029044 | 0.00072792
20 | 0.0032601 | 0.00081705
21 | 0.0024892 | 0.00062385
22 | 0.0027336 | 0.0006851
23 | 0.0023908 | 0.00059918
24 | 0.0037739 | 0.00094583
25 | 0.003769 | 0.0009446
26 | 0.0037959 | 0.00095133
27 | 0.0022176 | 0.00055577

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1