## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2238-2_1_3_node_49 | 0.4 | n |  | TRUE
1 | bus_LV_2238-2_1_3_node_50 | 0.4 | n |  | TRUE
2 | bus_LV_2238-2_1_3_node_51 | 0.4 | n |  | TRUE
3 | bus_LV_2238-2_1_3_node_52 | 0.4 | n |  | TRUE
4 | bus_LV_2238-2_1_3_node_53 | 0.4 | n |  | TRUE
5 | bus_LV_2238-2_1_3_node_54 | 0.4 | n |  | TRUE
6 | bus_LV_2238-2_1_3_node_66 | 0.4 | n |  | TRUE
7 | bus_LV_2238-2_1_3_node_78 | 0.4 | n |  | TRUE
8 | bus_LV_2238-2_1_3_node_60 | 0.4 | n |  | TRUE
9 | bus_LV_2238-2_1_3_node_72 | 0.4 | n |  | TRUE
10 | bus_LV_2238-2_1_3_node_55 | 0.4 | n |  | TRUE
11 | bus_LV_2238-2_1_3_node_56 | 0.4 | n |  | TRUE
12 | bus_LV_2238-2_1_3_node_57 | 0.4 | n |  | TRUE
13 | bus_LV_2238-2_1_3_node_58 | 0.4 | n |  | TRUE
14 | bus_LV_2238-2_1_3_node_59 | 0.4 | n |  | TRUE
15 | bus_LV_2238-2_1_3_node_74 | 0.4 | n |  | TRUE
16 | bus_LV_2238-2_1_3_node_64 | 0.4 | n |  | TRUE
17 | bus_LV_2238-2_1_3_node_61 | 0.4 | n |  | TRUE
18 | bus_LV_2238-2_1_3_node_62 | 0.4 | n |  | TRUE
19 | bus_LV_2238-2_1_3_node_63 | 0.4 | n |  | TRUE
20 | bus_LV_2238-2_1_3_node_65 | 0.4 | n |  | TRUE
21 | bus_LV_2238-2_1_3_node_67 | 0.4 | n |  | TRUE
22 | bus_LV_2238-2_1_3_node_68 | 0.4 | n |  | TRUE
23 | bus_LV_2238-2_1_3_node_69 | 0.4 | n |  | TRUE
24 | bus_LV_2238-2_1_3_node_70 | 0.4 | n |  | TRUE
25 | bus_LV_2238-2_1_3_node_71 | 0.4 | n |  | TRUE
26 | bus_LV_2238-2_1_3_node_73 | 0.4 | n |  | TRUE
27 | bus_LV_2238-2_1_3_node_75 | 0.4 | n |  | TRUE
28 | bus_LV_2238-2_1_3_node_76 | 0.4 | n |  | TRUE
29 | bus_LV_2238-2_1_3_node_83 | 0.4 | n |  | TRUE
30 | bus_LV_2238-2_1_3_node_77 | 0.4 | n |  | TRUE
31 | bus_LV_2238-2_1_3_node_80 | 0.4 | n |  | TRUE
32 | bus_LV_2238-2_1_3_node_81 | 0.4 | n |  | TRUE
33 | bus_LV_2238-2_1_3_node_82 | 0.4 | n |  | TRUE
34 | bus_LV_2238-2_1_3_node_84 | 0.4 | n |  | TRUE
35 | bus_LV_2238-2_1_3_node_89 | 0.4 | n |  | TRUE
36 | bus_LV_2238-2_1_3_node_85 | 0.4 | n |  | TRUE
37 | bus_LV_2238-2_1_3_node_86 | 0.4 | n |  | TRUE
38 | bus_LV_2238-2_1_3_node_87 | 0.4 | n |  | TRUE
39 | bus_LV_2238-2_1_3_node_88 | 0.4 | n |  | TRUE
40 | bus_LV_2238-2_1_3_node_110 | 0.4 | n |  | TRUE
41 | bus_MV_36_2_node_170 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2238-2_1_3_load_49 | 0 | 0.0020557 | 0.0005152 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2238-2_1_3_load_50 | 1 | 0.0014335 | 0.00035928 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2238-2_1_3_load_52 | 3 | 0.0017721 | 0.00044414 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2238-2_1_3_load_53 | 4 | 0.0046746 | 0.0011716 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2238-2_1_3_load_66 | 6 | 0.0010441 | 0.00026168 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2238-2_1_3_load_60 | 8 | 0.0048236 | 0.0012089 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2238-2_1_3_load_72 | 9 | 0.0015078 | 0.00037788 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2238-2_1_3_load_55 | 10 | 0.0056478 | 0.0014155 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2238-2_1_3_load_56 | 11 | 0.0039554 | 0.00099132 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2238-2_1_3_load_59 | 14 | 0.0035715 | 0.0008951 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2238-2_1_3_load_64 | 16 | 0.0056594 | 0.0014184 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2238-2_1_3_load_61 | 17 | 0.0048521 | 0.001216 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2238-2_1_3_load_62 | 18 | 0.011115 | 0.0027856 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2238-2_1_3_load_63 | 19 | 0.0078172 | 0.0019592 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2238-2_1_3_load_65 | 20 | 0.0015448 | 0.00038716 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2238-2_1_3_load_67 | 21 | 0.00039578 | 9.9191e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2238-2_1_3_load_68 | 22 | 0.00026525 | 6.6477e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2238-2_1_3_load_69 | 23 | 0.0004938 | 0.00012376 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2238-2_1_3_load_70 | 24 | 0.00055187 | 0.00013831 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2238-2_1_3_load_73 | 26 | 0.00022233 | 5.5722e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2238-2_1_3_load_75 | 27 | 0.0037127 | 0.0009305 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2238-2_1_3_load_76 | 28 | 0.004983 | 0.0012489 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2238-2_1_3_load_83 | 29 | 0.0025403 | 0.00063665 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2238-2_1_3_load_77 | 30 | 0.002666 | 0.00066817 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2238-2_1_3_load_80 | 31 | 0.0017818 | 0.00044656 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2238-2_1_3_load_81 | 32 | 0.0014126 | 0.00035404 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2238-2_1_3_load_82 | 33 | 0.0025247 | 0.00063276 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2238-2_1_3_load_84 | 34 | 0.0013672 | 0.00034266 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2238-2_1_3_load_85 | 36 | 0.00031732 | 7.9528e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2238-2_1_3_load_87 | 38 | 0.00050608 | 0.00012684 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2238-2_1_3_load_110 | 40 | 0.00067453 | 0.00016905 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2238-2_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.11278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2238-2_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.16362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2238-2_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.13347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2238-2_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.053387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2238-2_1_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.024593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2238-2_1_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.05379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2238-2_1_3_line_6 | NAYY 4x150 SE | 3 | 7 | 0.26938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2238-2_1_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.028798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2238-2_1_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.017367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2238-2_1_3_line_9 | NAYY 4x150 SE | 6 | 20 | 0.022917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2238-2_1_3_line_10 | NAYY 4x150 SE | 7 | 30 | 0.016879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2238-2_1_3_line_11 | NAYY 4x150 SE | 8 | 17 | 0.0033252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2238-2_1_3_line_12 | NAYY 4x150 SE | 9 | 24 | 0.059594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2238-2_1_3_line_13 | NAYY 4x150 SE | 10 | 11 | 0.10334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2238-2_1_3_line_14 | NAYY 4x150 SE | 10 | 12 | 0.025192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2238-2_1_3_line_15 | NAYY 4x150 SE | 11 | 13 | 0.064341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2238-2_1_3_line_16 | NAYY 4x150 SE | 12 | 14 | 0.0099994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2238-2_1_3_line_17 | NAYY 4x150 SE | 13 | 15 | 0.034316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2238-2_1_3_line_18 | NAYY 4x150 SE | 14 | 16 | 0.011674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2238-2_1_3_line_19 | NAYY 4x150 SE | 15 | 27 | 0.025045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2238-2_1_3_line_20 | NAYY 4x150 SE | 16 | 19 | 0.022388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2238-2_1_3_line_21 | NAYY 4x150 SE | 17 | 18 | 0.020092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2238-2_1_3_line_22 | NAYY 4x150 SE | 19 | 20 | 0.03382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2238-2_1_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.0029187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2238-2_1_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.053094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2238-2_1_3_line_25 | NAYY 4x150 SE | 22 | 24 | 0.044892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2238-2_1_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.025615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2238-2_1_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.032574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2238-2_1_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.1307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2238-2_1_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.25249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2238-2_1_3_line_30 | NAYY 4x150 SE | 29 | 32 | 0.028662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2238-2_1_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.0039127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2238-2_1_3_line_32 | NAYY 4x150 SE | 31 | 33 | 0.03023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2238-2_1_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.026208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2238-2_1_3_line_34 | NAYY 4x150 SE | 34 | 35 | 0.089645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2238-2_1_3_line_35 | NAYY 4x150 SE | 35 | 39 | 0.19414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2238-2_1_3_line_36 | NAYY 4x150 SE | 36 | 37 | 0.20518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2238-2_1_3_line_37 | NAYY 4x150 SE | 36 | 38 | 0.00099736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2238-2_1_3_line_38 | NAYY 4x150 SE | 37 | 39 | 0.14734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2238-2_1_3_line_39 | NAYY 4x150 SE | 39 | 40 | 0.0092897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2238-2_1_3_trafo_52 | 0.25 MVA 20/0.4 kV | 41 | 3 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2576625.0898 | 1177724.1343 | 2576535.0535 | 1177656.2197
1 | 2576768.1337 | 1177801.7971 | 2576716.6836 | 1177781.4091 | 2576677.1906 | 1177760.8303 | 2576642.6146 | 1177737.3533 | 2576625.0898 | 1177724.1343
2 | 2576535.0535 | 1177656.2197 | 2576519.6177 | 1177644.5764 | 2576473.1945 | 1177610.8972 | 2576453.4729 | 1177599.4023 | 2576423.4423 | 1177583.5482
3 | 2576768.1337 | 1177801.7971 | 2576779.988 | 1177773.1029 | 2576777.4941 | 1177766.4759 | 2576764.0084 | 1177759.3356
4 | 2576791.5755 | 1177809.4433 | 2576768.1337 | 1177801.7971
5 | 2576371.9103 | 1177568.8151 | 2576374.7476 | 1177569.2419 | 2576395.8028 | 1177573.9389 | 2576418.15 | 1177580.7542 | 2576423.4423 | 1177583.5482
6 | 2576423.4423 | 1177583.5482 | 2576474.9414 | 1177319.1401
7 | 2576738.5579 | 1177745.8604 | 2576764.0084 | 1177759.3356
8 | 2576791.5755 | 1177809.4433 | 2576803.7957 | 1177821.7836
9 | 2576349.2081 | 1177565.7414 | 2576354.9448 | 1177566.2632 | 2576371.9103 | 1177568.8151
10 | 2576474.9414 | 1177319.1401 | 2576486.4998 | 1177320.2174 | 2576491.7038 | 1177319.3822
11 | 2576738.5579 | 1177745.8604 | 2576735.6192 | 1177744.3045
12 | 2576803.7957 | 1177821.7836 | 2576828.6421 | 1177846.8743 | 2576844.1199 | 1177865.5847
13 | 2576246.8084 | 1177554.9458 | 2576238.7764 | 1177553.5174 | 2576210.7765 | 1177547.2478 | 2576162.6961 | 1177539.3464 | 2576145.9984 | 1177533.2766 | 2576145.9984 | 1177533.2766
14 | 2576271.6116 | 1177559.3566 | 2576246.8084 | 1177554.9458
15 | 2576100.4981 | 1177490.3918 | 2576109.9049 | 1177507.6298 | 2576130.7711 | 1177526.1115 | 2576145.9984 | 1177533.2766
16 | 2576271.6116 | 1177559.3566 | 2576281.5545 | 1177560.4183
17 | 2576085.6 | 1177517.7767 | 2576085.201 | 1177509.7297 | 2576088.2152 | 1177499.1344 | 2576091.6846 | 1177495.363 | 2576100.4981 | 1177490.3918
18 | 2576293.1628 | 1177561.6577 | 2576281.5545 | 1177560.4183
19 | 2576085.6 | 1177517.7767 | 2576087.9589 | 1177542.7107
20 | 2576315.5014 | 1177563.0441 | 2576298.4135 | 1177562.2184 | 2576293.1628 | 1177561.6577
21 | 2576717.8624 | 1177734.9028 | 2576735.6192 | 1177744.3045
22 | 2576315.5014 | 1177563.0441 | 2576324.1391 | 1177563.4615 | 2576349.2081 | 1177565.7414
23 | 2576877.9931 | 1177898.9238 | 2576877.4159 | 1177898.5786 | 2576875.6522 | 1177897.1877
24 | 2576877.9931 | 1177898.9238 | 2576894.0581 | 1177908.5305 | 2576897.9473 | 1177908.5155 | 2576901.1912 | 1177905.6348 | 2576913.6313 | 1177882.6353
25 | 2576875.6522 | 1177897.1877 | 2576860.1482 | 1177884.9607 | 2576844.1199 | 1177865.5847
26 | 2576925.8176 | 1177860.105 | 2576913.6313 | 1177882.6353
27 | 2576925.8176 | 1177860.105 | 2576900.0615 | 1177846.6865 | 2576896.7365 | 1177845.4945
28 | 2576186.5692 | 1177587.6428 | 2576184.6206 | 1177593.3757 | 2576178.8472 | 1177594.2325 | 2576094.4341 | 1177573.3033 | 2576090.1481 | 1177565.8499 | 2576087.9589 | 1177542.7107
29 | 2576186.5692 | 1177587.6428 | 2576110.3448 | 1177828.3532
30 | 2576110.3448 | 1177828.3532 | 2576109.0358 | 1177832.8898 | 2576105.3436 | 1177842.0315 | 2576099.2903 | 1177853.0725 | 2576098.5687 | 1177854.3756
31 | 2576096.6733 | 1177857.7985 | 2576098.5687 | 1177854.3756
32 | 2576096.6733 | 1177857.7985 | 2576092.7814 | 1177864.8268 | 2576082.8592 | 1177882.8536 | 2576082.4892 | 1177884.4294
33 | 2576086.9531 | 1177909.5788 | 2576086.7843 | 1177908.9847 | 2576082.3727 | 1177896.8405 | 2576081.1688 | 1177890.053 | 2576082.4892 | 1177884.4294
34 | 2576054.6907 | 1177984.7634 | 2576059.8248 | 1177977.0166 | 2576081.7894 | 1177955.3286 | 2576087.2014 | 1177948.27 | 2576090.9551 | 1177941.1624 | 2576092.7983 | 1177930.1493 | 2576086.9531 | 1177909.5788
35 | 2576054.6907 | 1177984.7634 | 2576087.9577 | 1178020.7488 | 2576101.0292 | 1178035.5819 | 2576105.43 | 1178041.2339 | 2576114.9117 | 1178046.8544 | 2576123.5942 | 1178051.3554 | 2576176.6075 | 1178070.9984 | 2576191.0253 | 1178078.6337 | 2576211.9888 | 1178091.4124
36 | 2576335.9367 | 1178170.7611 | 2576343.791 | 1178168.7846 | 2576385.0238 | 1178127.3668 | 2576391.8013 | 1178123.5714 | 2576399.507 | 1178122.6404 | 2576430.3687 | 1178134.5692 | 2576495.8423 | 1178150.4195 | 2576517.5229 | 1178143.8388
37 | 2576518.4773 | 1178143.5492 | 2576517.5229 | 1178143.8388
38 | 2576211.9888 | 1178091.4124 | 2576280.9131 | 1178135.1498 | 2576320.8101 | 1178159.6264 | 2576331.1117 | 1178165.9444 | 2576335.9367 | 1178170.7611
39 | 2576211.9888 | 1178091.4124 | 2576207.1726 | 1178099.3562

## bus_geodata
| x | y | coords
0 | 2576625.0898 | 1177724.1343
1 | 2576535.0535 | 1177656.2197
2 | 2576768.1337 | 1177801.7971
3 | 2576423.4423 | 1177583.5482
4 | 2576764.0084 | 1177759.3356
5 | 2576791.5755 | 1177809.4433
6 | 2576371.9103 | 1177568.8151
7 | 2576474.9414 | 1177319.1401
8 | 2576738.5579 | 1177745.8604
9 | 2576803.7957 | 1177821.7836
10 | 2576246.8084 | 1177554.9458
11 | 2576145.9984 | 1177533.2766
12 | 2576271.6116 | 1177559.3566
13 | 2576100.4981 | 1177490.3918
14 | 2576281.5545 | 1177560.4183
15 | 2576085.6 | 1177517.7767
16 | 2576293.1628 | 1177561.6577
17 | 2576735.6192 | 1177744.3045
18 | 2576717.8624 | 1177734.9028
19 | 2576315.5014 | 1177563.0441
20 | 2576349.2081 | 1177565.7414
21 | 2576877.9931 | 1177898.9238
22 | 2576875.6522 | 1177897.1877
23 | 2576913.6313 | 1177882.6353
24 | 2576844.1199 | 1177865.5847
25 | 2576925.8176 | 1177860.105
26 | 2576896.7365 | 1177845.4945
27 | 2576087.9589 | 1177542.7107
28 | 2576186.5692 | 1177587.6428
29 | 2576110.3448 | 1177828.3532
30 | 2576491.7038 | 1177319.3822
31 | 2576096.6733 | 1177857.7985
32 | 2576098.5687 | 1177854.3756
33 | 2576082.4892 | 1177884.4294
34 | 2576086.9531 | 1177909.5788
35 | 2576054.6907 | 1177984.7634
36 | 2576517.5229 | 1178143.8388
37 | 2576335.9367 | 1178170.7611
38 | 2576518.4773 | 1178143.5492
39 | 2576211.9888 | 1178091.4124
40 | 2576207.1726 | 1178099.3562
41 | 2576271.6116 | 1177559.3566

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98863 | -0.079043 | 0.0020557 | 0.0005152
1 | 0.99371 | -0.043511 | 0.0014335 | 0.00035928
2 | 0.98175 | -0.12774 | 0 | 0
3 | 1 | 0 | -0.086277 | -0.021572
4 | 0.97977 | -0.14185 | 0.0046746 | 0.0011716
5 | 0.98163 | -0.12862 | 0 | 0
6 | 0.99618 | -0.026514 | 0.0010441 | 0.00026168
7 | 0.99898 | -0.0072148 | 0 | 0
8 | 0.9789 | -0.14808 | 0.0048236 | 0.0012089
9 | 0.98154 | -0.12924 | 0.0015078 | 0.00037788
10 | 0.98899 | -0.076908 | 0.0056478 | 0.0014155
11 | 0.98541 | -0.1022 | 0.0039554 | 0.00099132
12 | 0.99007 | -0.069321 | 0 | 0
13 | 0.98355 | -0.1154 | 0 | 0
14 | 0.9905 | -0.066313 | 0.0035715 | 0.0008951
15 | 0.98256 | -0.12247 | 0 | 0
16 | 0.99106 | -0.062382 | 0.0056594 | 0.0014184
17 | 0.97882 | -0.14863 | 0.0048521 | 0.001216
18 | 0.9785 | -0.15096 | 0.011115 | 0.0027856
19 | 0.99231 | -0.053569 | 0.0078172 | 0.0019592
20 | 0.99459 | -0.03763 | 0.0015448 | 0.00038716
21 | 0.98128 | -0.13113 | 0.00039578 | 9.9191e-05
22 | 0.98128 | -0.13109 | 0.00026525 | 6.6477e-05
23 | 0.98122 | -0.13152 | 0.0004938 | 0.00012376
24 | 0.98137 | -0.13045 | 0.00055187 | 0.00013831
25 | 0.98122 | -0.13158 | 0 | 0
26 | 0.98121 | -0.13166 | 0.00022233 | 5.5722e-05
27 | 0.98183 | -0.12763 | 0.0037127 | 0.0009305
28 | 0.97876 | -0.14963 | 0.004983 | 0.0012489
29 | 0.97465 | -0.17923 | 0.0025403 | 0.00063665
30 | 0.99891 | -0.007665 | 0.002666 | 0.00066817
31 | 0.97425 | -0.18213 | 0.0017818 | 0.00044656
32 | 0.97429 | -0.18183 | 0.0014126 | 0.00035404
33 | 0.97401 | -0.18386 | 0.0025247 | 0.00063276
34 | 0.9739 | -0.18467 | 0.0013672 | 0.00034266
35 | 0.9737 | -0.18614 | 0 | 0
36 | 0.97285 | -0.19241 | 0.00031732 | 7.9528e-05
37 | 0.9731 | -0.1906 | 0 | 0
38 | 0.97285 | -0.19241 | 0.00050608 | 0.00012684
39 | 0.97328 | -0.18929 | 0 | 0
40 | 0.97327 | -0.18935 | 0.00067453 | 0.00016905
41 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.031228 | -0.0078561 | 0.031384 | 0.0079145 | 0.00015554 | 5.8369e-05 | 0.047013 | 0.047012 | 0.047013 | 0.98863 | -0.079043 | 0.99371 | -0.043511 | 17.4121
1 | 0.029172 | 0.0073409 | -0.028976 | -0.0072672 | 0.00019694 | 7.3661e-05 | 0.043919 | 0.043919 | 0.043919 | 0.98863 | -0.079043 | 0.98175 | -0.12774 | 16.2665
2 | -0.032817 | -0.0082737 | 0.033018 | 0.0083494 | 0.00020127 | 7.5671e-05 | 0.049159 | 0.049158 | 0.049159 | 0.99371 | -0.043511 | 1 | 0 | 18.207
3 | 0.025538 | 0.0064087 | -0.025488 | -0.0063902 | 4.9918e-05 | 1.8526e-05 | 0.03871 | 0.03871 | 0.03871 | 0.98175 | -0.12774 | 0.97977 | -0.14185 | 14.337
4 | 0.003438 | 0.00085851 | -0.0034376 | -0.00085866 | 4.1652e-07 | -1.5073e-07 | 0.0052097 | 0.0052098 | 0.0052098 | 0.98175 | -0.12774 | 0.98163 | -0.12862 | 1.9296
5 | 0.04979 | 0.012557 | -0.049605 | -0.012487 | 0.00018438 | 7.0211e-05 | 0.074116 | 0.074116 | 0.074116 | 1 | 0 | 0.99618 | -0.026514 | 27.4503
6 | 0.0026689 | 0.0006655 | -0.0026662 | -0.00066802 | 2.6502e-06 | -2.5111e-06 | 0.0039701 | 0.0039714 | 0.0039714 | 1 | 0 | 0.99898 | -0.0072148 | 1.4709
7 | 0.020813 | 0.0052186 | -0.020795 | -0.0052121 | 1.7956e-05 | 6.5437e-06 | 0.03161 | 0.03161 | 0.03161 | 0.97977 | -0.14185 | 0.9789 | -0.14808 | 11.7076
8 | 0.0034376 | 0.00085866 | -0.0034373 | -0.00085876 | 2.9415e-07 | -1.064e-07 | 0.0052098 | 0.0052099 | 0.0052099 | 0.98163 | -0.12862 | 0.98154 | -0.12924 | 1.9296
9 | 0.048561 | 0.012225 | -0.048486 | -0.012196 | 7.5281e-05 | 2.8656e-05 | 0.072556 | 0.072556 | 0.072556 | 0.99618 | -0.026514 | 0.99459 | -0.03763 | 26.8727
10 | 0.0026662 | 0.00066802 | -0.002666 | -0.00066817 | 1.6612e-07 | -1.5708e-07 | 0.0039714 | 0.0039714 | 0.0039714 | 0.99898 | -0.0072148 | 0.99891 | -0.007665 | 1.4709
11 | 0.015971 | 0.0040032 | -0.01597 | -0.0040027 | 1.223e-06 | 4.2859e-07 | 0.024278 | 0.024278 | 0.024278 | 0.9789 | -0.14808 | 0.97882 | -0.14863 | 8.9919
12 | 0.0019295 | 0.00048088 | -0.0019292 | -0.00048151 | 3.18e-07 | -6.3079e-07 | 0.0029242 | 0.0029244 | 0.0029244 | 0.98154 | -0.12924 | 0.98137 | -0.13045 | 1.0831
13 | 0.024031 | 0.0060402 | -0.023947 | -0.0060091 | 8.4335e-05 | 3.1115e-05 | 0.036163 | 0.036164 | 0.036164 | 0.98899 | -0.076908 | 0.98541 | -0.1022 | 13.394
14 | -0.029679 | -0.0074557 | 0.02971 | 0.0074674 | 3.1355e-05 | 1.1736e-05 | 0.044661 | 0.044661 | 0.044661 | 0.98899 | -0.076908 | 0.99007 | -0.069321 | 16.541
15 | 0.019992 | 0.0050178 | -0.019955 | -0.0050045 | 3.6595e-05 | 1.3257e-05 | 0.030191 | 0.030191 | 0.030191 | 0.98541 | -0.1022 | 0.98355 | -0.1154 | 11.1819
16 | -0.02971 | -0.0074674 | 0.029723 | 0.0074721 | 1.2445e-05 | 4.658e-06 | 0.044661 | 0.044661 | 0.044661 | 0.99007 | -0.069321 | 0.9905 | -0.066313 | 16.541
17 | 0.019955 | 0.0050045 | -0.019935 | -0.0049975 | 1.9518e-05 | 7.072e-06 | 0.030191 | 0.030191 | 0.030191 | 0.98355 | -0.1154 | 0.98256 | -0.12247 | 11.182
18 | -0.033294 | -0.0083672 | 0.033313 | 0.0083741 | 1.8231e-05 | 6.8615e-06 | 0.050026 | 0.050026 | 0.050026 | 0.9905 | -0.066313 | 0.99106 | -0.062382 | 18.5281
19 | 0.019935 | 0.0049975 | -0.019921 | -0.0049923 | 1.4245e-05 | 5.1621e-06 | 0.030191 | 0.030191 | 0.030191 | 0.98256 | -0.12247 | 0.98183 | -0.12763 | 11.182
20 | -0.038972 | -0.0097924 | 0.03902 | 0.0098105 | 4.7848e-05 | 1.8114e-05 | 0.058523 | 0.058523 | 0.058523 | 0.99106 | -0.062382 | 0.99231 | -0.053569 | 21.6753
21 | 0.011118 | 0.0027867 | -0.011115 | -0.0027856 | 3.5817e-06 | 1.1251e-06 | 0.016902 | 0.016902 | 0.016902 | 0.97882 | -0.14863 | 0.9785 | -0.15096 | 6.26
22 | -0.046837 | -0.01177 | 0.046941 | 0.011809 | 0.00010413 | 3.9614e-05 | 0.070245 | 0.070245 | 0.070245 | 0.99231 | -0.053569 | 0.99459 | -0.03763 | 26.0168
23 | -0.0011119 | -0.00027728 | 0.001112 | 0.00027725 | 5.1751e-09 | -3.4881e-08 | 0.0016857 | 0.0016856 | 0.0016857 | 0.98128 | -0.13113 | 0.98128 | -0.13109 | 0.62432
24 | 0.00071617 | 0.00017809 | -0.00071613 | -0.00017875 | 3.9047e-08 | -6.5567e-07 | 0.0010855 | 0.0010857 | 0.0010857 | 0.98128 | -0.13113 | 0.98122 | -0.13152 | 0.40213
25 | -0.0013772 | -0.00034372 | 0.0013773 | 0.0003432 | 1.221e-07 | -5.202e-07 | 0.0020879 | 0.0020877 | 0.0020879 | 0.98128 | -0.13109 | 0.98137 | -0.13045 | 0.77329
26 | 0.00022234 | 5.4988e-05 | -0.00022233 | -5.5311e-05 | 1.8149e-09 | -3.2285e-07 | 0.00033691 | 0.00033702 | 0.00033702 | 0.98122 | -0.13152 | 0.98122 | -0.13158 | 0.12482
27 | 0.00022233 | 5.5311e-05 | -0.00022233 | -5.5722e-05 | 2.3098e-09 | -4.1055e-07 | 0.00033702 | 0.00033717 | 0.00033717 | 0.98122 | -0.13158 | 0.98121 | -0.13166 | 0.12488
28 | 0.016209 | 0.0040618 | -0.016159 | -0.0040445 | 4.9215e-05 | 1.7281e-05 | 0.024565 | 0.024565 | 0.024565 | 0.98183 | -0.12763 | 0.97876 | -0.14963 | 9.0982
29 | 0.011176 | 0.0027957 | -0.011131 | -0.0027813 | 4.548e-05 | 1.4332e-05 | 0.016989 | 0.016991 | 0.016991 | 0.97876 | -0.14963 | 0.97465 | -0.17923 | 6.2928
30 | 0.0085906 | 0.0021447 | -0.0085875 | -0.0021439 | 3.0751e-06 | 8.2565e-07 | 0.013112 | 0.013112 | 0.013112 | 0.97465 | -0.17923 | 0.97429 | -0.18183 | 4.8565
31 | -0.0071746 | -0.0017898 | 0.0071748 | 0.0017898 | 2.9301e-07 | 6.3973e-08 | 0.010955 | 0.010955 | 0.010955 | 0.97425 | -0.18213 | 0.97429 | -0.18183 | 4.0574
32 | 0.0053928 | 0.0013432 | -0.0053915 | -0.0013431 | 1.2788e-06 | 1.1551e-07 | 0.0082336 | 0.0082337 | 0.0082337 | 0.97425 | -0.18213 | 0.97401 | -0.18386 | 3.0495
33 | 0.0028667 | 0.00071033 | -0.0028664 | -0.00071053 | 3.1327e-07 | -2.0567e-07 | 0.0043767 | 0.0043768 | 0.0043768 | 0.97401 | -0.18386 | 0.9739 | -0.18467 | 1.621
34 | 0.0014992 | 0.00036787 | -0.0014989 | -0.00036888 | 2.9284e-07 | -1.0026e-06 | 0.0022878 | 0.0022882 | 0.0022882 | 0.9739 | -0.18467 | 0.9737 | -0.18614 | 0.84749
35 | 0.0014989 | 0.00036888 | -0.0014983 | -0.00037105 | 6.3456e-07 | -2.1697e-06 | 0.0022882 | 0.0022891 | 0.0022891 | 0.9737 | -0.18614 | 0.97328 | -0.18929 | 0.84781
36 | -0.0008234 | -0.00020635 | 0.0008236 | 0.00020388 | 2.0293e-07 | -2.4703e-06 | 0.0012594 | 0.0012585 | 0.0012594 | 0.97285 | -0.19241 | 0.9731 | -0.1906 | 0.46645
37 | 0.00050608 | 0.00012682 | -0.00050608 | -0.00012684 | 3.729e-10 | -1.224e-08 | 0.00077406 | 0.00077407 | 0.00077407 | 0.97285 | -0.19241 | 0.97285 | -0.19241 | 0.28669
38 | -0.0008236 | -0.00020388 | 0.00082375 | 0.00020211 | 1.4554e-07 | -1.7748e-06 | 0.0012585 | 0.0012579 | 0.0012585 | 0.9731 | -0.1906 | 0.97328 | -0.18929 | 0.46611
39 | 0.00067454 | 0.00016894 | -0.00067453 | -0.00016905 | 6.1649e-09 | -1.1308e-07 | 0.0010312 | 0.0010313 | 0.0010313 | 0.97328 | -0.18929 | 0.97327 | -0.18935 | 0.38196

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.088049 | 0.022016

## res_load
| p_mw | q_mvar
0 | 0.0020557 | 0.0005152
1 | 0.0014335 | 0.00035928
2 | 0.0017721 | 0.00044414
3 | 0.0046746 | 0.0011716
4 | 0.0010441 | 0.00026168
5 | 0.0048236 | 0.0012089
6 | 0.0015078 | 0.00037788
7 | 0.0056478 | 0.0014155
8 | 0.0039554 | 0.00099132
9 | 0.0035715 | 0.0008951
10 | 0.0056594 | 0.0014184
11 | 0.0048521 | 0.001216
12 | 0.011115 | 0.0027856
13 | 0.0078172 | 0.0019592
14 | 0.0015448 | 0.00038716
15 | 0.00039578 | 9.9191e-05
16 | 0.00026525 | 6.6477e-05
17 | 0.0004938 | 0.00012376
18 | 0.00055187 | 0.00013831
19 | 0.00022233 | 5.5722e-05
20 | 0.0037127 | 0.0009305
21 | 0.004983 | 0.0012489
22 | 0.0025403 | 0.00063665
23 | 0.002666 | 0.00066817
24 | 0.0017818 | 0.00044656
25 | 0.0014126 | 0.00035404
26 | 0.0025247 | 0.00063276
27 | 0.0013672 | 0.00034266
28 | 0.00031732 | 7.9528e-05
29 | 0.00050608 | 0.00012684
30 | 0.00067453 | 0.00016905

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1