## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2265-20_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2265-20_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2265-20_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2265-20_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2265-20_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2265-20_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2265-20_0_3_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_2265-20_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2265-20_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2265-20_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2265-20_0_3_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_2265-20_0_3_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_2265-20_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2265-20_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2265-20_0_3_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_2265-20_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2265-20_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2265-20_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2265-20_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_2265-20_0_3_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_2265-20_0_3_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_2265-20_0_3_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_2265-20_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2265-20_0_3_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2265-20_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_2265-20_0_3_node_24 | 0.4 | n |  | TRUE
26 | bus_MV_381_0_node_66 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2265-20_0_3_load_0 | 0 | 0.0040398 | 0.0010125 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2265-20_0_3_load_1 | 1 | 0.027776 | 0.0069614 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2265-20_0_3_load_4 | 4 | 0.022224 | 0.0055699 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2265-20_0_3_load_5 | 5 | 0.014877 | 0.0037286 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2265-20_0_3_load_26 | 6 | 0.015857 | 0.0039741 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2265-20_0_3_load_8 | 8 | 0.004245 | 0.0010639 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2265-20_0_3_load_27 | 10 | 0.0069526 | 0.0017425 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2265-20_0_3_load_25 | 11 | 0.0070412 | 0.0017647 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2265-20_0_3_load_9 | 12 | 0.0021776 | 0.00054575 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2265-20_0_3_load_10 | 13 | 0.019472 | 0.0048801 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2265-20_0_3_load_14 | 14 | 0.0032762 | 0.0008211 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2265-20_0_3_load_12 | 15 | 0.0038365 | 0.00096152 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2265-20_0_3_load_11 | 16 | 0.0034498 | 0.00086461 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2265-20_0_3_load_15 | 17 | 0.015965 | 0.0040012 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2265-20_0_3_load_17 | 19 | 0.010759 | 0.0026965 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2265-20_0_3_load_22 | 20 | 0.038365 | 0.0096152 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2265-20_0_3_load_18 | 22 | 0.010317 | 0.0025856 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2265-20_0_3_load_23 | 24 | 0.01115 | 0.0027943 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2265-20_0_3_load_24 | 25 | 0.010922 | 0.0027373 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2265-20_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.011801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2265-20_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.022021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2265-20_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.016762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_2265-20_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.021591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2265-20_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.01705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2265-20_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.015626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_2265-20_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.024013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2265-20_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.033473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2265-20_0_3_line_8 | NAYY 4x150 SE | 6 | 11 | 0.014729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_2265-20_0_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.035901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2265-20_0_3_line_10 | NAYY 4x150 SE | 8 | 12 | 0.008677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2265-20_0_3_line_11 | NAYY 4x150 SE | 9 | 10 | 0.021318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2265-20_0_3_line_12 | NAYY 4x150 SE | 11 | 25 | 0.0139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2265-20_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0039865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2265-20_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.013741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2265-20_0_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.0019387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2265-20_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.026254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2265-20_0_3_line_17 | NAYY 4x150 SE | 17 | 18 | 0.034232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2265-20_0_3_line_18 | NAYY 4x150 SE | 18 | 19 | 0.019978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2265-20_0_3_line_19 | NAYY 4x150 SE | 19 | 20 | 0.027788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2265-20_0_3_line_20 | NAYY 4x150 SE | 20 | 21 | 0.022234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2265-20_0_3_line_21 | NAYY 4x150 SE | 21 | 23 | 0.022979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2265-20_0_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.028852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2265-20_0_3_line_23 | NAYY 4x150 SE | 23 | 24 | 0.011444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2265-20_0_3_line_24 | NAYY 4x150 SE | 24 | 25 | 0.018822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2265-20_0_3_trafo_25 | 0.25 MVA 20/0.4 kV | 26 | 11 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2581895.5043 | 1202564.0713 | 2581883.7621 | 1202562.889
1 | 2581915.7607 | 1202571.6471 | 2581911.3897 | 1202568.0918 | 2581895.5043 | 1202564.0713 | 2581895.5043 | 1202564.0713
2 | 2581867.0643 | 1202562.8796 | 2581876.5358 | 1202562.1614 | 2581883.7621 | 1202562.889
3 | 2581915.7607 | 1202571.6471 | 2581913.2155 | 1202562.939 | 2581911.5175 | 1202550.5359
4 | 2581915.7607 | 1202571.6471 | 2581921.7968 | 1202587.5927
5 | 2581867.0643 | 1202562.8796 | 2581854.9424 | 1202572.7393
6 | 2581908.2581 | 1202526.7455 | 2581910.5928 | 1202543.781 | 2581911.5175 | 1202550.5359
7 | 2581928.9554 | 1202620.1643 | 2581924.8739 | 1202595.7214 | 2581921.7968 | 1202587.5927
8 | 2581854.9424 | 1202572.7393 | 2581843.516 | 1202582.0332
9 | 2581884.6144 | 1202533.8547 | 2581889.2549 | 1202543.4124 | 2581908.2581 | 1202526.7455
10 | 2581930.3846 | 1202628.7228 | 2581928.9554 | 1202620.1643
11 | 2581867.1884 | 1202546.2034 | 2581881.0305 | 1202536.4003 | 2581884.6144 | 1202533.8547
12 | 2581832.7327 | 1202590.8042 | 2581843.516 | 1202582.0332
13 | 2581930.3846 | 1202628.7228 | 2581931.0411 | 1202632.6549
14 | 2581931.0411 | 1202632.6549 | 2581933.3044 | 1202646.2087
15 | 2581933.6237 | 1202648.121 | 2581933.3044 | 1202646.2087
16 | 2581933.6237 | 1202648.121 | 2581937.9479 | 1202674.0168
17 | 2581751.3451 | 1202566.8358 | 2581767.0945 | 1202536.4416
18 | 2581751.3451 | 1202566.8358 | 2581762.7491 | 1202583.2393
19 | 2581762.7491 | 1202583.2393 | 2581778.6112 | 1202606.0553
20 | 2581791.3031 | 1202624.3113 | 2581778.6112 | 1202606.0553
21 | 2581791.3031 | 1202624.3113 | 2581809.2551 | 1202609.904
22 | 2581791.3031 | 1202624.3113 | 2581787.0216 | 1202627.6262 | 2581768.4902 | 1202641.9748
23 | 2581809.2551 | 1202609.904 | 2581811.0616 | 1202608.431 | 2581818.1311 | 1202602.6809
24 | 2581832.7327 | 1202590.8042 | 2581818.1311 | 1202602.6809

## bus_geodata
| x | y | coords
0 | 2581895.5043 | 1202564.0713
1 | 2581883.7621 | 1202562.889
2 | 2581915.7607 | 1202571.6471
3 | 2581867.0643 | 1202562.8796
4 | 2581911.5175 | 1202550.5359
5 | 2581921.7968 | 1202587.5927
6 | 2581854.9424 | 1202572.7393
7 | 2581908.2581 | 1202526.7455
8 | 2581928.9554 | 1202620.1643
9 | 2581884.6144 | 1202533.8547
10 | 2581867.1884 | 1202546.2034
11 | 2581843.516 | 1202582.0332
12 | 2581930.3846 | 1202628.7228
13 | 2581931.0411 | 1202632.6549
14 | 2581933.3044 | 1202646.2087
15 | 2581933.6237 | 1202648.121
16 | 2581937.9479 | 1202674.0168
17 | 2581767.0945 | 1202536.4416
18 | 2581751.3451 | 1202566.8358
19 | 2581762.7491 | 1202583.2393
20 | 2581778.6112 | 1202606.0553
21 | 2581791.3031 | 1202624.3113
22 | 2581768.4902 | 1202641.9748
23 | 2581809.2551 | 1202609.904
24 | 2581818.1311 | 1202602.6809
25 | 2581832.7327 | 1202590.8042
26 | 2581867.0643 | 1202562.8796

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99459 | -0.037747 | 0.0040398 | 0.0010125
1 | 0.99603 | -0.027692 | 0.027776 | 0.0069614
2 | 0.99204 | -0.055685 | 0 | 0
3 | 0.99738 | -0.018232 | 0 | 0
4 | 0.99113 | -0.062081 | 0.022224 | 0.0055699
5 | 0.99078 | -0.064574 | 0.014877 | 0.0037286
6 | 0.99864 | -0.0094365 | 0.015857 | 0.0039741
7 | 0.99089 | -0.06378 | 0 | 0
8 | 0.98902 | -0.077005 | 0.004245 | 0.0010639
9 | 0.99053 | -0.066319 | 0 | 0
10 | 0.99032 | -0.067827 | 0.0069526 | 0.0017425
11 | 1 | 0 | -0.22826 | -0.057242
12 | 0.98862 | -0.079859 | 0.0021776 | 0.00054575
13 | 0.98844 | -0.081082 | 0.019472 | 0.0048801
14 | 0.98823 | -0.082565 | 0.0032762 | 0.0008211
15 | 0.98821 | -0.082709 | 0.0038365 | 0.00096152
16 | 0.98808 | -0.083635 | 0.0034498 | 0.00086461
17 | 0.98756 | -0.087282 | 0.015965 | 0.0040012
18 | 0.98835 | -0.081693 | 0 | 0
19 | 0.98881 | -0.078435 | 0.010759 | 0.0026965
20 | 0.98988 | -0.070861 | 0.038365 | 0.0096152
21 | 0.99197 | -0.056149 | 0 | 0
22 | 0.99154 | -0.05917 | 0.010317 | 0.0025856
23 | 0.99446 | -0.038616 | 0 | 0
24 | 0.99571 | -0.029916 | 0.01115 | 0.0027943
25 | 0.99805 | -0.013552 | 0.010922 | 0.0027373
26 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.084931 | -0.021334 | 0.085049 | 0.021379 | 0.00011893 | 4.5589e-05 | 0.12708 | 0.12708 | 0.12708 | 0.99459 | -0.037747 | 0.99603 | -0.027692 | 47.0674
1 | 0.080891 | 0.020321 | -0.080689 | -0.020244 | 0.00020131 | 7.7141e-05 | 0.12104 | 0.12104 | 0.12104 | 0.99459 | -0.037747 | 0.99204 | -0.055685 | 44.8289
2 | -0.11283 | -0.02834 | 0.11297 | 0.028397 | 0.00014862 | 5.6724e-05 | 0.16858 | 0.16858 | 0.16858 | 0.99603 | -0.027692 | 0.99738 | -0.018232 | 31.2182
3 | 0.029208 | 0.0073232 | -0.029182 | -0.0073135 | 2.5862e-05 | 9.6682e-06 | 0.043812 | 0.043812 | 0.043812 | 0.99204 | -0.055685 | 0.99113 | -0.062081 | 16.2268
4 | 0.051481 | 0.012921 | -0.051418 | -0.012897 | 6.345e-05 | 2.4184e-05 | 0.077226 | 0.077226 | 0.077226 | 0.99204 | -0.055685 | 0.99078 | -0.064574 | 28.6022
5 | -0.11297 | -0.028397 | 0.11311 | 0.02845 | 0.00013854 | 5.2878e-05 | 0.16858 | 0.16858 | 0.16858 | 0.99738 | -0.018232 | 0.99864 | -0.0094365 | 31.2182
6 | 0.0069581 | 0.0017436 | -0.0069565 | -0.0017432 | 1.6351e-06 | 3.1951e-07 | 0.010446 | 0.010446 | 0.010446 | 0.99113 | -0.062081 | 0.99089 | -0.06378 | 3.869
7 | 0.03654 | 0.0091679 | -0.036477 | -0.0091442 | 6.2914e-05 | 2.3767e-05 | 0.054882 | 0.054882 | 0.054882 | 0.99078 | -0.064574 | 0.98902 | -0.077005 | 20.3268
8 | -0.12897 | -0.032424 | 0.12914 | 0.032489 | 0.00016977 | 6.4909e-05 | 0.19221 | 0.19221 | 0.19221 | 0.99864 | -0.0094365 | 1 | 0 | 35.5936
9 | 0.0069565 | 0.0017432 | -0.006954 | -0.0017428 | 2.4448e-06 | 4.78e-07 | 0.010446 | 0.010447 | 0.010447 | 0.99089 | -0.06378 | 0.99053 | -0.066319 | 3.8691
10 | 0.032232 | 0.0080803 | -0.03222 | -0.0080755 | 1.2734e-05 | 4.7863e-06 | 0.048496 | 0.048496 | 0.048496 | 0.98902 | -0.077005 | 0.98862 | -0.079859 | 17.9613
11 | 0.006954 | 0.0017428 | -0.0069526 | -0.0017425 | 1.4517e-06 | 2.8401e-07 | 0.010447 | 0.010447 | 0.010447 | 0.99053 | -0.066319 | 0.99032 | -0.067827 | 3.8691
12 | 0.098323 | 0.024753 | -0.098138 | -0.024682 | 0.00018576 | 7.1265e-05 | 0.14635 | 0.14635 | 0.14635 | 1 | 0 | 0.99805 | -0.013552 | 54.2021
13 | 0.030042 | 0.0075297 | -0.030037 | -0.0075278 | 5.0862e-06 | 1.9051e-06 | 0.045218 | 0.045218 | 0.045218 | 0.98862 | -0.079859 | 0.98844 | -0.081082 | 16.7474
14 | 0.010565 | 0.0026477 | -0.010563 | -0.0026471 | 2.1692e-06 | 6.582e-07 | 0.015905 | 0.015905 | 0.015905 | 0.98844 | -0.081082 | 0.98823 | -0.082565 | 5.8908
15 | 0.0072869 | 0.001826 | -0.0072868 | -0.001826 | 1.4564e-07 | 3.1176e-08 | 0.010972 | 0.010972 | 0.010972 | 0.98823 | -0.082565 | 0.98821 | -0.082709 | 4.0637
16 | 0.0034503 | 0.00086444 | -0.0034498 | -0.00086461 | 4.4218e-07 | -1.6625e-07 | 0.0051952 | 0.0051953 | 0.0051953 | 0.98821 | -0.082709 | 0.98808 | -0.083635 | 1.9242
17 | -0.015965 | -0.0040012 | 0.015978 | 0.0040056 | 1.2361e-05 | 4.3159e-06 | 0.024056 | 0.024055 | 0.024056 | 0.98756 | -0.087282 | 0.98835 | -0.081693 | 8.9095
18 | -0.015978 | -0.0040056 | 0.015985 | 0.0040081 | 7.2138e-06 | 2.5184e-06 | 0.024055 | 0.024055 | 0.024055 | 0.98835 | -0.081693 | 0.98881 | -0.078435 | 8.9094
19 | -0.026744 | -0.0067046 | 0.026772 | 0.006715 | 2.8086e-05 | 1.0446e-05 | 0.040246 | 0.040246 | 0.040246 | 0.98881 | -0.078435 | 0.98988 | -0.070861 | 14.9061
20 | -0.065137 | -0.01633 | 0.06527 | 0.016381 | 0.00013303 | 5.0877e-05 | 0.097918 | 0.097918 | 0.097918 | 0.98988 | -0.070861 | 0.99197 | -0.056149 | 36.2659
21 | -0.075591 | -0.018968 | 0.075776 | 0.019039 | 0.00018439 | 7.0623e-05 | 0.1134 | 0.1134 | 0.1134 | 0.99197 | -0.056149 | 0.99446 | -0.038616 | 42
22 | 0.010321 | 0.0025869 | -0.010317 | -0.0025856 | 4.3154e-06 | 1.2875e-06 | 0.015482 | 0.015482 | 0.015482 | 0.99197 | -0.056149 | 0.99154 | -0.05917 | 5.7342
23 | -0.075776 | -0.019039 | 0.075867 | 0.019074 | 9.1828e-05 | 3.517e-05 | 0.1134 | 0.1134 | 0.1134 | 0.99446 | -0.038616 | 0.99571 | -0.029916 | 42
24 | -0.087017 | -0.021868 | 0.087216 | 0.021944 | 0.00019868 | 7.6169e-05 | 0.13006 | 0.13006 | 0.13006 | 0.99571 | -0.029916 | 0.99805 | -0.013552 | 48.1711

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2353 | 0.059007

## res_load
| p_mw | q_mvar
0 | 0.0040398 | 0.0010125
1 | 0.027776 | 0.0069614
2 | 0.022224 | 0.0055699
3 | 0.014877 | 0.0037286
4 | 0.015857 | 0.0039741
5 | 0.004245 | 0.0010639
6 | 0.0069526 | 0.0017425
7 | 0.0070412 | 0.0017647
8 | 0.0021776 | 0.00054575
9 | 0.019472 | 0.0048801
10 | 0.0032762 | 0.0008211
11 | 0.0038365 | 0.00096152
12 | 0.0034498 | 0.00086461
13 | 0.015965 | 0.0040012
14 | 0.010759 | 0.0026965
15 | 0.038365 | 0.0096152
16 | 0.010317 | 0.0025856
17 | 0.01115 | 0.0027943
18 | 0.010922 | 0.0027373

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1