## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2265-29_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2265-29_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2265-29_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2265-29_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2265-29_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2265-29_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_2265-29_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2265-29_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2265-29_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_2265-29_0_4_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_2265-29_0_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_2265-29_0_4_node_51 | 0.4 | n |  | TRUE
12 | bus_LV_2265-29_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_2265-29_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_2265-29_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2265-29_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2265-29_0_4_node_57 | 0.4 | n |  | TRUE
17 | bus_LV_2265-29_0_4_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_2265-29_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2265-29_0_4_node_60 | 0.4 | n |  | TRUE
20 | bus_LV_2265-29_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_2265-29_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2265-29_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_2265-29_0_4_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_2265-29_0_4_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_2265-29_0_4_node_40 | 0.4 | n |  | TRUE
26 | bus_LV_2265-29_0_4_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_2265-29_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_2265-29_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_2265-29_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2265-29_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_2265-29_0_4_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_2265-29_0_4_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_2265-29_0_4_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_2265-29_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_2265-29_0_4_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_2265-29_0_4_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_2265-29_0_4_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_2265-29_0_4_node_47 | 0.4 | n |  | TRUE
39 | bus_LV_2265-29_0_4_node_48 | 0.4 | n |  | TRUE
40 | bus_LV_2265-29_0_4_node_49 | 0.4 | n |  | TRUE
41 | bus_LV_2265-29_0_4_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_2265-29_0_4_node_56 | 0.4 | n |  | TRUE
43 | bus_LV_2265-29_0_4_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_2265-29_0_4_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_2265-29_0_4_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_2265-29_0_4_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_2265-29_0_4_node_52 | 0.4 | n |  | TRUE
48 | bus_LV_2265-29_0_4_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_2265-29_0_4_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_2265-29_0_4_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_2265-29_0_4_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_2265-29_0_4_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_2265-29_0_4_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_2265-29_0_4_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_2265-29_0_4_node_54 | 0.4 | n |  | TRUE
56 | bus_LV_2265-29_0_4_node_55 | 0.4 | n |  | TRUE
57 | bus_LV_2265-29_0_4_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_2265-29_0_4_node_61 | 0.4 | n |  | TRUE
59 | bus_LV_2265-29_0_4_node_59 | 0.4 | n |  | TRUE
60 | bus_MV_381_0_node_87 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2265-29_0_4_load_0 | 0 | 0.0032876 | 0.00082394 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2265-29_0_4_load_1 | 1 | 0.0012994 | 0.00032567 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2265-29_0_4_load_3 | 3 | 0.0025331 | 0.00063486 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2265-29_0_4_load_4 | 4 | 0.0032611 | 0.00081732 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2265-29_0_4_load_11 | 5 | 0.0035043 | 0.00087827 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2265-29_0_4_load_7 | 6 | 0.0049646 | 0.0012442 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2265-29_0_4_load_13 | 8 | 0.010951 | 0.0027446 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2265-29_0_4_load_50 | 9 | 0.0065664 | 0.0016457 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2265-29_0_4_load_12 | 10 | 0.0031965 | 0.00080113 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2265-29_0_4_load_51 | 11 | 0.0015897 | 0.00039842 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2265-29_0_4_load_5 | 12 | 0.015239 | 0.0038193 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2265-29_0_4_load_10 | 15 | 0.0018748 | 0.00046986 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2265-29_0_4_load_57 | 16 | 0.0027953 | 0.00070058 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2265-29_0_4_load_14 | 18 | 0.020143 | 0.0050484 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2265-29_0_4_load_60 | 19 | 0.0031189 | 0.00078167 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2265-29_0_4_load_17 | 21 | 0.044231 | 0.011085 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2265-29_0_4_load_16 | 22 | 0.011317 | 0.0028364 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2265-29_0_4_load_32 | 23 | 0.0008148 | 0.00020421 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2265-29_0_4_load_30 | 24 | 0.00090253 | 0.0002262 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2265-29_0_4_load_40 | 25 | 0.00097272 | 0.00024379 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2265-29_0_4_load_31 | 26 | 0.001191 | 0.0002985 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2265-29_0_4_load_21 | 27 | 0.0010782 | 0.00027021 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2265-29_0_4_load_22 | 28 | 0.0023156 | 0.00058034 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2265-29_0_4_load_24 | 30 | 0.0033695 | 0.00084448 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2265-29_0_4_load_25 | 31 | 0.002766 | 0.00069323 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2265-29_0_4_load_26 | 32 | 0.0012611 | 0.00031606 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2265-29_0_4_load_27 | 33 | 0.0044378 | 0.0011122 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2265-29_0_4_load_28 | 34 | 0.0028986 | 0.00072645 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2265-29_0_4_load_39 | 36 | 0.002236 | 0.0005604 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2265-29_0_4_load_29 | 37 | 0.0025108 | 0.00062926 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2265-29_0_4_load_47 | 38 | 0.0031967 | 0.00080118 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2265-29_0_4_load_48 | 39 | 0.0015029 | 0.00037666 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2265-29_0_4_load_49 | 40 | 0.00076186 | 0.00019094 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2265-29_0_4_load_37 | 41 | 0.0019364 | 0.00048531 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2265-29_0_4_load_56 | 42 | 0.0060345 | 0.0015124 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2265-29_0_4_load_38 | 43 | 0.00093553 | 0.00023447 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2265-29_0_4_load_33 | 44 | 0.0015639 | 0.00039194 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2265-29_0_4_load_34 | 45 | 0.0037194 | 0.00093218 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2265-29_0_4_load_35 | 46 | 0.0033194 | 0.00083193 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2265-29_0_4_load_53 | 48 | 0.00090946 | 0.00022793 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2265-29_0_4_load_36 | 49 | 0.00093608 | 0.0002346 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2265-29_0_4_load_41 | 50 | 0.0052621 | 0.0013188 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2265-29_0_4_load_42 | 51 | 0.0011968 | 0.00029995 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2265-29_0_4_load_43 | 52 | 0.0028363 | 0.00071083 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2265-29_0_4_load_44 | 53 | 0.0021301 | 0.00053386 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2265-29_0_4_load_45 | 54 | 0.0045416 | 0.0011382 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2265-29_0_4_load_54 | 55 | 0.0051363 | 0.0012873 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2265-29_0_4_load_55 | 56 | 0.0043504 | 0.0010903 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2265-29_0_4_load_58 | 57 | 0.004112 | 0.0010306 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2265-29_0_4_load_61 | 58 | 0.0037768 | 0.00094655 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2265-29_0_4_load_59 | 59 | 0.002758 | 0.00069121 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2265-29_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.020089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2265-29_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.036835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2265-29_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.018763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2265-29_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.034435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2265-29_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.020694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2265-29_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.059531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2265-29_0_4_line_6 | NAYY 4x150 SE | 4 | 9 | 0.021314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_2265-29_0_4_line_7 | NAYY 4x150 SE | 5 | 10 | 0.0096254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2265-29_0_4_line_8 | NAYY 4x150 SE | 6 | 7 | 0.035179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2265-29_0_4_line_9 | NAYY 4x150 SE | 7 | 8 | 0.11532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2265-29_0_4_line_10 | NAYY 4x150 SE | 8 | 18 | 0.029262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2265-29_0_4_line_11 | NAYY 4x150 SE | 9 | 11 | 0.010953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_2265-29_0_4_line_12 | NAYY 4x150 SE | 11 | 56 | 0.0011969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_2265-29_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.009722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2265-29_0_4_line_14 | NAYY 4x150 SE | 13 | 14 | 0.046672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_2265-29_0_4_line_15 | NAYY 4x150 SE | 13 | 15 | 0.001763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_2265-29_0_4_line_16 | NAYY 4x150 SE | 14 | 16 | 0.033527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_2265-29_0_4_line_17 | NAYY 4x150 SE | 15 | 17 | 0.044381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_2265-29_0_4_line_18 | NAYY 4x150 SE | 16 | 19 | 0.017373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_2265-29_0_4_line_19 | NAYY 4x150 SE | 17 | 20 | 0.005535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2265-29_0_4_line_20 | NAYY 4x150 SE | 17 | 21 | 0.012374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2265-29_0_4_line_21 | NAYY 4x150 SE | 19 | 59 | 0.0043084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_2265-29_0_4_line_22 | NAYY 4x150 SE | 20 | 23 | 0.01465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2265-29_0_4_line_23 | NAYY 4x150 SE | 20 | 24 | 0.037343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2265-29_0_4_line_24 | NAYY 4x150 SE | 21 | 22 | 0.080471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2265-29_0_4_line_25 | NAYY 4x150 SE | 23 | 25 | 0.01786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2265-29_0_4_line_26 | NAYY 4x150 SE | 24 | 26 | 0.0041982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2265-29_0_4_line_27 | NAYY 4x150 SE | 25 | 43 | 0.0176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2265-29_0_4_line_28 | NAYY 4x150 SE | 27 | 28 | 0.0013951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2265-29_0_4_line_29 | NAYY 4x150 SE | 27 | 29 | 0.017121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2265-29_0_4_line_30 | NAYY 4x150 SE | 28 | 30 | 0.010169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2265-29_0_4_line_31 | NAYY 4x150 SE | 29 | 31 | 0.014565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2265-29_0_4_line_32 | NAYY 4x150 SE | 29 | 32 | 0.041114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2265-29_0_4_line_33 | NAYY 4x150 SE | 29 | 33 | 0.019706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2265-29_0_4_line_34 | NAYY 4x150 SE | 31 | 34 | 0.025483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2265-29_0_4_line_35 | NAYY 4x150 SE | 32 | 35 | 0.02068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2265-29_0_4_line_36 | NAYY 4x150 SE | 33 | 36 | 0.014459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2265-29_0_4_line_37 | NAYY 4x150 SE | 34 | 37 | 0.0025429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2265-29_0_4_line_38 | NAYY 4x150 SE | 35 | 38 | 0.026178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2265-29_0_4_line_39 | NAYY 4x150 SE | 35 | 39 | 0.011317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2265-29_0_4_line_40 | NAYY 4x150 SE | 35 | 40 | 0.014976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2265-29_0_4_line_41 | NAYY 4x150 SE | 36 | 41 | 0.020382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2265-29_0_4_line_42 | NAYY 4x150 SE | 37 | 42 | 0.005438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2265-29_0_4_line_43 | NAYY 4x150 SE | 39 | 47 | 0.027016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2265-29_0_4_line_44 | NAYY 4x150 SE | 40 | 58 | 0.0071622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2265-29_0_4_line_45 | NAYY 4x150 SE | 41 | 49 | 0.018223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2265-29_0_4_line_46 | NAYY 4x150 SE | 43 | 49 | 0.0058505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2265-29_0_4_line_47 | NAYY 4x150 SE | 44 | 45 | 0.081573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2265-29_0_4_line_48 | NAYY 4x150 SE | 45 | 46 | 0.024101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2265-29_0_4_line_49 | NAYY 4x150 SE | 46 | 47 | 0.060642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2265-29_0_4_line_50 | NAYY 4x150 SE | 47 | 48 | 0.017151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2265-29_0_4_line_51 | NAYY 4x150 SE | 50 | 51 | 0.030238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_2265-29_0_4_line_52 | NAYY 4x150 SE | 50 | 52 | 0.012631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_2265-29_0_4_line_53 | NAYY 4x150 SE | 51 | 53 | 0.0061963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_2265-29_0_4_line_54 | NAYY 4x150 SE | 52 | 54 | 0.011117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_2265-29_0_4_line_55 | NAYY 4x150 SE | 53 | 55 | 0.03319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_2265-29_0_4_line_56 | NAYY 4x150 SE | 54 | 56 | 0.017283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_2265-29_0_4_line_57 | NAYY 4x150 SE | 55 | 57 | 0.0068498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_2265-29_0_4_line_58 | NAYY 4x150 SE | 57 | 59 | 0.018241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2265-29_0_4_trafo_57 | 0.25 MVA 20/0.4 kV | 60 | 16 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2582063.0956 | 1203009.1268 | 2582078.2782 | 1203014.3854 | 2582082.0532 | 1203015.7725
1 | 2582028.2892 | 1202997.0713 | 2582063.0956 | 1203009.1268
2 | 2582082.0532 | 1203015.7725 | 2582099.665 | 1203022.2438
3 | 2582028.2892 | 1202997.0713 | 2582033.5571 | 1203031.1013
4 | 2582119.0893 | 1203029.3811 | 2582099.665 | 1203022.2438
5 | 2582099.665 | 1203022.2438 | 2582121.3399 | 1202966.7992
6 | 2582033.5571 | 1203031.1013 | 2582036.8178 | 1203052.1648
7 | 2582119.0893 | 1203029.3811 | 2582128.1241 | 1203032.7009
8 | 2582106.6934 | 1202934.8231 | 2582118.5673 | 1202961.4241 | 2582121.3399 | 1202966.7992
9 | 2582106.6934 | 1202934.8231 | 2582217.1682 | 1202901.7406
10 | 2582217.1682 | 1202901.7406 | 2582225.4999 | 1202912.1654 | 2582236.4755 | 1202923.6928
11 | 2582036.8178 | 1203052.1648 | 2582038.4934 | 1203062.9892
12 | 2582038.4934 | 1203062.9892 | 2582038.6765 | 1203064.1721
13 | 2582208.3861 | 1203094.694 | 2582207.5659 | 1203085.0467 | 2582207.5391 | 1203085.0171
14 | 2582208.3861 | 1203094.694 | 2582174.1351 | 1203062.8904
15 | 2582208.3861 | 1203094.694 | 2582209.6795 | 1203095.8919
16 | 2582174.1351 | 1203062.8904 | 2582143.2728 | 1203075.9887
17 | 2582241.4127 | 1203126.8239 | 2582236.3953 | 1203120.6355 | 2582209.6795 | 1203095.8919
18 | 2582143.2728 | 1203075.9887 | 2582142.0823 | 1203076.494 | 2582128.6982 | 1203085.4065
19 | 2582244.9027 | 1203131.1269 | 2582241.4127 | 1203126.8239
20 | 2582241.4127 | 1203126.8239 | 2582253.0183 | 1203122.5313
21 | 2582125.1121 | 1203087.7944 | 2582128.6982 | 1203085.4065
22 | 2582244.9027 | 1203131.1269 | 2582231.7871 | 1203137.6531
23 | 2582244.9027 | 1203131.1269 | 2582267.2345 | 1203161.0572
24 | 2582302.9247 | 1203087.059 | 2582294.0452 | 1203125.3883 | 2582253.0183 | 1203122.5313 | 2582253.0183 | 1203122.5313
25 | 2582215.797 | 1203145.6097 | 2582231.7871 | 1203137.6531
26 | 2582267.2345 | 1203161.0572 | 2582269.745 | 1203164.422
27 | 2582215.797 | 1203145.6097 | 2582200.0398 | 1203153.4504
28 | 2582137.4228 | 1203203.673 | 2582136.79 | 1203202.4297
29 | 2582129.0238 | 1203187.1714 | 2582136.79 | 1203202.4297
30 | 2582142.0353 | 1203212.7352 | 2582137.4228 | 1203203.673
31 | 2582129.0238 | 1203187.1714 | 2582122.5307 | 1203174.1335
32 | 2582129.0238 | 1203187.1714 | 2582092.2217 | 1203205.5009
33 | 2582129.0238 | 1203187.1714 | 2582146.8736 | 1203178.8232
34 | 2582122.5307 | 1203174.1335 | 2582111.1709 | 1203151.3231
35 | 2582073.9382 | 1203215.1415 | 2582080.0675 | 1203211.5544 | 2582092.2217 | 1203205.5009
36 | 2582146.8736 | 1203178.8232 | 2582159.9705 | 1203172.6979
37 | 2582111.1709 | 1203151.3231 | 2582110.0373 | 1203149.0468
38 | 2582073.9382 | 1203215.1415 | 2582062.8038 | 1203191.4399
39 | 2582073.9382 | 1203215.1415 | 2582063.841 | 1203220.2527
40 | 2582073.9382 | 1203215.1415 | 2582080.7519 | 1203228.4773
41 | 2582159.9705 | 1203172.6979 | 2582178.4329 | 1203164.0632
42 | 2582107.6131 | 1203144.179 | 2582110.0373 | 1203149.0468
43 | 2582039.7368 | 1203232.4542 | 2582063.841 | 1203220.2527
44 | 2582084.0105 | 1203234.8552 | 2582080.7519 | 1203228.4773
45 | 2582194.8019 | 1203156.0567 | 2582183.068 | 1203161.8954 | 2582178.4329 | 1203164.0632
46 | 2582194.8019 | 1203156.0567 | 2582200.0398 | 1203153.4504
47 | 2581965.142 | 1203083.8818 | 2581967.5403 | 1203089.8949 | 2581978.7557 | 1203110.0163 | 2581999.6841 | 1203151.6756 | 2582001.9741 | 1203156.6134
48 | 2582012.114 | 1203178.4778 | 2582001.9741 | 1203156.6134
49 | 2582039.7368 | 1203232.4542 | 2582015.9741 | 1203186.8011 | 2582012.114 | 1203178.4778
50 | 2582039.7368 | 1203232.4542 | 2582048.1022 | 1203247.4268
51 | 2582046.3665 | 1203104.2383 | 2582050.6181 | 1203111.9444 | 2582061.9765 | 1203119.0473 | 2582069.9728 | 1203119.8911
52 | 2582046.3665 | 1203104.2383 | 2582044.2987 | 1203100.4905 | 2582043.0212 | 1203092.2377
53 | 2582069.9728 | 1203119.8911 | 2582071.3991 | 1203120.0416 | 2582075.8154 | 1203118.2603
54 | 2582041.3206 | 1203081.252 | 2582043.0212 | 1203092.2377
55 | 2582104.2282 | 1203101.701 | 2582099.7864 | 1203104.6588 | 2582089.8658 | 1203112.593 | 2582075.8154 | 1203118.2603
56 | 2582041.3206 | 1203081.252 | 2582038.6765 | 1203064.1721
57 | 2582104.2282 | 1203101.701 | 2582109.9296 | 1203097.9044
58 | 2582109.9296 | 1203097.9044 | 2582125.1121 | 1203087.7944

## bus_geodata
| x | y | coords
0 | 2582063.0956 | 1203009.1268
1 | 2582082.0532 | 1203015.7725
2 | 2582028.2892 | 1202997.0713
3 | 2582099.665 | 1203022.2438
4 | 2582033.5571 | 1203031.1013
5 | 2582119.0893 | 1203029.3811
6 | 2582121.3399 | 1202966.7992
7 | 2582106.6934 | 1202934.8231
8 | 2582217.1682 | 1202901.7406
9 | 2582036.8178 | 1203052.1648
10 | 2582128.1241 | 1203032.7009
11 | 2582038.4934 | 1203062.9892
12 | 2582207.5391 | 1203085.0171
13 | 2582208.3861 | 1203094.694
14 | 2582174.1351 | 1203062.8904
15 | 2582209.6795 | 1203095.8919
16 | 2582143.2728 | 1203075.9887
17 | 2582241.4127 | 1203126.8239
18 | 2582236.4755 | 1202923.6928
19 | 2582128.6982 | 1203085.4065
20 | 2582244.9027 | 1203131.1269
21 | 2582253.0183 | 1203122.5313
22 | 2582302.9247 | 1203087.059
23 | 2582231.7871 | 1203137.6531
24 | 2582267.2345 | 1203161.0572
25 | 2582215.797 | 1203145.6097
26 | 2582269.745 | 1203164.422
27 | 2582136.79 | 1203202.4297
28 | 2582137.4228 | 1203203.673
29 | 2582129.0238 | 1203187.1714
30 | 2582142.0353 | 1203212.7352
31 | 2582122.5307 | 1203174.1335
32 | 2582092.2216 | 1203205.5009
33 | 2582146.8736 | 1203178.8232
34 | 2582111.1709 | 1203151.3231
35 | 2582073.9382 | 1203215.1415
36 | 2582159.9705 | 1203172.6979
37 | 2582110.0373 | 1203149.0468
38 | 2582062.8038 | 1203191.4399
39 | 2582063.841 | 1203220.2527
40 | 2582080.7519 | 1203228.4773
41 | 2582178.4329 | 1203164.0632
42 | 2582107.6131 | 1203144.179
43 | 2582200.0398 | 1203153.4504
44 | 2581965.142 | 1203083.8818
45 | 2582001.9741 | 1203156.6134
46 | 2582012.114 | 1203178.4778
47 | 2582039.7368 | 1203232.4542
48 | 2582048.1022 | 1203247.4268
49 | 2582194.8019 | 1203156.0567
50 | 2582046.3665 | 1203104.2383
51 | 2582069.9728 | 1203119.8911
52 | 2582043.0212 | 1203092.2377
53 | 2582075.8154 | 1203118.2603
54 | 2582041.3206 | 1203081.252
55 | 2582104.2282 | 1203101.701
56 | 2582038.6765 | 1203064.1721
57 | 2582109.9296 | 1203097.9044
58 | 2582084.0105 | 1203234.8552
59 | 2582125.1121 | 1203087.7944
60 | 2582143.2728 | 1203075.9887

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98419 | -0.11016 | 0.0032876 | 0.00082394
1 | 0.98282 | -0.11982 | 0.0012994 | 0.00032567
2 | 0.98688 | -0.091266 | 0 | 0
3 | 0.98157 | -0.12862 | 0.0025331 | 0.00063486
4 | 0.98939 | -0.073697 | 0.0032611 | 0.00081732
5 | 0.98137 | -0.13005 | 0.0035043 | 0.00087827
6 | 0.97843 | -0.15094 | 0.0049646 | 0.0012442
7 | 0.97682 | -0.16236 | 0 | 0
8 | 0.97156 | -0.20008 | 0.010951 | 0.0027446
9 | 0.99021 | -0.067923 | 0.0065664 | 0.0016457
10 | 0.98133 | -0.13037 | 0.0031965 | 0.00080113
11 | 0.99069 | -0.064594 | 0.0015897 | 0.00039842
12 | 0.99236 | -0.053148 | 0.015239 | 0.0038193
13 | 0.99257 | -0.051646 | 0 | 0
14 | 0.99689 | -0.021498 | 0 | 0
15 | 0.99242 | -0.052654 | 0.0018748 | 0.00046986
16 | 1 | 0 | -0.22904 | -0.057647
17 | 0.98886 | -0.077696 | 0 | 0
18 | 0.97069 | -0.20632 | 0.020143 | 0.0050484
19 | 0.99878 | -0.0084033 | 0.0031189 | 0.00078167
20 | 0.98841 | -0.080827 | 0 | 0
21 | 0.98787 | -0.084719 | 0.044231 | 0.011085
22 | 0.98655 | -0.094048 | 0.011317 | 0.0028364
23 | 0.98728 | -0.088813 | 0.0008148 | 0.00020421
24 | 0.9883 | -0.081626 | 0.00090253 | 0.0002262
25 | 0.98591 | -0.098425 | 0.00097272 | 0.00024379
26 | 0.98829 | -0.081678 | 0.001191 | 0.0002985
27 | 0.97913 | -0.14661 | 0.0010782 | 0.00027021
28 | 0.97912 | -0.1467 | 0.0023156 | 0.00058034
29 | 0.9793 | -0.14541 | 0 | 0
30 | 0.97907 | -0.14705 | 0.0033695 | 0.00084448
31 | 0.97899 | -0.14756 | 0.002766 | 0.00069323
32 | 0.97809 | -0.15399 | 0.0012611 | 0.00031606
33 | 0.98047 | -0.137 | 0.0044378 | 0.0011122
34 | 0.97857 | -0.1506 | 0.0028986 | 0.00072645
35 | 0.97753 | -0.15805 | 0 | 0
36 | 0.98143 | -0.13019 | 0.002236 | 0.0005604
37 | 0.97854 | -0.15083 | 0.0025108 | 0.00062926
38 | 0.97741 | -0.15892 | 0.0031967 | 0.00080118
39 | 0.97735 | -0.15935 | 0.0015029 | 0.00037666
40 | 0.97743 | -0.15876 | 0.00076186 | 0.00019094
41 | 0.98284 | -0.12013 | 0.0019364 | 0.00048531
42 | 0.97849 | -0.15117 | 0.0060345 | 0.0015124
43 | 0.98459 | -0.10775 | 0.00093553 | 0.00023447
44 | 0.97584 | -0.17018 | 0.0015639 | 0.00039194
45 | 0.97602 | -0.16884 | 0.0037194 | 0.00093218
46 | 0.97621 | -0.16751 | 0.0033194 | 0.00083193
47 | 0.97697 | -0.16204 | 0 | 0
48 | 0.97695 | -0.1622 | 0.00090946 | 0.00022793
49 | 0.98416 | -0.11079 | 0.00093608 | 0.0002346
50 | 0.99281 | -0.049817 | 0.0052621 | 0.0013188
51 | 0.99453 | -0.037845 | 0.0011968 | 0.00029995
52 | 0.99214 | -0.054493 | 0.0028363 | 0.00071083
53 | 0.99489 | -0.035359 | 0.0021301 | 0.00053386
54 | 0.99157 | -0.058454 | 0.0045416 | 0.0011382
55 | 0.99686 | -0.02172 | 0.0051363 | 0.0012873
56 | 0.99074 | -0.064221 | 0.0043504 | 0.0010903
57 | 0.99729 | -0.018735 | 0.004112 | 0.0010306
58 | 0.97739 | -0.15904 | 0.0037768 | 0.00094655
59 | 0.99849 | -0.010423 | 0.002758 | 0.00069121
60 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.047057 | 0.011852 | -0.046994 | -0.011828 | 6.3492e-05 | 2.4165e-05 | 0.071168 | 0.071168 | 0.071168 | 0.98419 | -0.11016 | 0.98282 | -0.11982 | 26.3585
1 | -0.050345 | -0.012676 | 0.050478 | 0.012727 | 0.00013325 | 5.0779e-05 | 0.076138 | 0.076138 | 0.076138 | 0.98419 | -0.11016 | 0.98688 | -0.091266 | 28.1994
2 | 0.045694 | 0.011502 | -0.045638 | -0.011481 | 5.6067e-05 | 2.1327e-05 | 0.069201 | 0.069201 | 0.069201 | 0.98282 | -0.11982 | 0.98157 | -0.12862 | 25.6299
3 | -0.050478 | -0.012727 | 0.050603 | 0.012774 | 0.00012456 | 4.7468e-05 | 0.076138 | 0.076138 | 0.076138 | 0.98688 | -0.091266 | 0.98939 | -0.073697 | 28.1994
4 | 0.0067024 | 0.0016796 | -0.006701 | -0.0016793 | 1.3331e-06 | 2.5119e-07 | 0.01016 | 0.01016 | 0.01016 | 0.98157 | -0.12862 | 0.98137 | -0.13005 | 3.7631
5 | 0.036403 | 0.0091665 | -0.03629 | -0.0091237 | 0.00011319 | 4.2785e-05 | 0.0552 | 0.055201 | 0.055201 | 0.98157 | -0.12862 | 0.97843 | -0.15094 | 20.4446
6 | -0.053864 | -0.013592 | 0.053908 | 0.013608 | 4.3677e-05 | 1.6251e-05 | 0.081043 | 0.081043 | 0.081043 | 0.98939 | -0.073697 | 0.99021 | -0.067923 | 15.0079
7 | 0.0031967 | 0.00080106 | -0.0031965 | -0.00080113 | 1.4111e-07 | -6.7341e-08 | 0.004847 | 0.004847 | 0.004847 | 0.98137 | -0.13005 | 0.98133 | -0.13037 | 1.7952
8 | 0.031325 | 0.0078795 | -0.031275 | -0.0078607 | 4.9842e-05 | 1.8729e-05 | 0.04765 | 0.04765 | 0.04765 | 0.97843 | -0.15094 | 0.97682 | -0.16236 | 17.6483
9 | 0.031275 | 0.0078607 | -0.031112 | -0.0077993 | 0.00016339 | 6.1408e-05 | 0.04765 | 0.047651 | 0.047651 | 0.97682 | -0.16236 | 0.97156 | -0.20008 | 17.6485
10 | 0.020161 | 0.0050547 | -0.020143 | -0.0050484 | 1.741e-05 | 6.3342e-06 | 0.030878 | 0.030879 | 0.030879 | 0.97156 | -0.20008 | 0.97069 | -0.20632 | 11.4365
11 | -0.060474 | -0.015254 | 0.060502 | 0.015264 | 2.8244e-05 | 1.0581e-05 | 0.09091 | 0.09091 | 0.09091 | 0.99021 | -0.067923 | 0.99069 | -0.064594 | 16.8352
12 | -0.062092 | -0.015663 | 0.062095 | 0.015664 | 3.2506e-06 | 1.2194e-06 | 0.093298 | 0.093298 | 0.093298 | 0.99069 | -0.064594 | 0.99074 | -0.064221 | 17.2774
13 | -0.015239 | -0.0038193 | 0.015242 | 0.0038204 | 3.1678e-06 | 1.0927e-06 | 0.022851 | 0.022851 | 0.022851 | 0.99236 | -0.053148 | 0.99257 | -0.051646 | 8.4633
14 | -0.12901 | -0.032459 | 0.12956 | 0.032667 | 0.00054497 | 0.00020839 | 0.19346 | 0.19346 | 0.19346 | 0.99257 | -0.051646 | 0.99689 | -0.021498 | 35.8251
15 | 0.11377 | 0.028638 | -0.11376 | -0.028632 | 1.601e-05 | 6.1119e-06 | 0.1706 | 0.1706 | 0.1706 | 0.99257 | -0.051646 | 0.99242 | -0.052654 | 31.5935
16 | -0.12956 | -0.032667 | 0.12995 | 0.032817 | 0.00039148 | 0.00014969 | 0.19346 | 0.19345 | 0.19346 | 0.99689 | -0.021498 | 1 | 0 | 35.8251
17 | 0.11188 | 0.028162 | -0.11149 | -0.028013 | 0.00038985 | 0.0001488 | 0.16779 | 0.16779 | 0.16779 | 0.99242 | -0.052654 | 0.98886 | -0.077696 | 31.073
18 | 0.098287 | 0.024831 | -0.098171 | -0.024786 | 0.00011605 | 4.418e-05 | 0.14632 | 0.14632 | 0.14632 | 1 | 0 | 0.99878 | -0.0084033 | 27.0967
19 | 0.055874 | 0.014066 | -0.055849 | -0.014057 | 2.4429e-05 | 9.3247e-06 | 0.084101 | 0.084101 | 0.084101 | 0.98886 | -0.077696 | 0.98841 | -0.080827 | 31.1484
20 | 0.055617 | 0.013947 | -0.055562 | -0.013926 | 5.4086e-05 | 2.0644e-05 | 0.083694 | 0.083694 | 0.083694 | 0.98886 | -0.077696 | 0.98787 | -0.084719 | 30.9977
21 | 0.095052 | 0.024005 | -0.095025 | -0.023994 | 2.6981e-05 | 1.0265e-05 | 0.14168 | 0.14168 | 0.14168 | 0.99878 | -0.0084033 | 0.99849 | -0.010423 | 26.2362
22 | 0.053756 | 0.013533 | -0.053696 | -0.01351 | 5.99e-05 | 2.2851e-05 | 0.080949 | 0.080949 | 0.080949 | 0.98841 | -0.080827 | 0.98728 | -0.088813 | 29.981
23 | 0.0020938 | 0.00052426 | -0.0020936 | -0.00052465 | 2.3152e-07 | -3.8953e-07 | 0.003152 | 0.0031522 | 0.0031522 | 0.98841 | -0.080827 | 0.9883 | -0.081626 | 1.1675
24 | 0.011332 | 0.002841 | -0.011317 | -0.0028364 | 1.4631e-05 | 4.5984e-06 | 0.017069 | 0.01707 | 0.01707 | 0.98787 | -0.084719 | 0.98655 | -0.094048 | 6.3222
25 | 0.052881 | 0.013306 | -0.05281 | -0.013279 | 7.083e-05 | 2.7014e-05 | 0.079721 | 0.079721 | 0.079721 | 0.98728 | -0.088813 | 0.98591 | -0.098425 | 29.5262
26 | 0.0011911 | 0.00029845 | -0.001191 | -0.0002985 | 8.4246e-09 | -5.0556e-08 | 0.0017933 | 0.0017933 | 0.0017933 | 0.9883 | -0.081626 | 0.98829 | -0.081678 | 0.66418
27 | 0.051837 | 0.013035 | -0.05177 | -0.013009 | 6.7251e-05 | 2.5642e-05 | 0.078253 | 0.078253 | 0.078253 | 0.98591 | -0.098425 | 0.98459 | -0.10775 | 28.9825
28 | 0.0056853 | 0.0014248 | -0.0056853 | -0.0014248 | 6.4987e-08 | 7.449e-09 | 0.0086402 | 0.0086402 | 0.0086402 | 0.97913 | -0.14661 | 0.97912 | -0.1467 | 3.2001
29 | -0.0067635 | -0.001695 | 0.0067646 | 0.0016952 | 1.1287e-06 | 2.1875e-07 | 0.010279 | 0.010279 | 0.010279 | 0.97913 | -0.14661 | 0.9793 | -0.14541 | 3.8069
30 | 0.0033697 | 0.00084441 | -0.0033695 | -0.00084448 | 1.664e-07 | -6.3882e-08 | 0.005121 | 0.0051211 | 0.0051211 | 0.97912 | -0.1467 | 0.97907 | -0.14705 | 1.8967
31 | 0.014219 | 0.0035644 | -0.014215 | -0.003563 | 4.243e-06 | 1.4487e-06 | 0.021606 | 0.021607 | 0.021607 | 0.9793 | -0.14541 | 0.97899 | -0.14756 | 8.0024
32 | 0.02006 | 0.0050299 | -0.020036 | -0.0050213 | 2.3838e-05 | 8.6516e-06 | 0.030482 | 0.030482 | 0.030482 | 0.9793 | -0.14541 | 0.97809 | -0.15399 | 11.2896
33 | -0.041044 | -0.01029 | 0.041092 | 0.010308 | 4.7828e-05 | 1.8147e-05 | 0.062367 | 0.062367 | 0.062367 | 0.9793 | -0.14541 | 0.98047 | -0.137 | 23.0989
34 | 0.011449 | 0.0028698 | -0.011444 | -0.0028682 | 4.8156e-06 | 1.5319e-06 | 0.017402 | 0.017402 | 0.017402 | 0.97899 | -0.14756 | 0.97857 | -0.1506 | 6.4453
35 | 0.018775 | 0.0047052 | -0.018765 | -0.0047014 | 1.0528e-05 | 3.7899e-06 | 0.028563 | 0.028564 | 0.028564 | 0.97809 | -0.15399 | 0.97753 | -0.15805 | 10.5791
36 | -0.04553 | -0.01142 | 0.045573 | 0.011436 | 4.3081e-05 | 1.6387e-05 | 0.069102 | 0.069102 | 0.069102 | 0.98047 | -0.137 | 0.98143 | -0.13019 | 25.5933
37 | 0.0085459 | 0.0021418 | -0.0085456 | -0.0021417 | 2.6795e-07 | 7.1114e-08 | 0.012995 | 0.012995 | 0.012995 | 0.97857 | -0.1506 | 0.97854 | -0.15083 | 4.8129
38 | 0.0031971 | 0.000801 | -0.0031967 | -0.00080118 | 3.8689e-07 | -1.7933e-07 | 0.0048666 | 0.0048667 | 0.0048667 | 0.97753 | -0.15805 | 0.97741 | -0.15892 | 1.8025
39 | 0.011028 | 0.002763 | -0.011026 | -0.0027624 | 1.9901e-06 | 6.2359e-07 | 0.016787 | 0.016787 | 0.016787 | 0.97753 | -0.15805 | 0.97735 | -0.15935 | 6.2175
40 | 0.0045393 | 0.0011374 | -0.0045388 | -0.0011375 | 4.4616e-07 | -1.612e-08 | 0.0069097 | 0.0069097 | 0.0069097 | 0.97753 | -0.15805 | 0.97743 | -0.15876 | 2.5592
41 | -0.047809 | -0.011997 | 0.047876 | 0.012022 | 6.6835e-05 | 2.5448e-05 | 0.072492 | 0.072492 | 0.072492 | 0.98143 | -0.13019 | 0.98284 | -0.12013 | 26.8489
42 | 0.0060348 | 0.0015124 | -0.0060345 | -0.0015124 | 2.8577e-07 | 4.16e-08 | 0.0091768 | 0.0091769 | 0.0091769 | 0.97854 | -0.15083 | 0.97849 | -0.15117 | 3.3988
43 | 0.0095235 | 0.0023857 | -0.00952 | -0.0023847 | 3.5441e-06 | 1.0247e-06 | 0.014499 | 0.014499 | 0.014499 | 0.97735 | -0.15935 | 0.97697 | -0.16204 | 5.3701
44 | 0.0037769 | 0.00094652 | -0.0037768 | -0.00094655 | 1.4776e-07 | -3.2935e-08 | 0.0057499 | 0.0057499 | 0.0057499 | 0.97743 | -0.15876 | 0.97739 | -0.15904 | 2.1296
45 | -0.049812 | -0.012507 | 0.049877 | 0.012532 | 6.4689e-05 | 2.4649e-05 | 0.075424 | 0.075424 | 0.075424 | 0.98284 | -0.12013 | 0.98416 | -0.11079 | 27.9347
46 | 0.050835 | 0.012775 | -0.050813 | -0.012767 | 2.1554e-05 | 8.2158e-06 | 0.076839 | 0.076839 | 0.076839 | 0.98459 | -0.10775 | 0.98416 | -0.11079 | 28.4588
47 | -0.0015639 | -0.00039194 | 0.0015641 | 0.00039103 | 2.8941e-07 | -9.0798e-07 | 0.0023847 | 0.0023843 | 0.0023847 | 0.97584 | -0.17018 | 0.97602 | -0.16884 | 0.88321
48 | -0.0052836 | -0.0013232 | 0.0052845 | 0.0013233 | 9.7573e-07 | 7.4012e-08 | 0.0080548 | 0.0080547 | 0.0080548 | 0.97602 | -0.16884 | 0.97621 | -0.16751 | 2.9833
49 | -0.008604 | -0.0021552 | 0.0086105 | 0.002157 | 6.508e-06 | 1.7443e-06 | 0.013114 | 0.013114 | 0.013114 | 0.97621 | -0.16751 | 0.97697 | -0.16204 | 4.8572
50 | 0.00090948 | 0.00022772 | -0.00090946 | -0.00022793 | 2.0535e-08 | -2.0686e-07 | 0.0013851 | 0.0013852 | 0.0013852 | 0.97697 | -0.16204 | 0.97695 | -0.1622 | 0.51304
51 | -0.079227 | -0.019975 | 0.07936 | 0.020026 | 0.00013312 | 5.0417e-05 | 0.11879 | 0.11879 | 0.11879 | 0.99281 | -0.049817 | 0.99453 | -0.037845 | 21.9977
52 | 0.073965 | 0.018657 | -0.073917 | -0.018638 | 4.8471e-05 | 1.8316e-05 | 0.1109 | 0.1109 | 0.1109 | 0.99281 | -0.049817 | 0.99214 | -0.054493 | 20.5372
53 | -0.080557 | -0.020326 | 0.080585 | 0.020336 | 2.8107e-05 | 1.065e-05 | 0.12058 | 0.12058 | 0.12058 | 0.99453 | -0.037845 | 0.99489 | -0.035359 | 22.3292
54 | 0.07108 | 0.017927 | -0.071041 | -0.017913 | 3.9448e-05 | 1.4885e-05 | 0.10665 | 0.10665 | 0.10665 | 0.99214 | -0.054493 | 0.99157 | -0.058454 | 19.7494
55 | -0.082715 | -0.02087 | 0.082874 | 0.02093 | 0.00015862 | 6.0142e-05 | 0.12376 | 0.12376 | 0.12376 | 0.99489 | -0.035359 | 0.99686 | -0.02172 | 22.9192
56 | 0.066499 | 0.016774 | -0.066446 | -0.016754 | 5.3743e-05 | 2.0225e-05 | 0.099832 | 0.099832 | 0.099832 | 0.99157 | -0.058454 | 0.99074 | -0.064221 | 18.4873
57 | -0.08801 | -0.022218 | 0.088047 | 0.022232 | 3.6917e-05 | 1.402e-05 | 0.13143 | 0.13143 | 0.13143 | 0.99686 | -0.02172 | 0.99729 | -0.018735 | 24.3389
58 | -0.092159 | -0.023262 | 0.092267 | 0.023303 | 0.0001077 | 4.0946e-05 | 0.13757 | 0.13757 | 0.13757 | 0.99729 | -0.018735 | 0.99849 | -0.010423 | 25.4751

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23183 | 0.058348

## res_load
| p_mw | q_mvar
0 | 0.0032876 | 0.00082394
1 | 0.0012994 | 0.00032567
2 | 0.0025331 | 0.00063486
3 | 0.0032611 | 0.00081732
4 | 0.0035043 | 0.00087827
5 | 0.0049646 | 0.0012442
6 | 0.010951 | 0.0027446
7 | 0.0065664 | 0.0016457
8 | 0.0031965 | 0.00080113
9 | 0.0015897 | 0.00039842
10 | 0.015239 | 0.0038193
11 | 0.0018748 | 0.00046986
12 | 0.0027953 | 0.00070058
13 | 0.020143 | 0.0050484
14 | 0.0031189 | 0.00078167
15 | 0.044231 | 0.011085
16 | 0.011317 | 0.0028364
17 | 0.0008148 | 0.00020421
18 | 0.00090253 | 0.0002262
19 | 0.00097272 | 0.00024379
20 | 0.001191 | 0.0002985
21 | 0.0010782 | 0.00027021
22 | 0.0023156 | 0.00058034
23 | 0.0033695 | 0.00084448
24 | 0.002766 | 0.00069323
25 | 0.0012611 | 0.00031606
26 | 0.0044378 | 0.0011122
27 | 0.0028986 | 0.00072645
28 | 0.002236 | 0.0005604
29 | 0.0025108 | 0.00062926
30 | 0.0031967 | 0.00080118
31 | 0.0015029 | 0.00037666
32 | 0.00076186 | 0.00019094
33 | 0.0019364 | 0.00048531
34 | 0.0060345 | 0.0015124
35 | 0.00093553 | 0.00023447
36 | 0.0015639 | 0.00039194
37 | 0.0037194 | 0.00093218
38 | 0.0033194 | 0.00083193
39 | 0.00090946 | 0.00022793
40 | 0.00093608 | 0.0002346
41 | 0.0052621 | 0.0013188
42 | 0.0011968 | 0.00029995
43 | 0.0028363 | 0.00071083
44 | 0.0021301 | 0.00053386
45 | 0.0045416 | 0.0011382
46 | 0.0051363 | 0.0012873
47 | 0.0043504 | 0.0010903
48 | 0.004112 | 0.0010306
49 | 0.0037768 | 0.00094655
50 | 0.002758 | 0.00069121

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1