## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2265-8_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2265-8_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2265-8_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2265-8_0_3_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_2265-8_0_3_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_2265-8_0_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_2265-8_0_3_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_2265-8_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_2265-8_0_3_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_2265-8_0_3_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_2265-8_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2265-8_0_3_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_2265-8_0_3_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_2265-8_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2265-8_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2265-8_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2265-8_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2265-8_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2265-8_0_3_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_2265-8_0_3_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_2265-8_0_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2265-8_0_3_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_2265-8_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2265-8_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2265-8_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2265-8_0_3_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_2265-8_0_3_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_2265-8_0_3_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_2265-8_0_3_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_2265-8_0_3_node_24 | 0.4 | n |  | TRUE
30 | bus_MV_381_0_node_110 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2265-8_0_3_load_0 | 0 | 0.0053122 | 0.0013314 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2265-8_0_3_load_1 | 1 | 0.0066412 | 0.0016644 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2265-8_0_3_load_8 | 3 | 0.0034499 | 0.00086462 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2265-8_0_3_load_10 | 4 | 0.0085939 | 0.0021538 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2265-8_0_3_load_7 | 5 | 0.0029872 | 0.00074865 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2265-8_0_3_load_4 | 7 | 0.016593 | 0.0041586 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2265-8_0_3_load_28 | 8 | 0.0097577 | 0.0024455 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2265-8_0_3_load_29 | 9 | 0.012825 | 0.0032142 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2265-8_0_3_load_6 | 10 | 0.060664 | 0.015204 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2265-8_0_3_load_27 | 11 | 0.0017462 | 0.00043764 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2265-8_0_3_load_5 | 12 | 0.0056705 | 0.0014212 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2265-8_0_3_load_9 | 13 | 0.0085939 | 0.0021538 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2265-8_0_3_load_11 | 14 | 0.0085939 | 0.0021538 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2265-8_0_3_load_12 | 15 | 0.008594 | 0.0021539 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2265-8_0_3_load_14 | 17 | 0.00035721 | 8.9525e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2265-8_0_3_load_25 | 19 | 0.00052195 | 0.00013081 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2265-8_0_3_load_15 | 20 | 0.0026734 | 0.00067001 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2265-8_0_3_load_17 | 22 | 0.0011094 | 0.00027804 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2265-8_0_3_load_18 | 23 | 0.0011628 | 0.00029142 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2265-8_0_3_load_19 | 24 | 0.0025941 | 0.00065014 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2265-8_0_3_load_21 | 26 | 0.0023695 | 0.00059384 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2265-8_0_3_load_24 | 29 | 0.0020261 | 0.00050778 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2265-8_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.08274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2265-8_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.054837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2265-8_0_3_line_2 | NAYY 4x150 SE | 2 | 6 | 0.045681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2265-8_0_3_line_3 | NAYY 4x150 SE | 2 | 7 | 0.042562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2265-8_0_3_line_4 | NAYY 4x150 SE | 3 | 4 | 0.012186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2265-8_0_3_line_5 | NAYY 4x150 SE | 3 | 5 | 0.025139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2265-8_0_3_line_6 | NAYY 4x150 SE | 4 | 15 | 2.8683e-06 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2265-8_0_3_line_7 | NAYY 4x150 SE | 5 | 13 | 0.0048624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2265-8_0_3_line_8 | NAYY 4x150 SE | 6 | 12 | 0.082103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2265-8_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.032958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2265-8_0_3_line_10 | NAYY 4x150 SE | 8 | 9 | 0.064876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2265-8_0_3_line_11 | NAYY 4x150 SE | 8 | 10 | 0.14704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_2265-8_0_3_line_12 | NAYY 4x150 SE | 8 | 11 | 0.064432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2265-8_0_3_line_13 | NAYY 4x150 SE | 11 | 17 | 0.014081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2265-8_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 2.7939e-06 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2265-8_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.061904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2265-8_0_3_line_16 | NAYY 4x150 SE | 15 | 17 | 0.017714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2265-8_0_3_line_17 | NAYY 4x150 SE | 16 | 18 | 0.024198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2265-8_0_3_line_18 | NAYY 4x150 SE | 18 | 19 | 0.033584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2265-8_0_3_line_19 | NAYY 4x150 SE | 19 | 25 | 0.0086527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2265-8_0_3_line_20 | NAYY 4x150 SE | 20 | 21 | 0.050241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2265-8_0_3_line_21 | NAYY 4x150 SE | 21 | 22 | 0.024184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2265-8_0_3_line_22 | NAYY 4x150 SE | 21 | 23 | 0.020288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2265-8_0_3_line_23 | NAYY 4x150 SE | 22 | 24 | 0.0021674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2265-8_0_3_line_24 | NAYY 4x150 SE | 23 | 25 | 0.015635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2265-8_0_3_line_25 | NAYY 4x150 SE | 24 | 26 | 0.012109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2265-8_0_3_line_26 | NAYY 4x150 SE | 26 | 27 | 0.03911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2265-8_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.042283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2265-8_0_3_line_28 | NAYY 4x150 SE | 28 | 29 | 0.030595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2265-8_0_3_trafo_6 | 0.25 MVA 20/0.4 kV | 30 | 10 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2580731.901 | 1202082.4956 | 2580675.1976 | 1202022.2408
1 | 2580637.6164 | 1201982.3059 | 2580675.1976 | 1202022.2408
2 | 2580606.2681 | 1201949.001 | 2580637.6164 | 1201982.3059
3 | 2580637.6164 | 1201982.3059 | 2580668.2808 | 1201952.7899
4 | 2580882.0257 | 1201921.3369 | 2580890.3639 | 1201930.224
5 | 2580907.5645 | 1201948.5572 | 2580890.3639 | 1201930.224
6 | 2580882.0257 | 1201921.3369 | 2580882.0238 | 1201921.3348
7 | 2580910.8915 | 1201952.1032 | 2580907.5645 | 1201948.5572
8 | 2580606.2681 | 1201949.001 | 2580558.2483 | 1201897.9744 | 2580550.0004 | 1201889.2103
9 | 2580692.0263 | 1201929.9338 | 2580692.0263 | 1201929.9338 | 2580668.2808 | 1201952.7899
10 | 2580771.7935 | 1201803.8465 | 2580816.1831 | 1201851.1589
11 | 2580816.1831 | 1201851.1589 | 2580692.0263 | 1201929.9338
12 | 2580860.2687 | 1201898.1472 | 2580816.1831 | 1201851.1589
13 | 2580869.9035 | 1201908.4164 | 2580860.2687 | 1201898.1472
14 | 2580910.8934 | 1201952.1053 | 2580910.8915 | 1201952.1032
15 | 2580953.2496 | 1201997.2503 | 2580910.8934 | 1201952.1053
16 | 2580869.9035 | 1201908.4164 | 2580882.0238 | 1201921.3348
17 | 2580953.2496 | 1201997.2503 | 2580970.9052 | 1201980.6515
18 | 2580970.9052 | 1201980.6515 | 2580995.3688 | 1201957.6432
19 | 2581001.6719 | 1201951.7151 | 2580995.3688 | 1201957.6432
20 | 2581029.0992 | 1201930.3381 | 2581036.6336 | 1201930.4364 | 2581070.4864 | 1201956.4706
21 | 2581029.0992 | 1201930.3381 | 2581025.5602 | 1201906.4142
22 | 2581029.0992 | 1201930.3381 | 2581024.4796 | 1201930.2751 | 2581013.0637 | 1201941.0064
23 | 2581025.5602 | 1201906.4142 | 2581027.2774 | 1201905.0918
24 | 2581001.6719 | 1201951.7151 | 2581013.0637 | 1201941.0064
25 | 2581036.8711 | 1201897.7038 | 2581027.2774 | 1201905.0918
26 | 2581072.4263 | 1201887.977 | 2581050.3923 | 1201887.2912 | 2581036.8711 | 1201897.7038
27 | 2581072.4263 | 1201887.977 | 2581062.2392 | 1201879.3936 | 2581040.6858 | 1201859.9517
28 | 2581040.6858 | 1201859.9517 | 2581029.5225 | 1201850.7268 | 2581019.5704 | 1201841.9093 | 2581017.5472 | 1201839.8813

## bus_geodata
| x | y | coords
0 | 2580731.901 | 1202082.4956
1 | 2580675.1976 | 1202022.2408
2 | 2580637.6164 | 1201982.3059
3 | 2580890.3639 | 1201930.224
4 | 2580882.0257 | 1201921.3369
5 | 2580907.5645 | 1201948.5572
6 | 2580606.2681 | 1201949.001
7 | 2580668.2808 | 1201952.7899
8 | 2580816.1831 | 1201851.1589
9 | 2580771.7935 | 1201803.8465
10 | 2580692.0263 | 1201929.9338
11 | 2580860.2687 | 1201898.1472
12 | 2580550.0004 | 1201889.2103
13 | 2580910.8915 | 1201952.1032
14 | 2580910.8934 | 1201952.1053
15 | 2580882.0238 | 1201921.3348
16 | 2580953.2496 | 1201997.2503
17 | 2580869.9035 | 1201908.4164
18 | 2580970.9052 | 1201980.6515
19 | 2580995.3688 | 1201957.6432
20 | 2581070.4864 | 1201956.4706
21 | 2581029.0992 | 1201930.3381
22 | 2581025.5602 | 1201906.4142
23 | 2581013.0637 | 1201941.0064
24 | 2581027.2774 | 1201905.0918
25 | 2581001.6718 | 1201951.7151
26 | 2581036.8711 | 1201897.7038
27 | 2581072.4263 | 1201887.977
28 | 2581040.6858 | 1201859.9517
29 | 2581017.5472 | 1201839.8813
30 | 2580637.6164 | 1201982.3059

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99575 | -0.029828 | 0.0053122 | 0.0013314
1 | 0.99638 | -0.025403 | 0.0066412 | 0.0016644
2 | 0.99732 | -0.018814 | 0 | 0
3 | 0.98342 | -0.11617 | 0.0034499 | 0.00086462
4 | 0.98406 | -0.11163 | 0.0085939 | 0.0021538
5 | 0.98223 | -0.12466 | 0.0029872 | 0.00074865
6 | 0.99694 | -0.021419 | 0 | 0
7 | 0.99839 | -0.011284 | 0.016593 | 0.0041586
8 | 0.9917 | -0.057728 | 0.0097577 | 0.0024455
9 | 0.99051 | -0.066184 | 0.012825 | 0.0032142
10 | 1 | 0 | -0.11424 | -0.028583
11 | 0.98653 | -0.094154 | 0.0017462 | 0.00043764
12 | 0.99628 | -0.0261 | 0.0056705 | 0.0014212
13 | 0.98202 | -0.12615 | 0.0085939 | 0.0021538
14 | 0.98202 | -0.12615 | 0.0085939 | 0.0021538
15 | 0.98406 | -0.11163 | 0.008594 | 0.0021539
16 | 0.9809 | -0.13416 | 0 | 0
17 | 0.98543 | -0.10191 | 0.00035721 | 8.9525e-05
18 | 0.98046 | -0.1373 | 0 | 0
19 | 0.97985 | -0.14165 | 0.00052195 | 0.00013081
20 | 0.97891 | -0.14835 | 0.0026734 | 0.00067001
21 | 0.97911 | -0.14695 | 0 | 0
22 | 0.97882 | -0.14899 | 0.0011094 | 0.00027804
23 | 0.97943 | -0.14467 | 0.0011628 | 0.00029142
24 | 0.9788 | -0.14915 | 0.0025941 | 0.00065014
25 | 0.9797 | -0.14273 | 0 | 0
26 | 0.97872 | -0.14971 | 0.0023695 | 0.00059384
27 | 0.97861 | -0.15054 | 0 | 0
28 | 0.97848 | -0.15143 | 0 | 0
29 | 0.97839 | -0.15208 | 0.0020261 | 0.00050778
30 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0053122 | -0.0013314 | 0.0053154 | 0.0013315 | 3.2534e-06 | 1.7436e-07 | 0.0079384 | 0.007938 | 0.0079384 | 0.99575 | -0.029828 | 0.99638 | -0.025403 | 2.9401
1 | -0.011957 | -0.002996 | 0.011967 | 0.0029994 | 1.091e-05 | 3.4813e-06 | 0.017856 | 0.017856 | 0.017856 | 0.99638 | -0.025403 | 0.99732 | -0.018814 | 6.6134
2 | 0.0056762 | 0.0014217 | -0.0056742 | -0.0014215 | 2.0444e-06 | 1.9044e-07 | 0.0084687 | 0.0084689 | 0.0084689 | 0.99732 | -0.018814 | 0.99694 | -0.021419 | 3.1366
3 | -0.017644 | -0.0044211 | 0.017662 | 0.0044277 | 1.8404e-05 | 6.5226e-06 | 0.026325 | 0.026324 | 0.026325 | 0.99732 | -0.018814 | 0.99839 | -0.011284 | 9.7498
4 | -0.036166 | -0.0090702 | 0.036188 | 0.0090788 | 2.2773e-05 | 8.6042e-06 | 0.054725 | 0.054725 | 0.054725 | 0.98342 | -0.11617 | 0.98406 | -0.11163 | 20.2684
5 | 0.032716 | 0.0082056 | -0.032677 | -0.0081911 | 3.8444e-05 | 1.4467e-05 | 0.049505 | 0.049505 | 0.049505 | 0.98342 | -0.11617 | 0.98223 | -0.12466 | 18.3351
6 | -0.044782 | -0.011233 | 0.044782 | 0.011233 | 8.2079e-09 | 3.1283e-09 | 0.06772 | 0.06772 | 0.06772 | 0.98406 | -0.11163 | 0.98406 | -0.11163 | 25.0813
7 | 0.02969 | 0.0074425 | -0.029684 | -0.0074402 | 6.1385e-06 | 2.2994e-06 | 0.044979 | 0.044979 | 0.044979 | 0.98223 | -0.12466 | 0.98202 | -0.12615 | 16.659
8 | 0.0056742 | 0.0014215 | -0.0056705 | -0.0014212 | 3.6747e-06 | 3.4349e-07 | 0.0084689 | 0.0084693 | 0.0084693 | 0.99694 | -0.021419 | 0.99628 | -0.0261 | 3.1368
9 | -0.034255 | -0.0085863 | 0.034309 | 0.0086065 | 5.3607e-05 | 2.0186e-05 | 0.051055 | 0.051055 | 0.051055 | 0.99839 | -0.011284 | 1 | 0 | 18.9092
10 | 0.01284 | 0.0032191 | -0.012825 | -0.0032142 | 1.5026e-05 | 4.9434e-06 | 0.019266 | 0.019266 | 0.019266 | 0.9917 | -0.057728 | 0.99051 | -0.066184 | 7.1357
11 | -0.07849 | -0.019736 | 0.079127 | 0.019977 | 0.00063655 | 0.000241 | 0.11779 | 0.11779 | 0.11779 | 0.9917 | -0.057728 | 1 | 0 | 21.8138
12 | 0.055893 | 0.014071 | -0.05561 | -0.013963 | 0.00028293 | 0.00010799 | 0.083888 | 0.083888 | 0.083888 | 0.9917 | -0.057728 | 0.98653 | -0.094154 | 31.0696
13 | 0.053864 | 0.013526 | -0.053806 | -0.013504 | 5.8012e-05 | 2.2133e-05 | 0.081254 | 0.081254 | 0.081254 | 0.98653 | -0.094154 | 0.98543 | -0.10191 | 30.0941
14 | 0.02109 | 0.0052863 | -0.02109 | -0.0052863 | 1.7804e-09 | 6.5622e-10 | 0.031957 | 0.031957 | 0.031957 | 0.98202 | -0.12615 | 0.98202 | -0.12615 | 11.836
15 | 0.012496 | 0.0031325 | -0.012482 | -0.003128 | 1.385e-05 | 4.5447e-06 | 0.018935 | 0.018936 | 0.018936 | 0.98202 | -0.12615 | 0.9809 | -0.13416 | 7.0132
16 | -0.053376 | -0.013387 | 0.053448 | 0.013414 | 7.2012e-05 | 2.7472e-05 | 0.080715 | 0.080715 | 0.080715 | 0.98406 | -0.11163 | 0.98543 | -0.10191 | 29.8944
17 | 0.012482 | 0.003128 | -0.012477 | -0.0031262 | 5.4141e-06 | 1.777e-06 | 0.018936 | 0.018936 | 0.018936 | 0.9809 | -0.13416 | 0.98046 | -0.1373 | 7.0132
18 | 0.012477 | 0.0031262 | -0.012469 | -0.0031237 | 7.5141e-06 | 2.4668e-06 | 0.018936 | 0.018936 | 0.018936 | 0.98046 | -0.1373 | 0.97985 | -0.14165 | 7.0133
19 | 0.011948 | 0.0029929 | -0.011946 | -0.0029923 | 1.7773e-06 | 5.7462e-07 | 0.018143 | 0.018143 | 0.018143 | 0.97985 | -0.14165 | 0.9797 | -0.14273 | 6.7197
20 | -0.0026734 | -0.00067001 | 0.0026739 | 0.00066957 | 5.1768e-07 | -4.3264e-07 | 0.0040637 | 0.0040635 | 0.0040637 | 0.97891 | -0.14835 | 0.97911 | -0.14695 | 1.5051
21 | 0.0081025 | 0.0020292 | -0.0081002 | -0.0020287 | 2.2881e-06 | 5.7597e-07 | 0.012313 | 0.012313 | 0.012313 | 0.97911 | -0.14695 | 0.97882 | -0.14899 | 4.5605
22 | -0.010776 | -0.0026988 | 0.01078 | 0.0026999 | 3.3953e-06 | 1.0507e-06 | 0.016377 | 0.016377 | 0.016377 | 0.97911 | -0.14695 | 0.97943 | -0.14467 | 6.0655
23 | 0.0069908 | 0.0017506 | -0.0069906 | -0.0017506 | 1.5274e-07 | 3.1502e-08 | 0.010627 | 0.010627 | 0.010627 | 0.97882 | -0.14899 | 0.9788 | -0.14915 | 3.9359
24 | -0.011943 | -0.0029913 | 0.011946 | 0.0029923 | 3.2115e-06 | 1.0384e-06 | 0.018143 | 0.018143 | 0.018143 | 0.97943 | -0.14467 | 0.9797 | -0.14273 | 6.7198
25 | 0.0043965 | 0.0011005 | -0.0043962 | -0.0011005 | 3.375e-07 | -2.2376e-08 | 0.0066833 | 0.0066833 | 0.0066833 | 0.9788 | -0.14915 | 0.97872 | -0.14971 | 2.4753
26 | 0.0020267 | 0.00050663 | -0.0020265 | -0.00050703 | 2.3167e-07 | -4.0234e-07 | 0.0030809 | 0.0030811 | 0.0030811 | 0.97872 | -0.14971 | 0.97861 | -0.15054 | 1.1411
27 | 0.0020265 | 0.00050703 | -0.0020263 | -0.00050747 | 2.5049e-07 | -4.3483e-07 | 0.0030811 | 0.0030813 | 0.0030813 | 0.97861 | -0.15054 | 0.97848 | -0.15143 | 1.1412
28 | 0.0020263 | 0.00050747 | -0.0020261 | -0.00050778 | 1.8127e-07 | -3.1454e-07 | 0.0030813 | 0.0030814 | 0.0030814 | 0.97848 | -0.15143 | 0.97839 | -0.15208 | 1.1413

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.1749 | 0.043787

## res_load
| p_mw | q_mvar
0 | 0.0053122 | 0.0013314
1 | 0.0066412 | 0.0016644
2 | 0.0034499 | 0.00086462
3 | 0.0085939 | 0.0021538
4 | 0.0029872 | 0.00074865
5 | 0.016593 | 0.0041586
6 | 0.0097577 | 0.0024455
7 | 0.012825 | 0.0032142
8 | 0.060664 | 0.015204
9 | 0.0017462 | 0.00043764
10 | 0.0056705 | 0.0014212
11 | 0.0085939 | 0.0021538
12 | 0.0085939 | 0.0021538
13 | 0.008594 | 0.0021539
14 | 0.00035721 | 8.9525e-05
15 | 0.00052195 | 0.00013081
16 | 0.0026734 | 0.00067001
17 | 0.0011094 | 0.00027804
18 | 0.0011628 | 0.00029142
19 | 0.0025941 | 0.00065014
20 | 0.0023695 | 0.00059384
21 | 0.0020261 | 0.00050778

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1