## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2284-13_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2284-13_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2284-13_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2284-13_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2284-13_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2284-13_0_2_node_28 | 0.4 | n |  | TRUE
6 | bus_LV_2284-13_0_2_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_2284-13_0_2_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_2284-13_0_2_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_2284-13_0_2_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2284-13_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2284-13_0_2_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2284-13_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2284-13_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2284-13_0_2_node_39 | 0.4 | n |  | TRUE
15 | bus_LV_2284-13_0_2_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_2284-13_0_2_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_2284-13_0_2_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_2284-13_0_2_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2284-13_0_2_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2284-13_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2284-13_0_2_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_2284-13_0_2_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_2284-13_0_2_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_2284-13_0_2_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2284-13_0_2_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2284-13_0_2_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2284-13_0_2_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2284-13_0_2_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_2284-13_0_2_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_2284-13_0_2_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2284-13_0_2_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_2284-13_0_2_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_2284-13_0_2_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_2284-13_0_2_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_2284-13_0_2_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_2284-13_0_2_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_2284-13_0_2_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_2284-13_0_2_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2284-13_0_2_node_33 | 0.4 | n |  | TRUE
40 | bus_MV_379_0_node_28 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2284-13_0_2_load_0 | 0 | 0.0018718 | 0.00046912 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2284-13_0_2_load_1 | 1 | 0.0012016 | 0.00030115 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2284-13_0_2_load_3 | 3 | 0.0016557 | 0.00041496 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2284-13_0_2_load_4 | 4 | 0.0045314 | 0.0011357 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2284-13_0_2_load_28 | 5 | 0.0032031 | 0.00080278 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2284-13_0_2_load_14 | 6 | 0.0027705 | 0.00069435 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2284-13_0_2_load_35 | 7 | 0.0024708 | 0.00061924 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2284-13_0_2_load_5 | 9 | 0.0020853 | 0.00052262 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2284-13_0_2_load_6 | 10 | 0.00072669 | 0.00018212 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2284-13_0_2_load_7 | 12 | 0.0027805 | 0.00069686 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2284-13_0_2_load_9 | 13 | 0.0013834 | 0.00034671 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2284-13_0_2_load_39 | 14 | 0.0055658 | 0.0013949 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2284-13_0_2_load_38 | 16 | 0.0018278 | 0.00045808 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2284-13_0_2_load_11 | 18 | 0.0017636 | 0.00044199 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2284-13_0_2_load_15 | 20 | 0.0021936 | 0.00054976 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2284-13_0_2_load_37 | 22 | 0.0014228 | 0.00035659 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2284-13_0_2_load_41 | 23 | 0.0046842 | 0.001174 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2284-13_0_2_load_16 | 24 | 0.0018241 | 0.00045716 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2284-13_0_2_load_18 | 26 | 0.0035943 | 0.00090083 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2284-13_0_2_load_29 | 28 | 0.0036013 | 0.00090256 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2284-13_0_2_load_30 | 29 | 0.0016041 | 0.00040203 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2284-13_0_2_load_23 | 30 | 0.0033862 | 0.00084867 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2284-13_0_2_load_24 | 31 | 0.0036338 | 0.00091071 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2284-13_0_2_load_25 | 32 | 0.0030814 | 0.00077227 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2284-13_0_2_load_26 | 33 | 0.0048637 | 0.001219 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2284-13_0_2_load_27 | 34 | 0.0025249 | 0.00063281 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2284-13_0_2_load_34 | 36 | 0.0060851 | 0.0015251 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2284-13_0_2_load_31 | 37 | 0.0043569 | 0.0010919 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2284-13_0_2_load_32 | 38 | 0.0032834 | 0.0008229 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2284-13_0_2_load_33 | 39 | 0.000721 | 0.0001807 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2284-13_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2284-13_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.015459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2284-13_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.038793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2284-13_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.041712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2284-13_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0034631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2284-13_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.02026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2284-13_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0002756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2284-13_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.010372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2284-13_0_2_line_8 | NAYY 4x150 SE | 7 | 35 | 0.014452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2284-13_0_2_line_9 | NAYY 4x150 SE | 8 | 20 | 0.0048941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2284-13_0_2_line_10 | NAYY 4x150 SE | 8 | 18 | 0.023631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2284-13_0_2_line_11 | NAYY 4x150 SE | 9 | 10 | 0.0082307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2284-13_0_2_line_12 | NAYY 4x150 SE | 10 | 11 | 0.021078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2284-13_0_2_line_13 | NAYY 4x150 SE | 11 | 14 | 0.01634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2284-13_0_2_line_14 | NAYY 4x150 SE | 12 | 13 | 0.00060669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2284-13_0_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.022422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2284-13_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.017571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2284-13_0_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.011342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2284-13_0_2_line_18 | NAYY 4x150 SE | 16 | 22 | 0.0075266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2284-13_0_2_line_19 | NAYY 4x150 SE | 17 | 30 | 0.016069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2284-13_0_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.12847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2284-13_0_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.68964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2284-13_0_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.0086131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2284-13_0_2_line_23 | NAYY 4x150 SE | 21 | 23 | 0.010243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2284-13_0_2_line_24 | NAYY 4x150 SE | 24 | 25 | 0.013332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2284-13_0_2_line_25 | NAYY 4x150 SE | 24 | 26 | 0.0014905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2284-13_0_2_line_26 | NAYY 4x150 SE | 25 | 27 | 0.097627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2284-13_0_2_line_27 | NAYY 4x150 SE | 27 | 28 | 0.020069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2284-13_0_2_line_28 | NAYY 4x150 SE | 28 | 29 | 0.0012257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2284-13_0_2_line_29 | NAYY 4x150 SE | 29 | 37 | 0.0019716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2284-13_0_2_line_30 | NAYY 4x150 SE | 30 | 31 | 0.012076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2284-13_0_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.012271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2284-13_0_2_line_32 | NAYY 4x150 SE | 32 | 33 | 0.0242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2284-13_0_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.00083464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2284-13_0_2_line_34 | NAYY 4x150 SE | 34 | 35 | 0.026657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2284-13_0_2_line_35 | NAYY 4x150 SE | 35 | 36 | 0.0099173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2284-13_0_2_line_36 | NAYY 4x150 SE | 36 | 39 | 0.010158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2284-13_0_2_line_37 | NAYY 4x150 SE | 37 | 38 | 0.012429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2284-13_0_2_line_38 | NAYY 4x150 SE | 38 | 39 | 0.0017434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2284-13_0_2_trafo_4 | 0.25 MVA 20/0.4 kV | 40 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2574142.1089 | 1200460.4006 | 2574149.9796 | 1200444.7473
1 | 2574135.1644 | 1200474.2121 | 2574142.1089 | 1200460.4006
2 | 2574149.9796 | 1200444.7473 | 2574155.5336 | 1200433.7015 | 2574166.8893 | 1200409.8354
3 | 2574135.1644 | 1200474.2121 | 2574100.6173 | 1200450.8365
4 | 2574166.8893 | 1200409.8354 | 2574168.3772 | 1200406.7082
5 | 2574100.6173 | 1200450.8365 | 2574096.5714 | 1200448.0989 | 2574083.7431 | 1200439.6242
6 | 2574168.4956 | 1200406.4593 | 2574168.3772 | 1200406.7082
7 | 2574075.0889 | 1200433.9069 | 2574083.7431 | 1200439.6242
8 | 2574174.7013 | 1200393.4074 | 2574172.559 | 1200397.9192 | 2574168.4956 | 1200406.4593
9 | 2574075.0889 | 1200433.9069 | 2574071.6016 | 1200430.473
10 | 2574075.0889 | 1200433.9069 | 2574056.3468 | 1200438.9468 | 2574052.1289 | 1200438.7432
11 | 2574054.5781 | 1200372.747 | 2574049.4848 | 1200379.2126
12 | 2574035.9387 | 1200395.3564 | 2574045.9361 | 1200383.7175 | 2574049.4848 | 1200379.2126
13 | 2574035.9387 | 1200395.3564 | 2574047.5815 | 1200406.8208
14 | 2574083.858 | 1200335.7926 | 2574083.5015 | 1200336.2836
15 | 2574101.1677 | 1200321.8321 | 2574086.3921 | 1200332.3021 | 2574083.858 | 1200335.7926
16 | 2574060.1014 | 1200419.1489 | 2574047.5815 | 1200406.8208
17 | 2574101.1677 | 1200321.8321 | 2574107.2384 | 1200331.4221
18 | 2574065.4644 | 1200424.4298 | 2574060.1014 | 1200419.1489
19 | 2574107.2384 | 1200331.4221 | 2574117.0568 | 1200344.1424
20 | 2573927.9557 | 1200410.2252 | 2573951.9152 | 1200419.7922 | 2573985.9556 | 1200431.661 | 2574027.1936 | 1200437.5398 | 2574052.1289 | 1200438.7432
21 | 2573927.9557 | 1200410.2252 | 2573592.4945 | 1201012.7777
22 | 2574071.6016 | 1200430.473 | 2574065.4644 | 1200424.4298
23 | 2573592.4945 | 1201012.7777 | 2573582.9282 | 1201016.511
24 | 2574263.6947 | 1200333.2448 | 2574252.639 | 1200325.7932
25 | 2574251.403 | 1200324.9601 | 2574252.639 | 1200325.7932
26 | 2574224.2614 | 1200422.5531 | 2574254.563 | 1200351.5499 | 2574260.6695 | 1200339.5836 | 2574263.6947 | 1200333.2448
27 | 2574224.2614 | 1200422.5531 | 2574217.0516 | 1200418.7822 | 2574209.612 | 1200414.7122 | 2574206.6646 | 1200412.9135
28 | 2574206.6646 | 1200412.9135 | 2574205.6183 | 1200412.275
29 | 2574205.6183 | 1200412.275 | 2574203.9353 | 1200411.2479
30 | 2574117.0568 | 1200344.1424 | 2574117.313 | 1200344.4743 | 2574125.2773 | 1200352.9854
31 | 2574125.2773 | 1200352.9854 | 2574127.477 | 1200355.3361 | 2574134.0812 | 1200361.5267
32 | 2574152.4848 | 1200377.2263 | 2574148.2785 | 1200373.967 | 2574136.4962 | 1200363.7904 | 2574134.0812 | 1200361.5267
33 | 2574153.1445 | 1200377.7375 | 2574152.4848 | 1200377.2263
34 | 2574174.7013 | 1200393.4074 | 2574160.3771 | 1200383.3419 | 2574153.1445 | 1200377.7375
35 | 2574174.7013 | 1200393.4074 | 2574183.1668 | 1200398.5736
36 | 2574183.1668 | 1200398.5736 | 2574191.8376 | 1200403.8651
37 | 2574193.3258 | 1200404.7733 | 2574203.9353 | 1200411.2479
38 | 2574193.3258 | 1200404.7733 | 2574191.8376 | 1200403.8651

## bus_geodata
| x | y | coords
0 | 2574142.1089 | 1200460.4006
1 | 2574149.9796 | 1200444.7473
2 | 2574135.1644 | 1200474.2121
3 | 2574166.8893 | 1200409.8354
4 | 2574100.6173 | 1200450.8365
5 | 2574168.3772 | 1200406.7082
6 | 2574083.7431 | 1200439.6242
7 | 2574168.4956 | 1200406.4593
8 | 2574075.0889 | 1200433.9069
9 | 2574054.5781 | 1200372.747
10 | 2574049.4848 | 1200379.2126
11 | 2574035.9387 | 1200395.3564
12 | 2574083.5015 | 1200336.2836
13 | 2574083.858 | 1200335.7926
14 | 2574047.5815 | 1200406.8208
15 | 2574101.1677 | 1200321.8321
16 | 2574060.1014 | 1200419.1489
17 | 2574107.2384 | 1200331.4221
18 | 2574052.1289 | 1200438.7432
19 | 2573927.9557 | 1200410.2252
20 | 2574071.6016 | 1200430.473
21 | 2573592.4945 | 1201012.7777
22 | 2574065.4644 | 1200424.4298
23 | 2573582.9283 | 1201016.511
24 | 2574252.639 | 1200325.7932
25 | 2574263.6947 | 1200333.2448
26 | 2574251.403 | 1200324.9601
27 | 2574224.2614 | 1200422.5531
28 | 2574206.6646 | 1200412.9135
29 | 2574205.6183 | 1200412.275
30 | 2574117.0568 | 1200344.1424
31 | 2574125.2773 | 1200352.9854
32 | 2574134.0812 | 1200361.5267
33 | 2574152.4848 | 1200377.2263
34 | 2574153.1445 | 1200377.7375
35 | 2574174.7013 | 1200393.4074
36 | 2574183.1668 | 1200398.5736
37 | 2574203.9353 | 1200411.2479
38 | 2574193.3258 | 1200404.7733
39 | 2574191.8376 | 1200403.8651
40 | 2574075.0889 | 1200433.9069

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99529 | -0.032772 | 0.0018718 | 0.00046912
1 | 0.9939 | -0.042546 | 0.0012016 | 0.00030115
2 | 0.99657 | -0.02388 | 0 | 0
3 | 0.99087 | -0.063809 | 0.0016557 | 0.00041496
4 | 1 | 0 | -0.081634 | -0.02033
5 | 0.99061 | -0.065655 | 0.0032031 | 0.00080278
6 | 0.99933 | -0.0046806 | 0.0027705 | 0.00069435
7 | 0.99059 | -0.065793 | 0.0024708 | 0.00061924
8 | 0.99903 | -0.0067919 | 0 | 0
9 | 0.9983 | -0.011941 | 0.0020853 | 0.00052262
10 | 0.99832 | -0.011769 | 0.00072669 | 0.00018212
11 | 0.99841 | -0.011175 | 0 | 0
12 | 0.98763 | -0.086731 | 0.0027805 | 0.00069686
13 | 0.98764 | -0.086713 | 0.0013834 | 0.00034671
14 | 0.99847 | -0.010715 | 0.0055658 | 0.0013949
15 | 0.98777 | -0.085758 | 0 | 0
16 | 0.99868 | -0.0092403 | 0.0018278 | 0.00045808
17 | 0.98784 | -0.085274 | 0 | 0
18 | 0.99881 | -0.0083351 | 0.0017636 | 0.00044199
19 | 0.99795 | -0.014456 | 0 | 0
20 | 0.99894 | -0.0074687 | 0.0021936 | 0.00054976
21 | 0.99332 | -0.047218 | 0 | 0
22 | 0.99879 | -0.0084712 | 0.0014228 | 0.00035659
23 | 0.99325 | -0.047704 | 0.0046842 | 0.001174
24 | 0.9876 | -0.086997 | 0.0018241 | 0.00045716
25 | 0.9877 | -0.086258 | 0 | 0
26 | 0.98759 | -0.087052 | 0.0035943 | 0.00090083
27 | 0.98847 | -0.080845 | 0 | 0
28 | 0.98862 | -0.079732 | 0.0036013 | 0.00090256
29 | 0.98864 | -0.079619 | 0.0016041 | 0.00040203
30 | 0.98794 | -0.08459 | 0.0033862 | 0.00084867
31 | 0.98807 | -0.083657 | 0.0036338 | 0.00091071
32 | 0.98827 | -0.082253 | 0.0030814 | 0.00077227
33 | 0.98876 | -0.078725 | 0.0048637 | 0.001219
34 | 0.98879 | -0.078562 | 0.0025249 | 0.00063281
35 | 0.98962 | -0.072672 | 0 | 0
36 | 0.98926 | -0.075208 | 0.0060851 | 0.0015251
37 | 0.98867 | -0.079404 | 0.0043569 | 0.0010919
38 | 0.98894 | -0.077502 | 0.0032834 | 0.0008229
39 | 0.98898 | -0.077177 | 0.000721 | 0.0001807
40 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.055604 | 0.013978 | -0.055529 | -0.013949 | 7.5583e-05 | 2.8843e-05 | 0.083146 | 0.083146 | 0.083146 | 0.99529 | -0.032772 | 0.9939 | -0.042546 | 30.7949
1 | -0.057476 | -0.014447 | 0.057547 | 0.014474 | 7.1254e-05 | 2.7204e-05 | 0.085945 | 0.085945 | 0.085945 | 0.99529 | -0.032772 | 0.99657 | -0.02388 | 31.8314
2 | 0.054327 | 0.013648 | -0.054167 | -0.013587 | 0.00016019 | 6.111e-05 | 0.081347 | 0.081348 | 0.081348 | 0.9939 | -0.042546 | 0.99087 | -0.063809 | 30.1287
3 | -0.057547 | -0.014474 | 0.05774 | 0.014547 | 0.00019226 | 7.34e-05 | 0.085945 | 0.085944 | 0.085945 | 0.99657 | -0.02388 | 1 | 0 | 31.8314
4 | 0.052511 | 0.013172 | -0.052498 | -0.013167 | 1.3439e-05 | 5.1243e-06 | 0.078861 | 0.078861 | 0.078861 | 0.99087 | -0.063809 | 0.99061 | -0.065655 | 29.2078
5 | 0.023094 | 0.0057825 | -0.023079 | -0.005777 | 1.4928e-05 | 5.4758e-06 | 0.034362 | 0.034362 | 0.034362 | 1 | 0 | 0.99933 | -0.0046806 | 12.7268
6 | 0.049295 | 0.012364 | -0.049294 | -0.012363 | 9.4301e-07 | 3.5915e-07 | 0.07405 | 0.07405 | 0.07405 | 0.99061 | -0.065655 | 0.99059 | -0.065793 | 27.4258
7 | 0.020309 | 0.0050827 | -0.020303 | -0.0050806 | 5.9175e-06 | 2.1401e-06 | 0.030237 | 0.030237 | 0.030237 | 0.99933 | -0.0046806 | 0.99903 | -0.0067919 | 11.199
8 | 0.046823 | 0.011744 | -0.046778 | -0.011727 | 4.4617e-05 | 1.6974e-05 | 0.070338 | 0.070338 | 0.070338 | 0.99059 | -0.065793 | 0.98962 | -0.072672 | 26.0512
9 | 0.013828 | 0.0034654 | -0.013827 | -0.0034649 | 1.2955e-06 | 4.3419e-07 | 0.020596 | 0.020596 | 0.020596 | 0.99903 | -0.0067919 | 0.99894 | -0.0074687 | 7.6282
10 | 0.0064746 | 0.0016152 | -0.0064732 | -0.001615 | 1.3706e-06 | 2.178e-07 | 0.009641 | 0.0096411 | 0.0096411 | 0.99903 | -0.0067919 | 0.99881 | -0.0083351 | 3.5708
11 | -0.0020853 | -0.00052262 | 0.0020853 | 0.00052253 | 4.9617e-08 | -8.8534e-08 | 0.0031082 | 0.0031082 | 0.0031082 | 0.9983 | -0.011941 | 0.99832 | -0.011769 | 1.1512
12 | -0.002812 | -0.00070465 | 0.0028122 | 0.00070446 | 2.3104e-07 | -1.8676e-07 | 0.0041913 | 0.0041912 | 0.0041913 | 0.99832 | -0.011769 | 0.99841 | -0.011175 | 1.5523
13 | -0.0028122 | -0.00070446 | 0.0028124 | 0.00070432 | 1.791e-07 | -1.4481e-07 | 0.0041912 | 0.0041911 | 0.0041912 | 0.99841 | -0.011175 | 0.99847 | -0.010715 | 1.5523
14 | -0.0027805 | -0.00069686 | 0.0027805 | 0.00069685 | 6.6437e-09 | -5.2084e-09 | 0.0041892 | 0.0041892 | 0.0041892 | 0.98763 | -0.086731 | 0.98764 | -0.086713 | 1.5516
15 | -0.0041639 | -0.0010436 | 0.0041645 | 0.0010435 | 5.5066e-07 | -7.5185e-08 | 0.0062735 | 0.0062734 | 0.0062735 | 0.98764 | -0.086713 | 0.98777 | -0.085758 | 2.3235
16 | -0.0083782 | -0.0020992 | 0.0083799 | 0.0020997 | 1.7092e-06 | 4.2754e-07 | 0.012486 | 0.012486 | 0.012486 | 0.99847 | -0.010715 | 0.99868 | -0.0092403 | 4.6244
17 | -0.0041645 | -0.0010435 | 0.0041647 | 0.0010435 | 2.7853e-07 | -3.8063e-08 | 0.0062734 | 0.0062734 | 0.0062734 | 0.98777 | -0.085758 | 0.98784 | -0.085274 | 2.3235
18 | -0.010208 | -0.0025578 | 0.010209 | 0.0025581 | 1.0864e-06 | 3.1935e-07 | 0.015209 | 0.015209 | 0.015209 | 0.99868 | -0.0092403 | 0.99879 | -0.0084712 | 5.633
19 | -0.0041647 | -0.0010435 | 0.0041651 | 0.0010434 | 3.9461e-07 | -5.3964e-08 | 0.0062734 | 0.0062733 | 0.0062734 | 0.98784 | -0.085274 | 0.98794 | -0.08459 | 2.3235
20 | 0.0047097 | 0.001173 | -0.0047057 | -0.0011731 | 3.9439e-06 | -1.631e-07 | 0.0070138 | 0.0070144 | 0.0070144 | 0.99881 | -0.0083351 | 0.99795 | -0.014456 | 2.5979
21 | 0.0047057 | 0.0011731 | -0.0046845 | -0.001174 | 2.1183e-05 | -8.2164e-07 | 0.0070144 | 0.0070175 | 0.0070175 | 0.99795 | -0.014456 | 0.99332 | -0.047218 | 2.5991
22 | 0.011633 | 0.0029152 | -0.011632 | -0.0029147 | 1.6139e-06 | 5.0799e-07 | 0.017329 | 0.017329 | 0.017329 | 0.99894 | -0.0074687 | 0.99879 | -0.0084712 | 6.4181
23 | 0.0046845 | 0.001174 | -0.0046842 | -0.001174 | 3.1476e-07 | -1.1519e-08 | 0.0070175 | 0.0070176 | 0.0070176 | 0.99332 | -0.047218 | 0.99325 | -0.047704 | 2.5991
24 | -0.0054185 | -0.001358 | 0.005419 | 0.001358 | 5.545e-07 | 4.2648e-08 | 0.008164 | 0.0081639 | 0.008164 | 0.9876 | -0.086997 | 0.9877 | -0.086258 | 3.0237
25 | 0.0035944 | 0.00090082 | -0.0035943 | -0.00090083 | 2.7279e-08 | -8.5806e-09 | 0.0054156 | 0.0054156 | 0.0054156 | 0.9876 | -0.086997 | 0.98759 | -0.087052 | 2.0058
26 | -0.005419 | -0.001358 | 0.0054231 | 0.0013583 | 4.06e-06 | 3.111e-07 | 0.0081639 | 0.0081635 | 0.0081639 | 0.9877 | -0.086258 | 0.98847 | -0.080845 | 3.0237
27 | -0.0054231 | -0.0013583 | 0.0054239 | 0.0013584 | 8.3458e-07 | 6.3692e-08 | 0.0081635 | 0.0081634 | 0.0081635 | 0.98847 | -0.080845 | 0.98862 | -0.079732 | 3.0235
28 | -0.0090252 | -0.002261 | 0.0090253 | 0.002261 | 1.4113e-07 | 3.8564e-08 | 0.013584 | 0.013584 | 0.013584 | 0.98862 | -0.079732 | 0.98864 | -0.079619 | 5.031
29 | -0.010629 | -0.002663 | 0.01063 | 0.0026631 | 3.1489e-07 | 9.5827e-08 | 0.015998 | 0.015998 | 0.015998 | 0.98864 | -0.079619 | 0.98867 | -0.079404 | 5.9253
30 | -0.0075514 | -0.0018921 | 0.0075523 | 0.0018923 | 9.7473e-07 | 2.2025e-07 | 0.011374 | 0.011374 | 0.011374 | 0.98794 | -0.08459 | 0.98807 | -0.083657 | 4.2124
31 | -0.011186 | -0.002803 | 0.011188 | 0.0028037 | 2.173e-06 | 6.7858e-07 | 0.016846 | 0.016846 | 0.016846 | 0.98807 | -0.083657 | 0.98827 | -0.082253 | 6.2392
32 | -0.01427 | -0.0035759 | 0.014277 | 0.0035783 | 6.9709e-06 | 2.3709e-06 | 0.021485 | 0.021485 | 0.021485 | 0.98827 | -0.082253 | 0.98876 | -0.078725 | 7.9576
33 | -0.01914 | -0.0047973 | 0.019141 | 0.0047974 | 4.3213e-07 | 1.555e-07 | 0.028805 | 0.028805 | 0.028805 | 0.98876 | -0.078725 | 0.98879 | -0.078562 | 10.6685
34 | -0.021666 | -0.0054302 | 0.021683 | 0.0054367 | 1.7683e-05 | 6.4589e-06 | 0.032605 | 0.032605 | 0.032605 | 0.98879 | -0.078562 | 0.98962 | -0.072672 | 12.0758
35 | 0.025095 | 0.0062905 | -0.025086 | -0.0062873 | 8.8113e-06 | 3.2616e-06 | 0.037734 | 0.037734 | 0.037734 | 0.98962 | -0.072672 | 0.98926 | -0.075208 | 13.9755
36 | 0.019001 | 0.0047622 | -0.018996 | -0.0047603 | 5.1777e-06 | 1.861e-06 | 0.028581 | 0.028581 | 0.028581 | 0.98926 | -0.075208 | 0.98898 | -0.077177 | 10.5855
37 | -0.014987 | -0.0037551 | 0.014991 | 0.0037564 | 3.9458e-06 | 1.3582e-06 | 0.022556 | 0.022556 | 0.022556 | 0.98867 | -0.079404 | 0.98894 | -0.077502 | 8.3539
38 | -0.018274 | -0.0045793 | 0.018275 | 0.0045796 | 8.2248e-07 | 2.9397e-07 | 0.027496 | 0.027496 | 0.027496 | 0.98894 | -0.077502 | 0.98898 | -0.077177 | 10.1837

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.086165 | 0.021466

## res_load
| p_mw | q_mvar
0 | 0.0018718 | 0.00046912
1 | 0.0012016 | 0.00030115
2 | 0.0016557 | 0.00041496
3 | 0.0045314 | 0.0011357
4 | 0.0032031 | 0.00080278
5 | 0.0027705 | 0.00069435
6 | 0.0024708 | 0.00061924
7 | 0.0020853 | 0.00052262
8 | 0.00072669 | 0.00018212
9 | 0.0027805 | 0.00069686
10 | 0.0013834 | 0.00034671
11 | 0.0055658 | 0.0013949
12 | 0.0018278 | 0.00045808
13 | 0.0017636 | 0.00044199
14 | 0.0021936 | 0.00054976
15 | 0.0014228 | 0.00035659
16 | 0.0046842 | 0.001174
17 | 0.0018241 | 0.00045716
18 | 0.0035943 | 0.00090083
19 | 0.0036013 | 0.00090256
20 | 0.0016041 | 0.00040203
21 | 0.0033862 | 0.00084867
22 | 0.0036338 | 0.00091071
23 | 0.0030814 | 0.00077227
24 | 0.0048637 | 0.001219
25 | 0.0025249 | 0.00063281
26 | 0.0060851 | 0.0015251
27 | 0.0043569 | 0.0010919
28 | 0.0032834 | 0.0008229
29 | 0.000721 | 0.0001807

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1