## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2284-19_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2284-19_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2284-19_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2284-19_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2284-19_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2284-19_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2284-19_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_2284-19_0_4_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_2284-19_0_4_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_2284-19_0_4_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_2284-19_0_4_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_2284-19_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2284-19_0_4_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_2284-19_0_4_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_2284-19_0_4_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_2284-19_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2284-19_0_4_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_2284-19_0_4_node_6 | 0.4 | n |  | TRUE
18 | bus_LV_2284-19_0_4_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_2284-19_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_2284-19_0_4_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_2284-19_0_4_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_2284-19_0_4_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2284-19_0_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2284-19_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2284-19_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2284-19_0_4_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_2284-19_0_4_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_2284-19_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_2284-19_0_4_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_2284-19_0_4_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_2284-19_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2284-19_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2284-19_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_2284-19_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_2284-19_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_2284-19_0_4_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_2284-19_0_4_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_2284-19_0_4_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_2284-19_0_4_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_2284-19_0_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_2284-19_0_4_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_2284-19_0_4_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_2284-19_0_4_node_43 | 0.4 | n |  | TRUE
44 | bus_MV_379_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2284-19_0_4_load_0 | 0 | 0.0036961 | 0.00092634 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2284-19_0_4_load_1 | 1 | 0.008565 | 0.0021466 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2284-19_0_4_load_30 | 7 | 0.0018335 | 0.00045952 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2284-19_0_4_load_14 | 8 | 0.012309 | 0.0030849 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2284-19_0_4_load_36 | 9 | 0.0018333 | 0.00045947 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2284-19_0_4_load_18 | 14 | 0.0096933 | 0.0024294 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2284-19_0_4_load_28 | 16 | 0.007639 | 0.0019145 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2284-19_0_4_load_6 | 17 | 0.030832 | 0.0077272 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2284-19_0_4_load_8 | 19 | 0.0090488 | 0.0022678 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2284-19_0_4_load_31 | 20 | 0.0018335 | 0.00045952 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2284-19_0_4_load_32 | 21 | 0.0018335 | 0.00045952 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2284-19_0_4_load_10 | 22 | 0.018314 | 0.00459 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2284-19_0_4_load_11 | 23 | 0.001489 | 0.00037318 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2284-19_0_4_load_12 | 24 | 0.0077025 | 0.0019304 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2284-19_0_4_load_13 | 25 | 0.0010086 | 0.00025278 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2284-19_0_4_load_20 | 26 | 0.0010085 | 0.00025276 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2284-19_0_4_load_35 | 27 | 0.0010079 | 0.00025261 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2284-19_0_4_load_19 | 28 | 0.0044365 | 0.0011119 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2284-19_0_4_load_29 | 29 | 0.007248 | 0.0018165 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2284-19_0_4_load_34 | 30 | 0.0018326 | 0.00045929 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2284-19_0_4_load_21 | 31 | 0.00083726 | 0.00020984 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2284-19_0_4_load_22 | 32 | 0.00088333 | 0.00022138 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2284-19_0_4_load_24 | 33 | 0.00089746 | 0.00022493 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2284-19_0_4_load_26 | 34 | 0.0010179 | 0.00025511 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2284-19_0_4_load_27 | 35 | 0.0043202 | 0.0010828 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2284-19_0_4_load_37 | 36 | 0.001009 | 0.00025288 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2284-19_0_4_load_33 | 37 | 0.0018342 | 0.0004597 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2284-19_0_4_load_38 | 38 | 0.0010079 | 0.00025261 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2284-19_0_4_load_39 | 39 | 0.0010086 | 0.00025278 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2284-19_0_4_load_40 | 40 | 0.001009 | 0.00025288 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2284-19_0_4_load_41 | 41 | 0.0010079 | 0.00025261 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2284-19_0_4_load_42 | 42 | 0.001009 | 0.00025288 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2284-19_0_4_load_43 | 43 | 0.0034354 | 0.00086098 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2284-19_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.035354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_2284-19_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.056053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_2284-19_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.036677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_2284-19_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.087356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_2284-19_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.22188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_2284-19_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.034499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2284-19_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.04805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_2284-19_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.018791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2284-19_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.084988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2284-19_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.060516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2284-19_0_4_line_10 | NAYY 4x150 SE | 7 | 11 | 0.013995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_2284-19_0_4_line_11 | NAYY 4x150 SE | 8 | 15 | 0.046519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2284-19_0_4_line_12 | NAYY 4x150 SE | 9 | 36 | 0.021859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2284-19_0_4_line_13 | NAYY 4x150 SE | 10 | 31 | 0.10737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2284-19_0_4_line_14 | NAYY 4x150 SE | 11 | 20 | 0.0078189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_2284-19_0_4_line_15 | NAYY 4x150 SE | 11 | 18 | 0.011989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2284-19_0_4_line_16 | NAYY 4x150 SE | 12 | 13 | 0.084973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2284-19_0_4_line_17 | NAYY 4x150 SE | 12 | 14 | 0.031987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2284-19_0_4_line_18 | NAYY 4x150 SE | 12 | 15 | 0.007092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2284-19_0_4_line_19 | NAYY 4x150 SE | 13 | 16 | 0.0033772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2284-19_0_4_line_20 | NAYY 4x150 SE | 14 | 28 | 0.023009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2284-19_0_4_line_21 | NAYY 4x150 SE | 16 | 29 | 0.026397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2284-19_0_4_line_22 | NAYY 4x150 SE | 17 | 18 | 0.061094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2284-19_0_4_line_23 | NAYY 4x150 SE | 17 | 19 | 0.02145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2284-19_0_4_line_24 | NAYY 4x150 SE | 20 | 21 | 0.021595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_2284-19_0_4_line_25 | NAYY 4x150 SE | 21 | 37 | 0.021902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_2284-19_0_4_line_26 | NAYY 4x150 SE | 22 | 23 | 0.031131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2284-19_0_4_line_27 | NAYY 4x150 SE | 22 | 24 | 0.027541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2284-19_0_4_line_28 | NAYY 4x150 SE | 23 | 25 | 0.01729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2284-19_0_4_line_29 | NAYY 4x150 SE | 25 | 26 | 0.019622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2284-19_0_4_line_30 | NAYY 4x150 SE | 26 | 27 | 0.019574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_2284-19_0_4_line_31 | NAYY 4x150 SE | 27 | 30 | 0.019509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_2284-19_0_4_line_32 | NAYY 4x150 SE | 30 | 37 | 0.021958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_2284-19_0_4_line_33 | NAYY 4x150 SE | 31 | 32 | 0.021357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2284-19_0_4_line_34 | NAYY 4x150 SE | 32 | 33 | 0.022497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2284-19_0_4_line_35 | NAYY 4x150 SE | 33 | 34 | 0.023191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2284-19_0_4_line_36 | NAYY 4x150 SE | 34 | 35 | 0.0022166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2284-19_0_4_line_37 | NAYY 4x150 SE | 36 | 38 | 0.021676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2284-19_0_4_line_38 | NAYY 4x150 SE | 38 | 39 | 0.019405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2284-19_0_4_line_39 | NAYY 4x150 SE | 39 | 40 | 0.019851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2284-19_0_4_line_40 | NAYY 4x150 SE | 40 | 41 | 0.02241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2284-19_0_4_line_41 | NAYY 4x150 SE | 41 | 42 | 0.017564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2284-19_0_4_line_42 | NAYY 4x150 SE | 42 | 43 | 0.019705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2284-19_0_4_trafo_20 | 0.25 MVA 20/0.4 kV | 44 | 26 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2575538.0901 | 1201273.9132 | 2575536.6018 | 1201277.3724 | 2575531.3709 | 1201287.9664 | 2575527.3614 | 1201293.8972 | 2575523.6328 | 1201297.8035 | 2575518.8374 | 1201301.403 | 2575517.7084 | 1201301.86
1 | 2575527.3792 | 1201226.06 | 2575537.8528 | 1201233.61 | 2575540.3594 | 1201236.0788 | 2575541.7299 | 1201238.0632 | 2575542.7432 | 1201240.1601 | 2575543.4593 | 1201242.1583 | 2575543.9748 | 1201245.3802 | 2575544.2822 | 1201249.7924 | 2575543.7497 | 1201255.4088 | 2575542.699 | 1201260.8828 | 2575541.1252 | 1201266.8592 | 2575538.0901 | 1201273.9132
2 | 2575493.6879 | 1201284.1526 | 2575493.3405 | 1201288.5009 | 2575494.0177 | 1201292.1445 | 2575495.4144 | 1201294.9403 | 2575497.5877 | 1201297.7996 | 2575500.4663 | 1201300.0334 | 2575504.2265 | 1201301.9745 | 2575507.7099 | 1201303.2164 | 2575511.4716 | 1201303.6568 | 2575514.4532 | 1201303.1776 | 2575517.7084 | 1201301.86
3 | 2575527.3792 | 1201226.06 | 2575531.8024 | 1201222.6288 | 2575551.6292 | 1201218.8564 | 2575574.3303 | 1201253.3377 | 2575580.0362 | 1201262.0079 | 2575585.6335 | 1201270.1894
4 | 2575414.3215 | 1201476.1849 | 2575420.81 | 1201467.9759 | 2575415.3184 | 1201461.4283 | 2575407.3065 | 1201456.4698 | 2575417.9547 | 1201432.6683 | 2575440.9085 | 1201384.5695 | 2575464.7176 | 1201335.211 | 2575486.8024 | 1201290.2954 | 2575493.6879 | 1201284.1526
5 | 2575585.6335 | 1201270.1894 | 2575589.1843 | 1201274.8885 | 2575598.3442 | 1201285.0899 | 2575607.2449 | 1201297.0377
6 | 2575585.6335 | 1201270.1894 | 2575582.3939 | 1201274.5829 | 2575579.9003 | 1201278.9733 | 2575565.2334 | 1201313.5324
7 | 2575414.3215 | 1201476.1849 | 2575423.5581 | 1201484.6959 | 2575428.3387 | 1201488.693
8 | 2575607.2449 | 1201297.0377 | 2575574.0009 | 1201375.2545
9 | 2575649.2236 | 1201340.6897 | 2575623.287 | 1201315.1152 | 2575613.3162 | 1201303.8832 | 2575607.2449 | 1201297.0377
10 | 2575559.7659 | 1201326.4152 | 2575565.2334 | 1201313.5324
11 | 2575465.125 | 1201517.0644 | 2575450.9985 | 1201507.6397 | 2575428.3387 | 1201488.693
12 | 2575574.0009 | 1201375.2545 | 2575565.4506 | 1201395.3718
13 | 2575649.2236 | 1201340.6897 | 2575646.5477 | 1201347.0375 | 2575607.5541 | 1201439.6451
14 | 2575559.7659 | 1201326.4152 | 2575556.6507 | 1201333.5867
15 | 2575559.7659 | 1201326.4152 | 2575550.1011 | 1201319.2843
16 | 2575471.5232 | 1201520.1619 | 2575518.8312 | 1201542.1792 | 2575544.4959 | 1201551.7456 | 2575546.515 | 1201546.7346
17 | 2575471.5232 | 1201520.1619 | 2575485.9608 | 1201491.6183
18 | 2575465.125 | 1201517.0644 | 2575471.5232 | 1201520.1619
19 | 2575546.515 | 1201546.7346 | 2575549.7006 | 1201547.856
20 | 2575506.6353 | 1201496.9824 | 2575486.8558 | 1201489.8488 | 2575485.9608 | 1201491.6183
21 | 2575549.7006 | 1201547.856 | 2575574.5994 | 1201556.6212
22 | 2575550.1011 | 1201319.2843 | 2575545.9749 | 1201322.7365 | 2575540.1175 | 1201327.1963 | 2575525.6815 | 1201335.1155 | 2575517.0738 | 1201340.754 | 2575509.7278 | 1201347.8214 | 2575505.1004 | 1201353.388 | 2575502.8361 | 1201356.8831
23 | 2575493.1986 | 1201376.016 | 2575500.7819 | 1201360.0538 | 2575502.8361 | 1201356.8831
24 | 2575556.6507 | 1201333.5867 | 2575548.0468 | 1201353.3933
25 | 2575548.0468 | 1201353.3933 | 2575539.3206 | 1201373.4816
26 | 2575471.3725 | 1201451.8044 | 2575500.2939 | 1201463.3235 | 2575500.2939 | 1201463.3235
27 | 2575445.7866 | 1201441.6139 | 2575471.3725 | 1201451.8044
28 | 2575507.1826 | 1201447.4652 | 2575500.2939 | 1201463.3235
29 | 2575515.0005 | 1201429.4678 | 2575507.1826 | 1201447.4652
30 | 2575522.7993 | 1201411.5146 | 2575515.0005 | 1201429.4678
31 | 2575530.5721 | 1201393.6212 | 2575522.7993 | 1201411.5146
32 | 2575539.3206 | 1201373.4816 | 2575530.5721 | 1201393.6212
33 | 2575599.2662 | 1201459.3285 | 2575607.5541 | 1201439.6451
34 | 2575599.2662 | 1201459.3285 | 2575590.536 | 1201480.0624
35 | 2575590.536 | 1201480.0624 | 2575581.5365 | 1201501.4357
36 | 2575581.5365 | 1201501.4357 | 2575580.6764 | 1201503.4785
37 | 2575565.4506 | 1201395.3718 | 2575556.9719 | 1201415.3205
38 | 2575556.9719 | 1201415.3205 | 2575549.3817 | 1201433.179
39 | 2575541.6166 | 1201451.4486 | 2575549.3817 | 1201433.179
40 | 2575541.6166 | 1201451.4486 | 2575538.0673 | 1201459.7995 | 2575538.0832 | 1201463.6682 | 2575537.7125 | 1201471.6074 | 2575537.3624 | 1201473.0858
41 | 2575531.0166 | 1201489.415 | 2575536.5081 | 1201476.6929 | 2575537.3624 | 1201473.0858
42 | 2575531.0166 | 1201489.415 | 2575523.2075 | 1201507.5064

## bus_geodata
| x | y | coords
0 | 2575538.0901 | 1201273.9132
1 | 2575517.7084 | 1201301.86
2 | 2575527.3792 | 1201226.06
3 | 2575493.6879 | 1201284.1526
4 | 2575585.6335 | 1201270.1894
5 | 2575414.3215 | 1201476.1849
6 | 2575607.2449 | 1201297.0377
7 | 2575565.2334 | 1201313.5324
8 | 2575428.3387 | 1201488.693
9 | 2575574.0009 | 1201375.2545
10 | 2575649.2236 | 1201340.6897
11 | 2575559.7659 | 1201326.4152
12 | 2575471.5232 | 1201520.1619
13 | 2575546.515 | 1201546.7346
14 | 2575485.9608 | 1201491.6183
15 | 2575465.125 | 1201517.0644
16 | 2575549.7006 | 1201547.856
17 | 2575502.8361 | 1201356.8831
18 | 2575550.1011 | 1201319.2843
19 | 2575493.1986 | 1201376.016
20 | 2575556.6507 | 1201333.5867
21 | 2575548.0468 | 1201353.3933
22 | 2575471.3725 | 1201451.8044
23 | 2575500.2939 | 1201463.3235
24 | 2575445.7866 | 1201441.6139
25 | 2575507.1826 | 1201447.4652
26 | 2575515.0005 | 1201429.4678
27 | 2575522.7993 | 1201411.5146
28 | 2575506.6353 | 1201496.9824
29 | 2575574.5994 | 1201556.6212
30 | 2575530.5721 | 1201393.6212
31 | 2575607.5541 | 1201439.6451
32 | 2575599.2662 | 1201459.3285
33 | 2575590.536 | 1201480.0624
34 | 2575581.5365 | 1201501.4357
35 | 2575580.6764 | 1201503.4785
36 | 2575565.4506 | 1201395.3718
37 | 2575539.3206 | 1201373.4816
38 | 2575556.9719 | 1201415.3205
39 | 2575549.3817 | 1201433.179
40 | 2575541.6166 | 1201451.4486
41 | 2575537.3624 | 1201473.0858
42 | 2575531.0166 | 1201489.415
43 | 2575523.2075 | 1201507.5064
44 | 2575445.7866 | 1201441.6139

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98759 | -0.08658 | 0.0036961 | 0.00092634
1 | 0.98673 | -0.092612 | 0.008565 | 0.0021466
2 | 0.98905 | -0.076332 | 0 | 0
3 | 0.98599 | -0.097803 | 0 | 0
4 | 0.99132 | -0.060415 | 0 | 0
5 | 0.97929 | -0.14524 | 0 | 0
6 | 0.99036 | -0.067192 | 0 | 0
7 | 0.99302 | -0.048554 | 0.0018335 | 0.00045952
8 | 0.97816 | -0.15334 | 0.012309 | 0.0030849
9 | 0.98897 | -0.07701 | 0.0018333 | 0.00045947
10 | 0.98967 | -0.072107 | 0 | 0
11 | 0.99352 | -0.04502 | 0 | 0
12 | 0.97588 | -0.16961 | 0 | 0
13 | 0.97403 | -0.1829 | 0 | 0
14 | 0.97522 | -0.17435 | 0.0096933 | 0.0024294
15 | 0.97618 | -0.16745 | 0 | 0
16 | 0.97396 | -0.18343 | 0.007639 | 0.0019145
17 | 0.98932 | -0.074618 | 0.030832 | 0.0077272
18 | 0.99283 | -0.049858 | 0 | 0
19 | 0.98904 | -0.076598 | 0.0090488 | 0.0022678
20 | 0.99395 | -0.041996 | 0.0018335 | 0.00045952
21 | 0.99517 | -0.033527 | 0.0018335 | 0.00045952
22 | 0.99736 | -0.018467 | 0.018314 | 0.00459
23 | 0.99852 | -0.010349 | 0.001489 | 0.00037318
24 | 0.99706 | -0.020596 | 0.0077025 | 0.0019304
25 | 0.9992 | -0.0055902 | 0.0010086 | 0.00025278
26 | 1 | 0 | -0.15415 | -0.038659
27 | 0.99884 | -0.0080286 | 0.0010079 | 0.00025261
28 | 0.97507 | -0.17542 | 0.0044365 | 0.0011119
29 | 0.97368 | -0.18544 | 0.007248 | 0.0018165
30 | 0.99769 | -0.015983 | 0.0018326 | 0.00045929
31 | 0.98843 | -0.080835 | 0.00083726 | 0.00020984
32 | 0.98821 | -0.08239 | 0.00088333 | 0.00022138
33 | 0.98801 | -0.083825 | 0.00089746 | 0.00022493
34 | 0.98783 | -0.085091 | 0.0010179 | 0.00025511
35 | 0.98782 | -0.085189 | 0.0043202 | 0.0010828
36 | 0.98867 | -0.07913 | 0.001009 | 0.00025288
37 | 0.99642 | -0.024823 | 0.0018342 | 0.0004597
38 | 0.98841 | -0.081009 | 0.0010079 | 0.00025261
39 | 0.9882 | -0.082492 | 0.0010086 | 0.00025278
40 | 0.98801 | -0.083804 | 0.001009 | 0.00025288
41 | 0.98784 | -0.085055 | 0.0010079 | 0.00025261
42 | 0.98773 | -0.085854 | 0.001009 | 0.00025288
43 | 0.98763 | -0.086547 | 0.0034354 | 0.00086098
44 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.050391 | 0.012685 | -0.050349 | -0.01267 | 4.2414e-05 | 1.4957e-05 | 0.075945 | 0.075946 | 0.075946 | 0.98759 | -0.08658 | 0.98673 | -0.092612 | 9.376
1 | -0.054087 | -0.013611 | 0.054165 | 0.013639 | 7.7469e-05 | 2.7641e-05 | 0.081514 | 0.081514 | 0.081514 | 0.98759 | -0.08658 | 0.98905 | -0.076332 | 10.0635
2 | 0.041784 | 0.010523 | -0.041754 | -0.010513 | 3.0308e-05 | 1.0252e-05 | 0.06303 | 0.06303 | 0.06303 | 0.98673 | -0.092612 | 0.98599 | -0.097803 | 7.7815
3 | -0.054165 | -0.013639 | 0.054286 | 0.013682 | 0.00012073 | 4.3063e-05 | 0.081514 | 0.081512 | 0.081514 | 0.98905 | -0.076332 | 0.99132 | -0.060415 | 10.0634
4 | 0.041754 | 0.010513 | -0.041479 | -0.010413 | 0.00027503 | 0.00010016 | 0.06303 | 0.063032 | 0.063032 | 0.98599 | -0.097803 | 0.97929 | -0.14524 | 11.6726
5 | 0.019338 | 0.0048485 | -0.01932 | -0.004842 | 1.814e-05 | 6.5325e-06 | 0.029028 | 0.029028 | 0.029028 | 0.99132 | -0.060415 | 0.99036 | -0.067192 | 10.7512
6 | -0.073624 | -0.01853 | 0.073746 | 0.018576 | 0.00012212 | 4.5109e-05 | 0.11054 | 0.11054 | 0.11054 | 0.99132 | -0.060415 | 0.99302 | -0.048554 | 13.647
7 | 0.041479 | 0.010413 | -0.041432 | -0.010395 | 4.6587e-05 | 1.7682e-05 | 0.063032 | 0.063032 | 0.063032 | 0.97929 | -0.14524 | 0.97816 | -0.15334 | 23.3452
8 | 0.011345 | 0.0028438 | -0.01133 | -0.0028389 | 1.541e-05 | 4.8349e-06 | 0.017046 | 0.017046 | 0.017046 | 0.99036 | -0.067192 | 0.98897 | -0.07701 | 6.3135
9 | 0.007975 | 0.0019982 | -0.0079696 | -0.0019969 | 5.4218e-06 | 1.3072e-06 | 0.011982 | 0.011983 | 0.011983 | 0.99036 | -0.067192 | 0.98967 | -0.072107 | 4.438
10 | -0.075579 | -0.019035 | 0.075617 | 0.019049 | 3.7359e-05 | 1.3826e-05 | 0.11329 | 0.11329 | 0.11329 | 0.99302 | -0.048554 | 0.99352 | -0.04502 | 13.9861
11 | 0.029123 | 0.0073103 | -0.029066 | -0.007289 | 5.6986e-05 | 2.1335e-05 | 0.044307 | 0.044307 | 0.044307 | 0.97816 | -0.15334 | 0.97618 | -0.16745 | 16.4102
12 | 0.0094963 | 0.0023794 | -0.0094935 | -0.0023787 | 2.7846e-06 | 7.906e-07 | 0.014288 | 0.014288 | 0.014288 | 0.98897 | -0.07701 | 0.98867 | -0.07913 | 5.2919
13 | 0.0079696 | 0.0019969 | -0.00796 | -0.0019946 | 9.6202e-06 | 2.3221e-06 | 0.011983 | 0.011983 | 0.011983 | 0.98967 | -0.072107 | 0.98843 | -0.080835 | 4.4382
14 | -0.11566 | -0.029107 | 0.11571 | 0.029125 | 4.8829e-05 | 1.8476e-05 | 0.17327 | 0.17327 | 0.17327 | 0.99352 | -0.04502 | 0.99395 | -0.041996 | 21.3919
15 | 0.040047 | 0.010058 | -0.04002 | -0.010048 | 2.692e-05 | 1.0199e-05 | 0.059987 | 0.059987 | 0.059987 | 0.99352 | -0.04502 | 0.99283 | -0.049858 | 22.2174
16 | 0.014917 | 0.0037413 | -0.01489 | -0.0037318 | 2.7436e-05 | 9.4926e-06 | 0.022747 | 0.022747 | 0.022747 | 0.97588 | -0.16961 | 0.97403 | -0.1829 | 8.425
17 | 0.01414 | 0.0035444 | -0.014131 | -0.0035412 | 9.2786e-06 | 3.1693e-06 | 0.02156 | 0.021561 | 0.021561 | 0.97588 | -0.16961 | 0.97522 | -0.17435 | 7.9854
18 | -0.029057 | -0.0072858 | 0.029066 | 0.007289 | 8.6877e-06 | 3.2528e-06 | 0.044307 | 0.044307 | 0.044307 | 0.97588 | -0.16961 | 0.97618 | -0.16745 | 16.4102
19 | 0.01489 | 0.0037318 | -0.014889 | -0.0037315 | 1.0904e-06 | 3.7737e-07 | 0.022747 | 0.022747 | 0.022747 | 0.97403 | -0.1829 | 0.97396 | -0.18343 | 8.425
20 | 0.0044372 | 0.0011119 | -0.0044365 | -0.0011119 | 6.5813e-07 | -3.3921e-08 | 0.0067703 | 0.0067704 | 0.0067704 | 0.97522 | -0.17435 | 0.97507 | -0.17542 | 2.5076
21 | 0.00725 | 0.001817 | -0.007248 | -0.0018165 | 2.0209e-06 | 4.4886e-07 | 0.011077 | 0.011077 | 0.011077 | 0.97396 | -0.18343 | 0.97368 | -0.18544 | 4.1025
22 | -0.039883 | -0.0099957 | 0.04002 | 0.010048 | 0.00013718 | 5.1975e-05 | 0.059987 | 0.059987 | 0.059987 | 0.98932 | -0.074618 | 0.99283 | -0.049858 | 22.2175
23 | 0.0090513 | 0.0022685 | -0.0090488 | -0.0022678 | 2.4807e-06 | 6.7876e-07 | 0.013614 | 0.013614 | 0.013614 | 0.98932 | -0.074618 | 0.98904 | -0.076598 | 5.0422
24 | -0.11755 | -0.029585 | 0.11769 | 0.029637 | 0.00013916 | 5.2684e-05 | 0.17602 | 0.17602 | 0.17602 | 0.99395 | -0.041996 | 0.99517 | -0.033527 | 21.7307
25 | -0.11952 | -0.030097 | 0.11966 | 0.030152 | 0.00014557 | 5.5135e-05 | 0.17876 | 0.17876 | 0.17876 | 0.99517 | -0.033527 | 0.99642 | -0.024823 | 22.0691
26 | -0.026019 | -0.006521 | 0.026048 | 0.0065318 | 2.9273e-05 | 1.0852e-05 | 0.038819 | 0.038819 | 0.038819 | 0.99736 | -0.018467 | 0.99852 | -0.010349 | 14.3775
27 | 0.0077048 | 0.0019309 | -0.0077025 | -0.0019304 | 2.2709e-06 | 5.141e-07 | 0.011495 | 0.011495 | 0.011495 | 0.99736 | -0.018467 | 0.99706 | -0.020596 | 4.2575
28 | -0.027537 | -0.006905 | 0.027556 | 0.0069118 | 1.817e-05 | 6.762e-06 | 0.041038 | 0.041038 | 0.041038 | 0.99852 | -0.010349 | 0.9992 | -0.0055902 | 15.1993
29 | -0.028564 | -0.0071645 | 0.028586 | 0.0071728 | 2.2158e-05 | 8.265e-06 | 0.04254 | 0.04254 | 0.04254 | 0.9992 | -0.0055902 | 1 | 0 | 15.7556
30 | 0.12477 | 0.031486 | -0.12463 | -0.031433 | 0.00014045 | 5.325e-05 | 0.18573 | 0.18573 | 0.18573 | 1 | 0 | 0.99884 | -0.0080286 | 22.93
31 | 0.12362 | 0.03118 | -0.12348 | -0.031128 | 0.00013773 | 5.2207e-05 | 0.18423 | 0.18423 | 0.18423 | 0.99884 | -0.0080286 | 0.99769 | -0.015983 | 22.7447
32 | 0.12165 | 0.030669 | -0.1215 | -0.030612 | 0.00015045 | 5.7007e-05 | 0.1815 | 0.1815 | 0.1815 | 0.99769 | -0.015983 | 0.99642 | -0.024823 | 22.4073
33 | 0.0071227 | 0.0017847 | -0.0071212 | -0.0017844 | 1.5322e-06 | 3.1564e-07 | 0.010723 | 0.010723 | 0.010723 | 0.98843 | -0.080835 | 0.98821 | -0.08239 | 3.9714
34 | 0.0062378 | 0.001563 | -0.0062366 | -0.0015628 | 1.2385e-06 | 1.8816e-07 | 0.0093926 | 0.0093927 | 0.0093927 | 0.98821 | -0.08239 | 0.98801 | -0.083825 | 3.4788
35 | 0.0053391 | 0.0013379 | -0.0053382 | -0.0013379 | 9.3568e-07 | 6.2937e-08 | 0.008041 | 0.0080411 | 0.0080411 | 0.98801 | -0.083825 | 0.98783 | -0.085091 | 2.9782
36 | 0.0043203 | 0.0010827 | -0.0043202 | -0.0010828 | 5.8579e-08 | -5.8459e-09 | 0.0065078 | 0.0065078 | 0.0065078 | 0.98783 | -0.085091 | 0.98782 | -0.085189 | 2.4103
37 | 0.0084845 | 0.0021258 | -0.0084823 | -0.0021252 | 2.2055e-06 | 5.7038e-07 | 0.012769 | 0.01277 | 0.01277 | 0.98867 | -0.07913 | 0.98841 | -0.081009 | 4.7295
38 | 0.0074744 | 0.0018726 | -0.0074728 | -0.0018722 | 1.5331e-06 | 3.4099e-07 | 0.011252 | 0.011252 | 0.011252 | 0.98841 | -0.081009 | 0.9882 | -0.082492 | 4.1675
39 | 0.0064642 | 0.0016195 | -0.0064631 | -0.0016193 | 1.1736e-06 | 1.9711e-07 | 0.0097335 | 0.0097336 | 0.0097336 | 0.9882 | -0.082492 | 0.98801 | -0.083804 | 3.605
40 | 0.005454 | 0.0013664 | -0.0054531 | -0.0013663 | 9.4348e-07 | 7.5935e-08 | 0.008214 | 0.0082141 | 0.0082141 | 0.98801 | -0.083804 | 0.98784 | -0.085055 | 3.0423
41 | 0.0044452 | 0.0011137 | -0.0044447 | -0.0011137 | 4.9137e-07 | -3.5836e-08 | 0.0066958 | 0.0066959 | 0.0066959 | 0.98784 | -0.085055 | 0.98773 | -0.085854 | 2.48
42 | 0.0034357 | 0.00086086 | -0.0034354 | -0.00086098 | 3.294e-07 | -1.2549e-07 | 0.0051758 | 0.0051759 | 0.0051759 | 0.98773 | -0.085854 | 0.98763 | -0.086547 | 1.917

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15516 | 0.038912

## res_load
| p_mw | q_mvar
0 | 0.0036961 | 0.00092634
1 | 0.008565 | 0.0021466
2 | 0.0018335 | 0.00045952
3 | 0.012309 | 0.0030849
4 | 0.0018333 | 0.00045947
5 | 0.0096933 | 0.0024294
6 | 0.007639 | 0.0019145
7 | 0.030832 | 0.0077272
8 | 0.0090488 | 0.0022678
9 | 0.0018335 | 0.00045952
10 | 0.0018335 | 0.00045952
11 | 0.018314 | 0.00459
12 | 0.001489 | 0.00037318
13 | 0.0077025 | 0.0019304
14 | 0.0010086 | 0.00025278
15 | 0.0010085 | 0.00025276
16 | 0.0010079 | 0.00025261
17 | 0.0044365 | 0.0011119
18 | 0.007248 | 0.0018165
19 | 0.0018326 | 0.00045929
20 | 0.00083726 | 0.00020984
21 | 0.00088333 | 0.00022138
22 | 0.00089746 | 0.00022493
23 | 0.0010179 | 0.00025511
24 | 0.0043202 | 0.0010828
25 | 0.001009 | 0.00025288
26 | 0.0018342 | 0.0004597
27 | 0.0010079 | 0.00025261
28 | 0.0010086 | 0.00025278
29 | 0.001009 | 0.00025288
30 | 0.0010079 | 0.00025261
31 | 0.001009 | 0.00025288
32 | 0.0034354 | 0.00086098

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1