## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2306-11_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2306-11_0_2_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2306-11_0_2_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_2306-11_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2306-11_0_2_node_15 | 0.4 | n |  | TRUE
5 | bus_LV_2306-11_0_2_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2306-11_0_2_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_2306-11_0_2_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_2306-11_0_2_node_35 | 0.4 | n |  | TRUE
9 | bus_LV_2306-11_0_2_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_2306-11_0_2_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_2306-11_0_2_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_2306-11_0_2_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_2306-11_0_2_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_2306-11_0_2_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2306-11_0_2_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2306-11_0_2_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_2306-11_0_2_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2306-11_0_2_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_2306-11_0_2_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_2306-11_0_2_node_37 | 0.4 | n |  | TRUE
21 | bus_LV_2306-11_0_2_node_36 | 0.4 | n |  | TRUE
22 | bus_LV_2306-11_0_2_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_2306-11_0_2_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_2306-11_0_2_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_2306-11_0_2_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_2306-11_0_2_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_2306-11_0_2_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_2306-11_0_2_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_2306-11_0_2_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2306-11_0_2_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_2306-11_0_2_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_2306-11_0_2_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2306-11_0_2_node_34 | 0.4 | n |  | TRUE
34 | bus_MV_119_1_node_105 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2306-11_0_2_load_0 | 0 | 0.0062965 | 0.001578 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2306-11_0_2_load_5 | 2 | 0.0025716 | 0.0006445 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2306-11_0_2_load_13 | 7 | 0.0060606 | 0.0015189 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2306-11_0_2_load_35 | 8 | 0.0049748 | 0.0012468 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2306-11_0_2_load_26 | 10 | 0.0033519 | 0.00084007 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2306-11_0_2_load_12 | 12 | 0.019026 | 0.0047683 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2306-11_0_2_load_6 | 13 | 0.022328 | 0.0055958 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2306-11_0_2_load_7 | 14 | 0.0074497 | 0.0018671 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2306-11_0_2_load_23 | 18 | 0.025338 | 0.0063503 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2306-11_0_2_load_31 | 19 | 0.0052174 | 0.0013076 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2306-11_0_2_load_37 | 20 | 0.0049826 | 0.0012488 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2306-11_0_2_load_36 | 21 | 0.0037496 | 0.00093973 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2306-11_0_2_load_30 | 23 | 0.020152 | 0.0050505 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2306-11_0_2_load_33 | 24 | 0.011008 | 0.0027588 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2306-11_0_2_load_39 | 26 | 0.0040199 | 0.0010075 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2306-11_0_2_load_25 | 27 | 0.012765 | 0.0031993 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2306-11_0_2_load_24 | 28 | 0.024731 | 0.0061983 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2306-11_0_2_load_17 | 29 | 0.005996 | 0.0015027 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2306-11_0_2_load_27 | 31 | 0.004763 | 0.0011937 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2306-11_0_2_load_34 | 33 | 0.02656 | 0.0066567 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2306-11_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.019707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2306-11_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.0014517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2306-11_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.036501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2306-11_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.025368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2306-11_0_2_line_4 | NAYY 4x150 SE | 4 | 8 | 0.011355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2306-11_0_2_line_5 | NAYY 4x150 SE | 4 | 9 | 0.012175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2306-11_0_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.007404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2306-11_0_2_line_7 | NAYY 4x150 SE | 5 | 7 | 0.0082169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2306-11_0_2_line_8 | NAYY 4x150 SE | 6 | 10 | 0.016892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2306-11_0_2_line_9 | NAYY 4x150 SE | 6 | 11 | 0.023269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2306-11_0_2_line_10 | NAYY 4x150 SE | 7 | 12 | 0.020742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2306-11_0_2_line_11 | NAYY 4x150 SE | 8 | 26 | 0.30802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2306-11_0_2_line_12 | NAYY 4x150 SE | 9 | 12 | 0.01994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2306-11_0_2_line_13 | NAYY 4x150 SE | 10 | 32 | 0.011637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2306-11_0_2_line_14 | NAYY 4x150 SE | 11 | 30 | 0.013062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2306-11_0_2_line_15 | NAYY 4x150 SE | 11 | 29 | 0.028801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2306-11_0_2_line_16 | NAYY 4x150 SE | 13 | 14 | 0.014896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2306-11_0_2_line_17 | NAYY 4x150 SE | 13 | 15 | 0.025349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2306-11_0_2_line_18 | NAYY 4x150 SE | 14 | 16 | 0.017782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2306-11_0_2_line_19 | NAYY 4x150 SE | 15 | 17 | 0.016098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2306-11_0_2_line_20 | NAYY 4x150 SE | 16 | 18 | 0.0049091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2306-11_0_2_line_21 | NAYY 4x150 SE | 16 | 19 | 0.040083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2306-11_0_2_line_22 | NAYY 4x150 SE | 17 | 20 | 0.004348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2306-11_0_2_line_23 | NAYY 4x150 SE | 17 | 21 | 0.01814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2306-11_0_2_line_24 | NAYY 4x150 SE | 18 | 22 | 0.019882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2306-11_0_2_line_25 | NAYY 4x150 SE | 19 | 23 | 0.028804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2306-11_0_2_line_26 | NAYY 4x150 SE | 22 | 29 | 0.014656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2306-11_0_2_line_27 | NAYY 4x150 SE | 23 | 25 | 0.0025987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2306-11_0_2_line_28 | NAYY 4x150 SE | 24 | 25 | 0.03318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2306-11_0_2_line_29 | NAYY 4x150 SE | 25 | 33 | 0.03024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2306-11_0_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.0018161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2306-11_0_2_line_31 | NAYY 4x150 SE | 28 | 32 | 0.024642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2306-11_0_2_line_32 | NAYY 4x150 SE | 30 | 31 | 0.029307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2306-11_0_2_trafo_23 | 0.25 MVA 20/0.4 kV | 34 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2586244.3436 | 1182722.0676 | 2586262.6483 | 1182729.3674
1 | 2586244.3436 | 1182722.0676 | 2586244.8593 | 1182720.7106
2 | 2586270.224 | 1182708.3453 | 2586254.3579 | 1182704.5021 | 2586252.6476 | 1182704.4727 | 2586251.3435 | 1182705.076 | 2586250.4751 | 1182705.934 | 2586244.8593 | 1182720.7106
3 | 2586275.9851 | 1182683.8194 | 2586274.7288 | 1182695.217 | 2586274.0333 | 1182698.2091 | 2586270.224 | 1182708.3453
4 | 2586275.9851 | 1182683.8194 | 2586268.6074 | 1182685.9931 | 2586265.2185 | 1182687.3865
5 | 2586275.9851 | 1182683.8194 | 2586279.0833 | 1182683.1675 | 2586283.4643 | 1182682.5904 | 2586288.0514 | 1182682.0018
6 | 2586341.6689 | 1182694.7741 | 2586334.9507 | 1182691.6212
7 | 2586334.9507 | 1182691.6212 | 2586327.4009 | 1182688.3781
8 | 2586341.6689 | 1182694.7741 | 2586347.5878 | 1182678.9528
9 | 2586362.7178 | 1182704.7643 | 2586358.5222 | 1182702.973 | 2586353.2876 | 1182700.8617 | 2586341.6689 | 1182694.7741
10 | 2586307.9385 | 1182681.3779 | 2586307.9385 | 1182681.3779 | 2586312.1932 | 1182682.3131 | 2586316.8539 | 1182683.8476 | 2586327.4009 | 1182688.3781
11 | 2586265.2185 | 1182687.3865 | 2586098.7439 | 1182428.2319
12 | 2586288.0514 | 1182682.0018 | 2586298.0356 | 1182681.1117 | 2586303.876 | 1182681.0538 | 2586307.9385 | 1182681.3779
13 | 2586353.0233 | 1182668.8347 | 2586349.9856 | 1182672.5436 | 2586347.5878 | 1182678.9528
14 | 2586357.7524 | 1182716.8486 | 2586362.7178 | 1182704.7643
15 | 2586362.7178 | 1182704.7643 | 2586367.0019 | 1182695.2274 | 2586372.7746 | 1182682.2631 | 2586374.5299 | 1182678.4973
16 | 2586420.9249 | 1182662.8963 | 2586408.7191 | 1182654.3571
17 | 2586440.822 | 1182678.5281 | 2586438.0597 | 1182675.8107 | 2586433.1869 | 1182671.6419 | 2586426.0443 | 1182666.4777 | 2586420.9249 | 1182662.8963
18 | 2586394.0194 | 1182644.3616 | 2586398.5085 | 1182647.6308 | 2586403.8763 | 1182651.2093 | 2586407.5922 | 1182653.5687 | 2586408.7191 | 1182654.3571
19 | 2586451.4161 | 1182690.6658 | 2586444.1512 | 1182682.0779 | 2586440.822 | 1182678.5281
20 | 2586394.0194 | 1182644.3616 | 2586391.0306 | 1182648.256
21 | 2586394.0194 | 1182644.3616 | 2586405.6726 | 1182632.0842 | 2586423.7453 | 1182617.6079
22 | 2586451.4161 | 1182690.6658 | 2586454.3022 | 1182693.9178
23 | 2586451.4161 | 1182690.6658 | 2586442.8273 | 1182697.4666 | 2586438.4206 | 1182703.1407
24 | 2586380.7215 | 1182665.2139 | 2586384.1425 | 1182658.8139 | 2586386.4313 | 1182654.7621 | 2586389.1477 | 1182650.7094 | 2586391.0306 | 1182648.256
25 | 2586423.7453 | 1182617.6079 | 2586438.1299 | 1182606.0858 | 2586446.5722 | 1182600.057
26 | 2586380.7215 | 1182665.2139 | 2586374.5299 | 1182678.4973
27 | 2586448.687 | 1182598.5467 | 2586446.5722 | 1182600.057
28 | 2586448.687 | 1182598.5467 | 2586452.0863 | 1182602.6745 | 2586454.2607 | 1182605.382 | 2586468.6988 | 1182622.458 | 2586470.2483 | 1182623.7203
29 | 2586448.687 | 1182598.5467 | 2586473.5119 | 1182581.2782
30 | 2586341.7961 | 1182644.8771 | 2586342.5667 | 1182646.5216
31 | 2586353.0233 | 1182668.8347 | 2586342.5667 | 1182646.5216
32 | 2586357.7524 | 1182716.8486 | 2586366.297 | 1182724.1328 | 2586372.5387 | 1182729.299 | 2586379.4443 | 1182734.3413 | 2586380.6702 | 1182735.0697

## bus_geodata
| x | y | coords
0 | 2586262.6483 | 1182729.3674
1 | 2586244.3436 | 1182722.0676
2 | 2586244.8593 | 1182720.7106
3 | 2586270.224 | 1182708.3453
4 | 2586275.9851 | 1182683.8194
5 | 2586334.9507 | 1182691.6212
6 | 2586341.6689 | 1182694.7741
7 | 2586327.4009 | 1182688.3781
8 | 2586265.2185 | 1182687.3865
9 | 2586288.0514 | 1182682.0018
10 | 2586347.5878 | 1182678.9528
11 | 2586362.7178 | 1182704.7643
12 | 2586307.9385 | 1182681.3779
13 | 2586420.9249 | 1182662.8963
14 | 2586408.7191 | 1182654.3571
15 | 2586440.822 | 1182678.5281
16 | 2586394.0194 | 1182644.3616
17 | 2586451.4161 | 1182690.6658
18 | 2586391.0306 | 1182648.256
19 | 2586423.7453 | 1182617.6079
20 | 2586454.3022 | 1182693.9178
21 | 2586438.4206 | 1182703.1407
22 | 2586380.7215 | 1182665.2139
23 | 2586446.5722 | 1182600.057
24 | 2586470.2483 | 1182623.7203
25 | 2586448.687 | 1182598.5467
26 | 2586098.7439 | 1182428.2319
27 | 2586341.7961 | 1182644.8771
28 | 2586342.5667 | 1182646.5216
29 | 2586374.5299 | 1182678.4973
30 | 2586357.7524 | 1182716.8486
31 | 2586380.6702 | 1182735.0697
32 | 2586353.0233 | 1182668.8347
33 | 2586473.5119 | 1182581.2782
34 | 2586394.0194 | 1182644.3616

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98489 | -0.10606 | 0.0062965 | 0.001578
1 | 0.98506 | -0.10478 | 0 | 0
2 | 0.98508 | -0.10469 | 0.0025716 | 0.0006445
3 | 0.98555 | -0.10136 | 0 | 0
4 | 0.98587 | -0.099045 | 0 | 0
5 | 0.98832 | -0.081691 | 0 | 0
6 | 0.98878 | -0.07844 | 0 | 0
7 | 0.98781 | -0.085302 | 0.0060606 | 0.0015189
8 | 0.98572 | -0.1001 | 0.0049748 | 0.0012468
9 | 0.98619 | -0.096807 | 0 | 0
10 | 0.98778 | -0.085492 | 0.0033519 | 0.00084007
11 | 0.9916 | -0.05858 | 0 | 0
12 | 0.9867 | -0.093146 | 0.019026 | 0.0047683
13 | 0.99765 | -0.016464 | 0.022328 | 0.0055958
14 | 0.99831 | -0.011827 | 0.0074497 | 0.0018671
15 | 0.99733 | -0.018686 | 0 | 0
16 | 0.99929 | -0.0049749 | 0 | 0
17 | 0.99713 | -0.020097 | 0 | 0
18 | 1 | 0 | -0.19855 | -0.049784
19 | 0.99566 | -0.030285 | 0.0052174 | 0.0013076
20 | 0.9971 | -0.020315 | 0.0049826 | 0.0012488
21 | 0.99703 | -0.02078 | 0.0037496 | 0.00093973
22 | 0.99728 | -0.018826 | 0 | 0
23 | 0.99328 | -0.047065 | 0.020152 | 0.0050505
24 | 0.99261 | -0.051751 | 0.011008 | 0.0027588
25 | 0.99314 | -0.048053 | 0 | 0
26 | 0.98393 | -0.11288 | 0.0040199 | 0.0010075
27 | 0.98578 | -0.099673 | 0.012765 | 0.0031993
28 | 0.98581 | -0.099435 | 0.024731 | 0.0061983
29 | 0.99528 | -0.032769 | 0.005996 | 0.0015027
30 | 0.99151 | -0.059212 | 0 | 0
31 | 0.99131 | -0.060629 | 0.004763 | 0.0011937
32 | 0.98715 | -0.089958 | 0 | 0
33 | 0.99198 | -0.05619 | 0.02656 | 0.0066567
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0062965 | -0.001578 | 0.0062976 | 0.0015782 | 1.1128e-06 | 1.7719e-07 | 0.009513 | 0.009513 | 0.009513 | 0.98489 | -0.10606 | 0.98506 | -0.10478 | 3.5233
1 | -0.0062976 | -0.0015782 | 0.0062977 | 0.0015782 | 8.1976e-08 | 1.3049e-08 | 0.009513 | 0.0095129 | 0.009513 | 0.98506 | -0.10478 | 0.98508 | -0.10469 | 3.5233
2 | -0.0088693 | -0.0022227 | 0.0088734 | 0.0022238 | 4.0882e-06 | 1.1075e-06 | 0.013397 | 0.013397 | 0.013397 | 0.98508 | -0.10469 | 0.98555 | -0.10136 | 4.962
3 | -0.0088734 | -0.0022238 | 0.0088762 | 0.0022246 | 2.8412e-06 | 7.6941e-07 | 0.013397 | 0.013397 | 0.013397 | 0.98555 | -0.10136 | 0.98587 | -0.099045 | 4.962
4 | 0.0090032 | 0.0022535 | -0.0090019 | -0.0022531 | 1.3082e-06 | 3.584e-07 | 0.013588 | 0.013588 | 0.013588 | 0.98587 | -0.099045 | 0.98572 | -0.1001 | 5.0325
5 | -0.017879 | -0.0044781 | 0.017885 | 0.0044801 | 5.5322e-06 | 1.9725e-06 | 0.026985 | 0.026985 | 0.026985 | 0.98587 | -0.099045 | 0.98619 | -0.096807 | 9.9944
6 | -0.043042 | -0.010794 | 0.043061 | 0.010801 | 1.9404e-05 | 7.3681e-06 | 0.064807 | 0.064806 | 0.064807 | 0.98832 | -0.081691 | 0.98878 | -0.07844 | 24.0024
7 | 0.043042 | 0.010794 | -0.04302 | -0.010786 | 2.1534e-05 | 8.1772e-06 | 0.064807 | 0.064807 | 0.064807 | 0.98832 | -0.081691 | 0.98781 | -0.085302 | 24.0024
8 | 0.040962 | 0.01028 | -0.040922 | -0.010265 | 4.0061e-05 | 1.5191e-05 | 0.061649 | 0.061649 | 0.061649 | 0.98878 | -0.07844 | 0.98778 | -0.085492 | 22.8328
9 | -0.084023 | -0.021082 | 0.084255 | 0.021171 | 0.00023219 | 8.9003e-05 | 0.12646 | 0.12645 | 0.12646 | 0.98878 | -0.07844 | 0.9916 | -0.05858 | 46.8352
10 | 0.03696 | 0.0092668 | -0.03692 | -0.0092516 | 4.0122e-05 | 1.5166e-05 | 0.055677 | 0.055677 | 0.055677 | 0.98781 | -0.085302 | 0.9867 | -0.093146 | 20.6211
11 | 0.004027 | 0.0010063 | -0.0040199 | -0.0010075 | 7.102e-06 | -1.1877e-06 | 0.006078 | 0.0060794 | 0.0060794 | 0.98572 | -0.1001 | 0.98393 | -0.11288 | 2.2516
12 | -0.017885 | -0.0044801 | 0.017894 | 0.0044833 | 9.0604e-06 | 3.2302e-06 | 0.026985 | 0.026985 | 0.026985 | 0.98619 | -0.096807 | 0.9867 | -0.093146 | 9.9944
13 | 0.03757 | 0.0094251 | -0.037546 | -0.0094164 | 2.3262e-05 | 8.7982e-06 | 0.056599 | 0.056599 | 0.056599 | 0.98778 | -0.085492 | 0.98715 | -0.089958 | 20.9627
14 | 0.0047643 | 0.0011937 | -0.0047639 | -0.0011937 | 4.1661e-07 | -8.2456e-09 | 0.0071494 | 0.0071494 | 0.0071494 | 0.9916 | -0.05858 | 0.99151 | -0.059212 | 2.6479
15 | -0.08902 | -0.022364 | 0.08934 | 0.022487 | 0.0003208 | 0.00012301 | 0.1336 | 0.1336 | 0.1336 | 0.9916 | -0.05858 | 0.99528 | -0.032769 | 49.4831
16 | -0.031065 | -0.0077854 | 0.031085 | 0.0077928 | 1.9955e-05 | 7.4804e-06 | 0.046334 | 0.046334 | 0.046334 | 0.99765 | -0.016464 | 0.99831 | -0.011827 | 17.1606
17 | 0.0087371 | 0.0021895 | -0.0087344 | -0.0021888 | 2.6862e-06 | 7.0227e-07 | 0.013031 | 0.013032 | 0.013032 | 0.99765 | -0.016464 | 0.99733 | -0.018686 | 4.8265
18 | -0.038534 | -0.0096599 | 0.038571 | 0.0096738 | 3.6606e-05 | 1.3846e-05 | 0.057438 | 0.057438 | 0.057438 | 0.99831 | -0.011827 | 0.99929 | -0.0049749 | 21.2732
19 | 0.0087344 | 0.0021888 | -0.0087327 | -0.0021884 | 1.7059e-06 | 4.4609e-07 | 0.013032 | 0.013032 | 0.013032 | 0.99733 | -0.018686 | 0.99713 | -0.020097 | 4.8265
20 | -0.10191 | -0.025599 | 0.10198 | 0.025626 | 7.0556e-05 | 2.7073e-05 | 0.15177 | 0.15177 | 0.15177 | 0.99929 | -0.0049749 | 1 | 0 | 56.2099
21 | 0.063335 | 0.015925 | -0.063113 | -0.01584 | 0.00022256 | 8.5075e-05 | 0.094329 | 0.094329 | 0.094329 | 0.99929 | -0.0049749 | 0.99566 | -0.030285 | 34.9368
22 | 0.0049828 | 0.0012488 | -0.0049826 | -0.0012488 | 1.5001e-07 | 9.8315e-10 | 0.0074358 | 0.0074358 | 0.0074358 | 0.99713 | -0.020097 | 0.9971 | -0.020315 | 2.754
23 | 0.0037499 | 0.00093963 | -0.0037496 | -0.00093973 | 3.5446e-07 | -1.0026e-07 | 0.0055959 | 0.005596 | 0.005596 | 0.99713 | -0.020097 | 0.99703 | -0.02078 | 2.0726
24 | 0.095774 | 0.024158 | -0.095522 | -0.024061 | 0.00025217 | 9.6728e-05 | 0.14257 | 0.14257 | 0.14257 | 1 | 0 | 0.99728 | -0.018826 | 52.8032
25 | 0.057895 | 0.014532 | -0.057761 | -0.014481 | 0.00013458 | 5.139e-05 | 0.086532 | 0.086532 | 0.086532 | 0.99566 | -0.030285 | 0.99328 | -0.047065 | 32.049
26 | 0.095522 | 0.024061 | -0.095336 | -0.02399 | 0.00018588 | 7.1302e-05 | 0.14257 | 0.14257 | 0.14257 | 0.99728 | -0.018826 | 0.99528 | -0.032769 | 52.8032
27 | 0.037609 | 0.0094303 | -0.037604 | -0.0094284 | 5.1478e-06 | 1.9463e-06 | 0.056343 | 0.056343 | 0.056343 | 0.99328 | -0.047065 | 0.99314 | -0.048053 | 20.8679
28 | -0.011008 | -0.0027588 | 0.011014 | 0.0027606 | 5.638e-06 | 1.7393e-06 | 0.016502 | 0.016502 | 0.016502 | 0.99261 | -0.051751 | 0.99314 | -0.048053 | 6.1118
29 | 0.02659 | 0.0066678 | -0.02656 | -0.0066567 | 2.9954e-05 | 1.113e-05 | 0.039842 | 0.039842 | 0.039842 | 0.99314 | -0.048053 | 0.99198 | -0.05619 | 14.7562
30 | -0.012765 | -0.0031993 | 0.012766 | 0.0031994 | 4.2077e-07 | 1.3868e-07 | 0.019269 | 0.019269 | 0.019269 | 0.98578 | -0.099673 | 0.98581 | -0.099435 | 7.1367
31 | -0.037497 | -0.0093977 | 0.037546 | 0.0094164 | 4.9258e-05 | 1.8631e-05 | 0.056599 | 0.056599 | 0.056599 | 0.98581 | -0.099435 | 0.98715 | -0.089958 | 20.9627
32 | 0.0047639 | 0.0011937 | -0.004763 | -0.0011937 | 9.3477e-07 | -1.838e-08 | 0.0071494 | 0.0071496 | 0.0071496 | 0.99151 | -0.059212 | 0.99131 | -0.060629 | 2.648

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22389 | 0.056134

## res_load
| p_mw | q_mvar
0 | 0.0062965 | 0.001578
1 | 0.0025716 | 0.0006445
2 | 0.0060606 | 0.0015189
3 | 0.0049748 | 0.0012468
4 | 0.0033519 | 0.00084007
5 | 0.019026 | 0.0047683
6 | 0.022328 | 0.0055958
7 | 0.0074497 | 0.0018671
8 | 0.025338 | 0.0063503
9 | 0.0052174 | 0.0013076
10 | 0.0049826 | 0.0012488
11 | 0.0037496 | 0.00093973
12 | 0.020152 | 0.0050505
13 | 0.011008 | 0.0027588
14 | 0.0040199 | 0.0010075
15 | 0.012765 | 0.0031993
16 | 0.024731 | 0.0061983
17 | 0.005996 | 0.0015027
18 | 0.004763 | 0.0011937
19 | 0.02656 | 0.0066567

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1