## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2306-22_1_3_node_3 | 0.4 | n |  | TRUE
1 | bus_LV_2306-22_1_3_node_4 | 0.4 | n |  | TRUE
2 | bus_LV_2306-22_1_3_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_2306-22_1_3_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_2306-22_1_3_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_2306-22_1_3_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_2306-22_1_3_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_2306-22_1_3_node_42 | 0.4 | n |  | TRUE
8 | bus_LV_2306-22_1_3_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_2306-22_1_3_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_2306-22_1_3_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_2306-22_1_3_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_2306-22_1_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_2306-22_1_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_2306-22_1_3_node_254 | 0.4 | n |  | TRUE
15 | bus_LV_2306-22_1_3_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_2306-22_1_3_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_2306-22_1_3_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_2306-22_1_3_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_2306-22_1_3_node_255 | 0.4 | n |  | TRUE
20 | bus_LV_2306-22_1_3_node_107 | 0.4 | n |  | TRUE
21 | bus_LV_2306-22_1_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2306-22_1_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_2306-22_1_3_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_2306-22_1_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2306-22_1_3_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_2306-22_1_3_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_2306-22_1_3_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_2306-22_1_3_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_2306-22_1_3_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_2306-22_1_3_node_47 | 0.4 | n |  | TRUE
31 | bus_LV_2306-22_1_3_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_2306-22_1_3_node_116 | 0.4 | n |  | TRUE
33 | bus_LV_2306-22_1_3_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_2306-22_1_3_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_2306-22_1_3_node_43 | 0.4 | n |  | TRUE
36 | bus_LV_2306-22_1_3_node_45 | 0.4 | n |  | TRUE
37 | bus_LV_2306-22_1_3_node_46 | 0.4 | n |  | TRUE
38 | bus_LV_2306-22_1_3_node_154 | 0.4 | n |  | TRUE
39 | bus_LV_2306-22_1_3_node_122 | 0.4 | n |  | TRUE
40 | bus_LV_2306-22_1_3_node_91 | 0.4 | n |  | TRUE
41 | bus_LV_2306-22_1_3_node_67 | 0.4 | n |  | TRUE
42 | bus_LV_2306-22_1_3_node_68 | 0.4 | n |  | TRUE
43 | bus_LV_2306-22_1_3_node_69 | 0.4 | n |  | TRUE
44 | bus_LV_2306-22_1_3_node_70 | 0.4 | n |  | TRUE
45 | bus_LV_2306-22_1_3_node_71 | 0.4 | n |  | TRUE
46 | bus_LV_2306-22_1_3_node_72 | 0.4 | n |  | TRUE
47 | bus_LV_2306-22_1_3_node_146 | 0.4 | n |  | TRUE
48 | bus_LV_2306-22_1_3_node_103 | 0.4 | n |  | TRUE
49 | bus_LV_2306-22_1_3_node_79 | 0.4 | n |  | TRUE
50 | bus_LV_2306-22_1_3_node_80 | 0.4 | n |  | TRUE
51 | bus_LV_2306-22_1_3_node_81 | 0.4 | n |  | TRUE
52 | bus_LV_2306-22_1_3_node_139 | 0.4 | n |  | TRUE
53 | bus_LV_2306-22_1_3_node_86 | 0.4 | n |  | TRUE
54 | bus_LV_2306-22_1_3_node_87 | 0.4 | n |  | TRUE
55 | bus_LV_2306-22_1_3_node_88 | 0.4 | n |  | TRUE
56 | bus_LV_2306-22_1_3_node_89 | 0.4 | n |  | TRUE
57 | bus_LV_2306-22_1_3_node_90 | 0.4 | n |  | TRUE
58 | bus_LV_2306-22_1_3_node_161 | 0.4 | n |  | TRUE
59 | bus_LV_2306-22_1_3_node_92 | 0.4 | n |  | TRUE
60 | bus_LV_2306-22_1_3_node_93 | 0.4 | n |  | TRUE
61 | bus_LV_2306-22_1_3_node_94 | 0.4 | n |  | TRUE
62 | bus_LV_2306-22_1_3_node_95 | 0.4 | n |  | TRUE
63 | bus_LV_2306-22_1_3_node_96 | 0.4 | n |  | TRUE
64 | bus_LV_2306-22_1_3_node_97 | 0.4 | n |  | TRUE
65 | bus_LV_2306-22_1_3_node_98 | 0.4 | n |  | TRUE
66 | bus_LV_2306-22_1_3_node_191 | 0.4 | n |  | TRUE
67 | bus_LV_2306-22_1_3_node_121 | 0.4 | n |  | TRUE
68 | bus_LV_2306-22_1_3_node_157 | 0.4 | n |  | TRUE
69 | bus_LV_2306-22_1_3_node_99 | 0.4 | n |  | TRUE
70 | bus_LV_2306-22_1_3_node_100 | 0.4 | n |  | TRUE
71 | bus_LV_2306-22_1_3_node_101 | 0.4 | n |  | TRUE
72 | bus_LV_2306-22_1_3_node_102 | 0.4 | n |  | TRUE
73 | bus_LV_2306-22_1_3_node_117 | 0.4 | n |  | TRUE
74 | bus_LV_2306-22_1_3_node_144 | 0.4 | n |  | TRUE
75 | bus_LV_2306-22_1_3_node_104 | 0.4 | n |  | TRUE
76 | bus_LV_2306-22_1_3_node_105 | 0.4 | n |  | TRUE
77 | bus_LV_2306-22_1_3_node_106 | 0.4 | n |  | TRUE
78 | bus_LV_2306-22_1_3_node_208 | 0.4 | n |  | TRUE
79 | bus_LV_2306-22_1_3_node_108 | 0.4 | n |  | TRUE
80 | bus_LV_2306-22_1_3_node_152 | 0.4 | n |  | TRUE
81 | bus_LV_2306-22_1_3_node_151 | 0.4 | n |  | TRUE
82 | bus_LV_2306-22_1_3_node_115 | 0.4 | n |  | TRUE
83 | bus_LV_2306-22_1_3_node_195 | 0.4 | n |  | TRUE
84 | bus_LV_2306-22_1_3_node_118 | 0.4 | n |  | TRUE
85 | bus_LV_2306-22_1_3_node_119 | 0.4 | n |  | TRUE
86 | bus_LV_2306-22_1_3_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_2306-22_1_3_node_158 | 0.4 | n |  | TRUE
88 | bus_LV_2306-22_1_3_node_140 | 0.4 | n |  | TRUE
89 | bus_LV_2306-22_1_3_node_141 | 0.4 | n |  | TRUE
90 | bus_LV_2306-22_1_3_node_145 | 0.4 | n |  | TRUE
91 | bus_LV_2306-22_1_3_node_142 | 0.4 | n |  | TRUE
92 | bus_LV_2306-22_1_3_node_143 | 0.4 | n |  | TRUE
93 | bus_LV_2306-22_1_3_node_173 | 0.4 | n |  | TRUE
94 | bus_LV_2306-22_1_3_node_160 | 0.4 | n |  | TRUE
95 | bus_LV_2306-22_1_3_node_155 | 0.4 | n |  | TRUE
96 | bus_LV_2306-22_1_3_node_156 | 0.4 | n |  | TRUE
97 | bus_LV_2306-22_1_3_node_193 | 0.4 | n |  | TRUE
98 | bus_LV_2306-22_1_3_node_159 | 0.4 | n |  | TRUE
99 | bus_LV_2306-22_1_3_node_162 | 0.4 | n |  | TRUE
100 | bus_LV_2306-22_1_3_node_212 | 0.4 | n |  | TRUE
101 | bus_LV_2306-22_1_3_node_163 | 0.4 | n |  | TRUE
102 | bus_LV_2306-22_1_3_node_167 | 0.4 | n |  | TRUE
103 | bus_LV_2306-22_1_3_node_168 | 0.4 | n |  | TRUE
104 | bus_LV_2306-22_1_3_node_169 | 0.4 | n |  | TRUE
105 | bus_LV_2306-22_1_3_node_170 | 0.4 | n |  | TRUE
106 | bus_LV_2306-22_1_3_node_171 | 0.4 | n |  | TRUE
107 | bus_LV_2306-22_1_3_node_172 | 0.4 | n |  | TRUE
108 | bus_LV_2306-22_1_3_node_175 | 0.4 | n |  | TRUE
109 | bus_LV_2306-22_1_3_node_209 | 0.4 | n |  | TRUE
110 | bus_LV_2306-22_1_3_node_174 | 0.4 | n |  | TRUE
111 | bus_LV_2306-22_1_3_node_185 | 0.4 | n |  | TRUE
112 | bus_LV_2306-22_1_3_node_213 | 0.4 | n |  | TRUE
113 | bus_LV_2306-22_1_3_node_201 | 0.4 | n |  | TRUE
114 | bus_LV_2306-22_1_3_node_176 | 0.4 | n |  | TRUE
115 | bus_LV_2306-22_1_3_node_186 | 0.4 | n |  | TRUE
116 | bus_LV_2306-22_1_3_node_190 | 0.4 | n |  | TRUE
117 | bus_LV_2306-22_1_3_node_194 | 0.4 | n |  | TRUE
118 | bus_LV_2306-22_1_3_node_202 | 0.4 | n |  | TRUE
119 | bus_MV_0_node_163 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2306-22_1_3_load_3 | 0 | 0.00056028 | 0.00014042 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2306-22_1_3_load_6 | 2 | 0.00059342 | 0.00014872 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2306-22_1_3_load_7 | 4 | 0.0027465 | 0.00068835 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2306-22_1_3_load_15 | 5 | 0.00014817 | 3.7135e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2306-22_1_3_load_8 | 6 | 0.00016231 | 4.068e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2306-22_1_3_load_42 | 7 | 0.00033999 | 8.5209e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2306-22_1_3_load_9 | 8 | 0.0010313 | 0.00025847 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2306-22_1_3_load_13 | 12 | 0.0016615 | 0.00041641 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2306-22_1_3_load_254 | 14 | 0.00037747 | 9.4602e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2306-22_1_3_load_22 | 16 | 0.00033827 | 8.4778e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2306-22_1_3_load_255 | 19 | 0.0010885 | 0.00027281 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2306-22_1_3_load_18 | 21 | 0.00012832 | 3.216e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2306-22_1_3_load_19 | 22 | 0.00015581 | 3.905e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2306-22_1_3_load_33 | 23 | 0.0019974 | 0.00050059 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2306-22_1_3_load_21 | 24 | 0.00045946 | 0.00011515 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2306-22_1_3_load_34 | 25 | 0.00051496 | 0.00012906 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2306-22_1_3_load_35 | 26 | 0.00063095 | 0.00015813 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2306-22_1_3_load_36 | 27 | 0.00011929 | 2.9898e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2306-22_1_3_load_37 | 28 | 0.00079831 | 0.00020008 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2306-22_1_3_load_47 | 30 | 0.00066983 | 0.00016788 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2306-22_1_3_load_39 | 31 | 0.0020655 | 0.00051766 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2306-22_1_3_load_116 | 32 | 0.00011657 | 2.9214e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2306-22_1_3_load_41 | 34 | 0.00068355 | 0.00017131 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2306-22_1_3_load_45 | 36 | 0.00031067 | 7.7861e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2306-22_1_3_load_122 | 39 | 0.00040588 | 0.00010172 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2306-22_1_3_load_91 | 40 | 0.0019463 | 0.00048779 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2306-22_1_3_load_67 | 41 | 0.00063392 | 0.00015888 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2306-22_1_3_load_68 | 42 | 0.0013585 | 0.00034047 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2306-22_1_3_load_70 | 44 | 0.00081825 | 0.00020507 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2306-22_1_3_load_71 | 45 | 0.00038199 | 9.5737e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2306-22_1_3_load_72 | 46 | 0.00058868 | 0.00014754 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2306-22_1_3_load_146 | 47 | 0.00014692 | 3.6823e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2306-22_1_3_load_79 | 49 | 0.00030249 | 7.5812e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2306-22_1_3_load_80 | 50 | 0.00021298 | 5.3377e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2306-22_1_3_load_81 | 51 | 0.00024081 | 6.0352e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2306-22_1_3_load_139 | 52 | 0.00067696 | 0.00016966 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2306-22_1_3_load_86 | 53 | 0.0020444 | 0.00051239 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2306-22_1_3_load_87 | 54 | 0.00032515 | 8.1491e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2306-22_1_3_load_88 | 55 | 0.0004004 | 0.00010035 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2306-22_1_3_load_90 | 57 | 0.0023019 | 0.00057691 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2306-22_1_3_load_161 | 58 | 0.00056322 | 0.00014116 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2306-22_1_3_load_92 | 59 | 0.00029792 | 7.4665e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2306-22_1_3_load_93 | 60 | 0.0015073 | 0.00037776 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2306-22_1_3_load_94 | 61 | 0.00020965 | 5.2542e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2306-22_1_3_load_96 | 63 | 0.00010879 | 2.7266e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2306-22_1_3_load_97 | 64 | 0.0012221 | 0.0003063 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2306-22_1_3_load_98 | 65 | 0.00040227 | 0.00010082 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2306-22_1_3_load_191 | 66 | 0.00027499 | 6.8918e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2306-22_1_3_load_121 | 67 | 0.0002604 | 6.5263e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2306-22_1_3_load_99 | 69 | 0.003194 | 0.0008005 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2306-22_1_3_load_100 | 70 | 0.00012436 | 3.1167e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2306-22_1_3_load_102 | 72 | 0.00035835 | 8.9811e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2306-22_1_3_load_117 | 73 | 0.00053002 | 0.00013284 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2306-22_1_3_load_144 | 74 | 0.00081927 | 0.00020533 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2306-22_1_3_load_104 | 75 | 0.00050628 | 0.00012688 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2306-22_1_3_load_105 | 76 | 0.00068942 | 0.00017279 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2306-22_1_3_load_208 | 78 | 0.00058449 | 0.00014649 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2306-22_1_3_load_152 | 80 | 0.00076321 | 0.00019128 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2306-22_1_3_load_151 | 81 | 0.0025091 | 0.00062884 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2306-22_1_3_load_115 | 82 | 0.00054387 | 0.00013631 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2306-22_1_3_load_195 | 83 | 0.00052689 | 0.00013205 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2306-22_1_3_load_118 | 84 | 0.00070523 | 0.00017675 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2306-22_1_3_load_119 | 85 | 0.00030162 | 7.5593e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2306-22_1_3_load_120 | 86 | 0.00039509 | 9.9018e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2306-22_1_3_load_158 | 87 | 0.00032975 | 8.2642e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2306-22_1_3_load_140 | 88 | 0.00056331 | 0.00014118 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2306-22_1_3_load_145 | 90 | 0.0004506 | 0.00011293 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2306-22_1_3_load_142 | 91 | 0.0018802 | 0.00047121 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2306-22_1_3_load_143 | 92 | 0.00034171 | 8.5642e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2306-22_1_3_load_173 | 93 | 0.00036092 | 9.0456e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2306-22_1_3_load_160 | 94 | 0.00038056 | 9.5376e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2306-22_1_3_load_155 | 95 | 0.00086479 | 0.00021674 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2306-22_1_3_load_193 | 97 | 0.00016368 | 4.1023e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2306-22_1_3_load_159 | 98 | 0.00071027 | 0.00017801 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2306-22_1_3_load_163 | 101 | 0.0003921 | 9.8269e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2306-22_1_3_load_167 | 102 | 0.00014291 | 3.5816e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2306-22_1_3_load_168 | 103 | 7.842e-05 | 1.9654e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2306-22_1_3_load_172 | 107 | 0.00026294 | 6.59e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2306-22_1_3_load_175 | 108 | 0.00022149 | 5.5512e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2306-22_1_3_load_209 | 109 | 0.00015358 | 3.849e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2306-22_1_3_load_174 | 110 | 0.00054345 | 0.0001362 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2306-22_1_3_load_185 | 111 | 0.00023144 | 5.8004e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2306-22_1_3_load_213 | 112 | 0.00080915 | 0.00020279 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2306-22_1_3_load_176 | 114 | 0.0012865 | 0.00032242 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2306-22_1_3_load_186 | 115 | 0.00025718 | 6.4455e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2306-22_1_3_load_190 | 116 | 0.00064632 | 0.00016198 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2306-22_1_3_load_202 | 118 | 0.0011011 | 0.00027596 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 101 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2306-22_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.013418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2306-22_1_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.007111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2306-22_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.021943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2306-22_1_3_line_3 | NAYY 4x150 SE | 2 | 6 | 0.017246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2306-22_1_3_line_4 | NAYY 4x150 SE | 3 | 4 | 0.06806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2306-22_1_3_line_5 | NAYY 4x150 SE | 3 | 5 | 0.22193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2306-22_1_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.29945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2306-22_1_3_line_7 | NAYY 4x150 SE | 5 | 17 | 0.070238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2306-22_1_3_line_8 | NAYY 4x150 SE | 7 | 35 | 0.0054469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2306-22_1_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.017932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_2306-22_1_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.03266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_2306-22_1_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.077288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_2306-22_1_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.009821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2306-22_1_3_line_13 | NAYY 4x150 SE | 10 | 13 | 0.005675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_2306-22_1_3_line_14 | NAYY 4x150 SE | 11 | 14 | 0.012104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_2306-22_1_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.039239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_2306-22_1_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.0085423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2306-22_1_3_line_17 | NAYY 4x150 SE | 14 | 19 | 0.41869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_2306-22_1_3_line_18 | NAYY 4x150 SE | 15 | 24 | 0.015865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2306-22_1_3_line_19 | NAYY 4x150 SE | 15 | 21 | 0.040238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_2306-22_1_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.044828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2306-22_1_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.04049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_2306-22_1_3_line_22 | NAYY 4x150 SE | 18 | 20 | 0.14775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_2306-22_1_3_line_23 | NAYY 4x150 SE | 20 | 79 | 0.032301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_2306-22_1_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.00010398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_2306-22_1_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.35172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_2306-22_1_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.044408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_2306-22_1_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.087073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_2306-22_1_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.023081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_2306-22_1_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.038772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_2306-22_1_3_line_30 | NAYY 4x150 SE | 28 | 29 | 0.075155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_2306-22_1_3_line_31 | NAYY 4x150 SE | 29 | 30 | 0.0070285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_2306-22_1_3_line_32 | NAYY 4x150 SE | 30 | 40 | 0.033582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_2306-22_1_3_line_33 | NAYY 4x150 SE | 31 | 32 | 0.21019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_2306-22_1_3_line_34 | NAYY 4x150 SE | 31 | 33 | 0.22718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_2306-22_1_3_line_35 | NAYY 4x150 SE | 32 | 82 | 0.0089914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_2306-22_1_3_line_36 | NAYY 4x150 SE | 33 | 34 | 0.095411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2306-22_1_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.010017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2306-22_1_3_line_38 | NAYY 4x150 SE | 37 | 38 | 0.024868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_2306-22_1_3_line_39 | NAYY 4x150 SE | 37 | 39 | 0.016503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_2306-22_1_3_line_40 | NAYY 4x150 SE | 38 | 59 | 0.062412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_2306-22_1_3_line_41 | NAYY 4x150 SE | 38 | 77 | 0.018011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2306-22_1_3_line_42 | NAYY 4x150 SE | 39 | 67 | 0.016711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_2306-22_1_3_line_43 | NAYY 4x150 SE | 40 | 59 | 0.013653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_2306-22_1_3_line_44 | NAYY 4x150 SE | 41 | 42 | 0.049272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2306-22_1_3_line_45 | NAYY 4x150 SE | 41 | 43 | 0.0080139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2306-22_1_3_line_46 | NAYY 4x150 SE | 42 | 44 | 0.061033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2306-22_1_3_line_47 | NAYY 4x150 SE | 43 | 45 | 0.077459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2306-22_1_3_line_48 | NAYY 4x150 SE | 43 | 46 | 0.012318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2306-22_1_3_line_49 | NAYY 4x150 SE | 44 | 47 | 0.003606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2306-22_1_3_line_50 | NAYY 4x150 SE | 45 | 48 | 0.018087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2306-22_1_3_line_51 | NAYY 4x150 SE | 47 | 56 | 0.21887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2306-22_1_3_line_52 | NAYY 4x150 SE | 48 | 74 | 0.052048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2306-22_1_3_line_53 | NAYY 4x150 SE | 48 | 71 | 0.012565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2306-22_1_3_line_54 | NAYY 4x150 SE | 49 | 50 | 0.018295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2306-22_1_3_line_55 | NAYY 4x150 SE | 50 | 51 | 0.010307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2306-22_1_3_line_56 | NAYY 4x150 SE | 51 | 52 | 0.13168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2306-22_1_3_line_57 | NAYY 4x150 SE | 52 | 88 | 0.088532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2306-22_1_3_line_58 | NAYY 4x150 SE | 53 | 54 | 0.032422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2306-22_1_3_line_59 | NAYY 4x150 SE | 53 | 55 | 0.015227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2306-22_1_3_line_60 | NAYY 4x150 SE | 54 | 56 | 0.038052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2306-22_1_3_line_61 | NAYY 4x150 SE | 55 | 57 | 0.040612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2306-22_1_3_line_62 | NAYY 4x150 SE | 55 | 58 | 0.29992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2306-22_1_3_line_63 | NAYY 4x150 SE | 58 | 100 | 0.27316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2306-22_1_3_line_64 | NAYY 4x150 SE | 58 | 98 | 0.027943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2306-22_1_3_line_65 | NAYY 4x150 SE | 60 | 61 | 0.025499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2306-22_1_3_line_66 | NAYY 4x150 SE | 60 | 62 | 0.019851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2306-22_1_3_line_67 | NAYY 4x150 SE | 61 | 63 | 0.014381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2306-22_1_3_line_68 | NAYY 4x150 SE | 62 | 64 | 0.020022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_2306-22_1_3_line_69 | NAYY 4x150 SE | 62 | 65 | 0.02246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_2306-22_1_3_line_70 | NAYY 4x150 SE | 63 | 66 | 0.0038113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2306-22_1_3_line_71 | NAYY 4x150 SE | 64 | 67 | 0.012005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_2306-22_1_3_line_72 | NAYY 4x150 SE | 65 | 68 | 0.018717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_2306-22_1_3_line_73 | NAYY 4x150 SE | 66 | 116 | 0.004289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2306-22_1_3_line_74 | NAYY 4x150 SE | 68 | 97 | 0.087027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_2306-22_1_3_line_75 | NAYY 4x150 SE | 68 | 96 | 0.014406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2306-22_1_3_line_76 | NAYY 4x150 SE | 69 | 70 | 0.017401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2306-22_1_3_line_77 | NAYY 4x150 SE | 69 | 71 | 0.015396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2306-22_1_3_line_78 | NAYY 4x150 SE | 70 | 72 | 0.0043103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2306-22_1_3_line_79 | NAYY 4x150 SE | 72 | 73 | 0.014695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2306-22_1_3_line_80 | NAYY 4x150 SE | 74 | 92 | 0.055702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2306-22_1_3_line_81 | NAYY 4x150 SE | 75 | 76 | 0.036066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2306-22_1_3_line_82 | NAYY 4x150 SE | 76 | 77 | 0.0094849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2306-22_1_3_line_83 | NAYY 4x150 SE | 77 | 78 | 0.045981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2306-22_1_3_line_84 | NAYY 4x150 SE | 79 | 80 | 0.010605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2306-22_1_3_line_85 | NAYY 4x150 SE | 79 | 81 | 0.030781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_2306-22_1_3_line_86 | NAYY 4x150 SE | 81 | 94 | 0.30599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_2306-22_1_3_line_87 | NAYY 4x150 SE | 82 | 83 | 0.11939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_2306-22_1_3_line_88 | NAYY 4x150 SE | 83 | 117 | 0.097916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_2306-22_1_3_line_89 | NAYY 4x150 SE | 84 | 85 | 0.0011427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2306-22_1_3_line_90 | NAYY 4x150 SE | 85 | 86 | 0.081067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2306-22_1_3_line_91 | NAYY 4x150 SE | 86 | 87 | 0.025925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2306-22_1_3_line_92 | NAYY 4x150 SE | 87 | 96 | 0.039272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2306-22_1_3_line_93 | NAYY 4x150 SE | 88 | 89 | 0.034664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2306-22_1_3_line_94 | NAYY 4x150 SE | 89 | 90 | 0.18031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2306-22_1_3_line_95 | NAYY 4x150 SE | 89 | 91 | 0.053987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2306-22_1_3_line_96 | NAYY 4x150 SE | 90 | 93 | 0.023222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2306-22_1_3_line_97 | NAYY 4x150 SE | 91 | 92 | 0.047388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2306-22_1_3_line_98 | NAYY 4x150 SE | 93 | 110 | 0.0046254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2306-22_1_3_line_99 | NAYY 4x150 SE | 94 | 99 | 0.0067014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_2306-22_1_3_line_100 | NAYY 4x150 SE | 94 | 98 | 0.050414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2306-22_1_3_line_101 | NAYY 4x150 SE | 95 | 96 | 0.012316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2306-22_1_3_line_102 | NAYY 4x150 SE | 97 | 117 | 0.0021372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_2306-22_1_3_line_103 | NAYY 4x150 SE | 99 | 101 | 0.17454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_2306-22_1_3_line_104 | NAYY 4x150 SE | 100 | 112 | 0.083607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2306-22_1_3_line_105 | NAYY 4x150 SE | 102 | 103 | 0.015611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2306-22_1_3_line_106 | NAYY 4x150 SE | 102 | 104 | 0.022004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2306-22_1_3_line_107 | NAYY 4x150 SE | 103 | 105 | 0.0084763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2306-22_1_3_line_108 | NAYY 4x150 SE | 104 | 106 | 0.027018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2306-22_1_3_line_109 | NAYY 4x150 SE | 104 | 107 | 0.0058547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2306-22_1_3_line_110 | NAYY 4x150 SE | 105 | 108 | 0.0042339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2306-22_1_3_line_111 | NAYY 4x150 SE | 106 | 109 | 0.027533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2306-22_1_3_line_112 | NAYY 4x150 SE | 108 | 112 | 0.25066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2306-22_1_3_line_113 | NAYY 4x150 SE | 108 | 113 | 0.18787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2306-22_1_3_line_114 | NAYY 4x150 SE | 109 | 114 | 0.005982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2306-22_1_3_line_115 | NAYY 4x150 SE | 110 | 111 | 0.0018324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2306-22_1_3_line_116 | NAYY 4x150 SE | 111 | 115 | 0.0042137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2306-22_1_3_line_117 | NAYY 4x150 SE | 113 | 118 | 0.16806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2306-22_1_3_trafo_163 | 0.25 MVA 20/0.4 kV | 119 | 101 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2588725.7738 | 1181474.5221 | 2588725.8336 | 1181477.8792 | 2588726.8404 | 1181481.2791 | 2588729.642 | 1181484.82 | 2588731.1075 | 1181486.1803
1 | 2588725.7738 | 1181474.5221 | 2588720.1877 | 1181478.9224
2 | 2588725.7738 | 1181474.5221 | 2588729.983 | 1181459.284 | 2588733.092 | 1181459.8118 | 2588736.0699 | 1181459.6838
3 | 2588708.6707 | 1181491.73 | 2588719.1249 | 1181479.7596 | 2588720.1877 | 1181478.9224
4 | 2588736.0699 | 1181459.6838 | 2588741.5734 | 1181458.495 | 2588746.6802 | 1181457.5071 | 2588751.2536 | 1181457.1093 | 2588755.859 | 1181457.5008 | 2588762.5133 | 1181459.1447 | 2588784.0693 | 1181470.6321 | 2588797.7691 | 1181480.2447
5 | 2588736.0699 | 1181459.6838 | 2588663.9634 | 1181249.7909
6 | 2588797.7691 | 1181480.2447 | 2589084.0715 | 1181568.0164
7 | 2588595.4906 | 1181262.8394 | 2588616.546 | 1181255.6398 | 2588645.8821 | 1181249.8364 | 2588663.9634 | 1181249.7909
8 | 2589083.4541 | 1181573.4282 | 2589084.0715 | 1181568.0164
9 | 2588640.9508 | 1180790.8437 | 2588634.6202 | 1180779.1387 | 2588631.8441 | 1180775.4395
10 | 2588603.5687 | 1180759.7881 | 2588608.3471 | 1180762.4581 | 2588617.7935 | 1180766.0419 | 2588624.0999 | 1180769.0647 | 2588628.3745 | 1180771.9247 | 2588631.4044 | 1180774.8537 | 2588631.8441 | 1180775.4395
11 | 2588715.5524 | 1180804.0308 | 2588713.5026 | 1180802.4339 | 2588710.6812 | 1180800.6939 | 2588707.1649 | 1180798.9997 | 2588698.9798 | 1180795.9359 | 2588694.2803 | 1180794.5663 | 2588689.4445 | 1180793.7529 | 2588684.1513 | 1180793.3961 | 2588676.9728 | 1180793.621 | 2588664.3896 | 1180795.0679 | 2588659.9527 | 1180795.1986 | 2588655.6751 | 1180794.7621 | 2588650.6097 | 1180793.7157 | 2588640.9508 | 1180790.8437
12 | 2588603.5687 | 1180759.7881 | 2588607.3283 | 1180768.8634
13 | 2588599.1019 | 1180756.2727 | 2588603.5687 | 1180759.7881
14 | 2588715.5524 | 1180804.0308 | 2588704.2272 | 1180808.3879
15 | 2588599.1019 | 1180756.2727 | 2588567.0584 | 1180733.5002
16 | 2588599.1019 | 1180756.2727 | 2588602.786 | 1180748.5656
17 | 2588610.4381 | 1181216.4425 | 2588704.2272 | 1180808.3879
18 | 2588551.5538 | 1180736.9095 | 2588560.5629 | 1180735.4581 | 2588567.0584 | 1180733.5002
19 | 2588567.0584 | 1180733.5002 | 2588550.7152 | 1180721.8145 | 2588532.5549 | 1180713.0916
20 | 2588573.576 | 1181224.2283 | 2588577.2772 | 1181226.9114 | 2588595.4906 | 1181262.8394
21 | 2588573.576 | 1181224.2283 | 2588595.4803 | 1181213.6141 | 2588603.0606 | 1181212.1655 | 2588610.4381 | 1181216.4425
22 | 2588428.7121 | 1181233.0682 | 2588430.6859 | 1181234.9097 | 2588433.2931 | 1181236.5055 | 2588436.3809 | 1181237.8557 | 2588440.0249 | 1181238.5935 | 2588443.2097 | 1181238.7429 | 2588446.3937 | 1181238.5478 | 2588558.3828 | 1181222.1008 | 2588573.576 | 1181224.2283
23 | 2588428.7121 | 1181233.0682 | 2588422.6459 | 1181239.4833 | 2588407.999 | 1181247.3603 | 2588405.5296 | 1181249.833 | 2588404.4591 | 1181253.059
24 | 2588532.5549 | 1180713.0916 | 2588532.4612 | 1180713.0466
25 | 2588180.8373 | 1180721.2977 | 2588532.4612 | 1180713.0466
26 | 2588180.8373 | 1180721.2977 | 2588174.236 | 1180732.0001 | 2588166.4367 | 1180742.6766 | 2588156.4523 | 1180752.8683 | 2588153.0859 | 1180755.6142
27 | 2588073.2552 | 1180788.8817 | 2588076.4007 | 1180787.8571 | 2588134.2734 | 1180767.9424 | 2588146.7383 | 1180760.7917 | 2588153.0859 | 1180755.6142
28 | 2588051.3095 | 1180796.0301 | 2588073.2552 | 1180788.8817
29 | 2588051.3095 | 1180796.0301 | 2588014.4441 | 1180808.0382
30 | 2587942.9841 | 1180831.3147 | 2588014.4441 | 1180808.0382
31 | 2587942.9841 | 1180831.3147 | 2587937.8991 | 1180836.1668
32 | 2587937.8991 | 1180836.1668 | 2587926.779 | 1180846.7777 | 2587915.0509 | 1180851.7374 | 2587911.1399 | 1180855.5734
33 | 2587519.5699 | 1180999.3559 | 2587385.347 | 1180837.5985
34 | 2587385.347 | 1180837.5985 | 2587494.5113 | 1180638.3628
35 | 2587520.8199 | 1181008.26 | 2587519.5699 | 1180999.3559
36 | 2587494.5113 | 1180638.3628 | 2587451.0703 | 1180605.8041 | 2587434.2445 | 1180601.8709 | 2587420.9736 | 1180603.2218 | 2587414.3468 | 1180611.6179
37 | 2589083.4541 | 1181573.4282 | 2589082.327 | 1181583.3798
38 | 2587839.4025 | 1180872.5243 | 2587847.1565 | 1180896.1539
39 | 2587839.4025 | 1180872.5243 | 2587836.9119 | 1180868.2938 | 2587829.8288 | 1180859.1147 | 2587829.8288 | 1180859.1147
40 | 2587847.1565 | 1180896.1539 | 2587854.8081 | 1180892.0806 | 2587864.6244 | 1180885.9241 | 2587878.1516 | 1180879.4488 | 2587894.0009 | 1180869.4114 | 2587900.6532 | 1180864.2846
41 | 2587855.4827 | 1180912.0451 | 2587851.6606 | 1180906.5056 | 2587847.1565 | 1180896.1539
42 | 2587829.8288 | 1180859.1147 | 2587819.7873 | 1180855.9781 | 2587813.6265 | 1180856.5875
43 | 2587911.1399 | 1180855.5734 | 2587908.1455 | 1180858.5104 | 2587900.6532 | 1180864.2846
44 | 2587730.9448 | 1181329.7253 | 2587736.399 | 1181330.7151 | 2587750.037 | 1181330.3869 | 2587758.7219 | 1181331.4918 | 2587765.9273 | 1181333.5336 | 2587778.0927 | 1181340.1389
45 | 2587723.3033 | 1181327.3848 | 2587728.7062 | 1181329.3191 | 2587730.9448 | 1181329.7253
46 | 2587778.0927 | 1181340.1389 | 2587813.2495 | 1181359.2275 | 2587832.2175 | 1181368.3048
47 | 2587723.3033 | 1181327.3848 | 2587716.8264 | 1181323.1071 | 2587710.4841 | 1181317.4728 | 2587699.4268 | 1181306.49 | 2587680.8105 | 1181285.0397 | 2587674.3313 | 1181276.0263 | 2587670.9086 | 1181270.9452
48 | 2587723.3033 | 1181327.3848 | 2587732.6054 | 1181319.3095
49 | 2587835.4702 | 1181369.8615 | 2587832.2175 | 1181368.3048
50 | 2587660.8036 | 1181255.944 | 2587670.9086 | 1181270.9452
51 | 2587835.4702 | 1181369.8615 | 2587926.3959 | 1181568.9492
52 | 2587660.8036 | 1181255.944 | 2587656.9429 | 1181264.9344 | 2587651.7767 | 1181274.1053 | 2587647.5374 | 1181280.951 | 2587641.9987 | 1181287.2212 | 2587635.0811 | 1181295.1285 | 2587631.4219 | 1181298.2561
53 | 2587660.8036 | 1181255.944 | 2587664.3755 | 1181243.897
54 | 2587251.4257 | 1181339.0409 | 2587243.9268 | 1181338.7759 | 2587233.5549 | 1181341.7554
55 | 2587261.7265 | 1181339.405 | 2587251.4257 | 1181339.0409
56 | 2587261.7265 | 1181339.405 | 2587309.4752 | 1181341.0926 | 2587388.1612 | 1181355.6218 | 2587391.867 | 1181356.7741
57 | 2587391.867 | 1181356.7741 | 2587467.7007 | 1181380.3555 | 2587475.8928 | 1181384.3556
58 | 2587937.7016 | 1181605.2556 | 2587938.7208 | 1181610.4566 | 2587939.9647 | 1181625.1617 | 2587942.4623 | 1181633.0162 | 2587944.1025 | 1181636.7985
59 | 2587952.3906 | 1181649.4449 | 2587947.3628 | 1181643.3894 | 2587944.8176 | 1181638.4476 | 2587944.1025 | 1181636.7985
60 | 2587926.3959 | 1181568.9492 | 2587936.9461 | 1181601.4 | 2587937.7016 | 1181605.2556
61 | 2587983.0699 | 1181676.0288 | 2587953.1957 | 1181650.4145 | 2587952.3906 | 1181649.4449
62 | 2588094.388 | 1181385.2717 | 2587952.3906 | 1181649.4449
63 | 2588094.388 | 1181385.2717 | 2588284.7838 | 1181581.1395
64 | 2588094.388 | 1181385.2717 | 2588093.3943 | 1181379.9936 | 2588089.2996 | 1181357.7954
65 | 2587768.2027 | 1180816.8415 | 2587776.636 | 1180832.6656 | 2587778.9391 | 1180839.8744
66 | 2587781.7314 | 1180859.4467 | 2587780.3024 | 1180844.1418 | 2587778.9391 | 1180839.8744
67 | 2587768.2027 | 1180816.8415 | 2587768.2027 | 1180816.8415 | 2587765.7378 | 1180802.6728
68 | 2587781.7314 | 1180859.4467 | 2587790.2914 | 1180858.8955 | 2587801.6801 | 1180857.7691
69 | 2587781.7314 | 1180859.4467 | 2587783.3635 | 1180876.9412 | 2587784.7224 | 1180881.6378
70 | 2587765.0846 | 1180798.9179 | 2587765.7378 | 1180802.6728
71 | 2587801.6801 | 1180857.7691 | 2587813.6265 | 1180856.5875
72 | 2587789.9244 | 1180899.6172 | 2587784.7224 | 1180881.6378
73 | 2587765.0846 | 1180798.9179 | 2587764.9104 | 1180797.9163 | 2587764.9843 | 1180794.6447
74 | 2587789.9244 | 1180899.6172 | 2587768.0777 | 1180912.124 | 2587733.2063 | 1180933.8735 | 2587716.9824 | 1180946.8181
75 | 2587789.9244 | 1180899.6172 | 2587802.3883 | 1180892.3323
76 | 2587657.7883 | 1181229.9814 | 2587650.3432 | 1181214.2532
77 | 2587664.3755 | 1181243.897 | 2587657.7883 | 1181229.9814
78 | 2587649.9691 | 1181209.9896 | 2587650.155 | 1181213.8555 | 2587650.3432 | 1181214.2532
79 | 2587650.0855 | 1181195.3367 | 2587649.5165 | 1181200.5723 | 2587649.9691 | 1181209.9896
80 | 2587631.4219 | 1181298.2561 | 2587625.9412 | 1181302.9404 | 2587587.7848 | 1181332.8663
81 | 2587863.9274 | 1180916.3638 | 2587869.7941 | 1180919.3641 | 2587882.8362 | 1180922.2168 | 2587894.0657 | 1180920.0261 | 2587898.258 | 1180917.9338
82 | 2587855.4827 | 1180912.0451 | 2587863.9274 | 1180916.3638
83 | 2587855.4827 | 1180912.0451 | 2587860.6972 | 1180926.2195 | 2587861.6121 | 1180936.723 | 2587853.1194 | 1180955.2054
84 | 2588404.4591 | 1181253.059 | 2588404.3066 | 1181257.0613 | 2588406.7907 | 1181262.1369 | 2588407.3822 | 1181262.8783
85 | 2588404.4591 | 1181253.059 | 2588396.7352 | 1181251.3287 | 2588391.4772 | 1181249.2156 | 2588385.6814 | 1181245.5028 | 2588377.783 | 1181238.8674
86 | 2588079.7802 | 1181308.3063 | 2588377.783 | 1181238.8674
87 | 2587640.1516 | 1181004.491 | 2587520.8199 | 1181008.26
88 | 2587715.3118 | 1180948.1511 | 2587705.8902 | 1180945.5692 | 2587679.7564 | 1180967.6012 | 2587640.1516 | 1181004.491
89 | 2587762.1557 | 1181027.4885 | 2587762.6699 | 1181028.509
90 | 2587783.6864 | 1180954.0273 | 2587783.1863 | 1180958.0387 | 2587779.1795 | 1180985.3388 | 2587773.7482 | 1180995.7997 | 2587762.2152 | 1181006.2732 | 2587759.5642 | 1181016.9397 | 2587760.0048 | 1181023.2198 | 2587762.1557 | 1181027.4885
91 | 2587783.6864 | 1180954.0273 | 2587785.6055 | 1180938.6349 | 2587789.7898 | 1180929.0992
92 | 2587802.3883 | 1180892.3323 | 2587801.5762 | 1180902.2391 | 2587789.7898 | 1180929.0992
93 | 2587508.244 | 1181395.7116 | 2587499.9876 | 1181391.36 | 2587484.8162 | 1181388.7127 | 2587475.8928 | 1181384.3556
94 | 2587508.244 | 1181395.7116 | 2587491.5103 | 1181412.7443 | 2587483.2149 | 1181422.5334 | 2587475.3855 | 1181432.4105 | 2587465.0072 | 1181446.6286 | 2587457.0771 | 1181459.4296 | 2587450.6827 | 1181472.572 | 2587445.8383 | 1181485.5889 | 2587443.1095 | 1181495.1996 | 2587441.1598 | 1181504.9087 | 2587439.5746 | 1181520.8425 | 2587438.9095 | 1181534.9845 | 2587438.3836 | 1181554.7468
95 | 2587508.244 | 1181395.7116 | 2587528.1028 | 1181379.5616 | 2587548.4283 | 1181363.7332 | 2587550.4967 | 1181362.111
96 | 2587437.5807 | 1181577.953 | 2587437.9331 | 1181571.6721 | 2587438.3836 | 1181554.7468
97 | 2587550.4967 | 1181362.111 | 2587587.7848 | 1181332.8663
98 | 2587437.5807 | 1181577.953 | 2587437.3215 | 1181582.5712
99 | 2588076.3857 | 1181302.5546 | 2588077.9631 | 1181304.697 | 2588079.7802 | 1181308.3063
100 | 2588089.2996 | 1181357.7954 | 2588080.849 | 1181311.9838 | 2588079.7802 | 1181308.3063
101 | 2587802.3883 | 1180892.3323 | 2587813.2474 | 1180886.5211
102 | 2587715.3118 | 1180948.1511 | 2587716.9824 | 1180946.8181
103 | 2588076.3857 | 1181302.5546 | 2588075.8359 | 1181298.7649 | 2588074.8015 | 1181297.0327 | 2588073.462 | 1181295.479 | 2588070.572 | 1181293.7728 | 2588033.4274 | 1181278.2394 | 2588014.1843 | 1181267.2836 | 2587992.5911 | 1181246.0051 | 2587960.766 | 1181210.251 | 2587952.5655 | 1181203.2751 | 2587941.2016 | 1181199.6255
104 | 2588284.7838 | 1181581.1395 | 2588284.2836 | 1181598.5939 | 2588284.7564 | 1181609.8654 | 2588285.8382 | 1181620.2241 | 2588289.0912 | 1181635.7702 | 2588295.6441 | 1181663.5604
105 | 2588416.4466 | 1181900.6073 | 2588414.043 | 1181900.0837 | 2588406.0487 | 1181896.3307 | 2588401.8501 | 1181895.3155
106 | 2588438.2143 | 1181902.2823 | 2588432.9895 | 1181901.2808 | 2588421.934 | 1181901.8026 | 2588416.4466 | 1181900.6073
107 | 2588393.4341 | 1181896.0996 | 2588401.4422 | 1181895.2168 | 2588401.8501 | 1181895.3155
108 | 2588438.2143 | 1181902.2823 | 2588442.7279 | 1181906.6646 | 2588446.4298 | 1181913.8056 | 2588446.6472 | 1181919.6192 | 2588446.042 | 1181926.4684
109 | 2588438.2143 | 1181902.2823 | 2588443.4319 | 1181899.6263
110 | 2588393.4341 | 1181896.0996 | 2588389.2001 | 1181896.1033
111 | 2588446.042 | 1181926.4684 | 2588443.699 | 1181930.9641 | 2588439.9159 | 1181933.117 | 2588433.563 | 1181933.1294 | 2588422.0368 | 1181930.8075
112 | 2588389.2001 | 1181896.1033 | 2588295.6441 | 1181663.5604
113 | 2588389.2001 | 1181896.1033 | 2588201.6304 | 1181906.6376
114 | 2588416.1726 | 1181929.6262 | 2588422.0368 | 1181930.8075
115 | 2587437.3215 | 1181582.5712 | 2587437.2855 | 1181583.2127 | 2587437.1102 | 1181584.3896
116 | 2587436.4893 | 1181588.5573 | 2587437.1102 | 1181584.3896
117 | 2588201.6304 | 1181906.6376 | 2588208.6989 | 1181920.9532 | 2588210.7226 | 1181928.7754 | 2588211.1171 | 1181939.0243 | 2588211.0514 | 1182052.3272 | 2588210.104 | 1182072.7614

## bus_geodata
| x | y | coords
0 | 2588731.1075 | 1181486.1803
1 | 2588725.7738 | 1181474.5221
2 | 2588720.1877 | 1181478.9224
3 | 2588736.0699 | 1181459.6838
4 | 2588797.7691 | 1181480.2447
5 | 2588663.9634 | 1181249.7909
6 | 2588708.6707 | 1181491.73
7 | 2589084.0715 | 1181568.0164
8 | 2588631.8441 | 1180775.4395
9 | 2588640.9508 | 1180790.8437
10 | 2588603.5687 | 1180759.7881
11 | 2588715.5524 | 1180804.0308
12 | 2588607.3283 | 1180768.8634
13 | 2588599.1019 | 1180756.2727
14 | 2588704.2272 | 1180808.3879
15 | 2588567.0584 | 1180733.5002
16 | 2588602.786 | 1180748.5656
17 | 2588595.4906 | 1181262.8394
18 | 2588573.576 | 1181224.2283
19 | 2588610.4381 | 1181216.4425
20 | 2588428.7121 | 1181233.0682
21 | 2588532.5549 | 1180713.0916
22 | 2588532.4612 | 1180713.0466
23 | 2588180.8373 | 1180721.2977
24 | 2588551.5538 | 1180736.9095
25 | 2588153.0859 | 1180755.6142
26 | 2588073.2552 | 1180788.8817
27 | 2588051.3095 | 1180796.0301
28 | 2588014.4441 | 1180808.0382
29 | 2587942.9841 | 1180831.3147
30 | 2587937.8991 | 1180836.1668
31 | 2587385.347 | 1180837.5985
32 | 2587519.5699 | 1180999.3559
33 | 2587494.5113 | 1180638.3628
34 | 2587414.3468 | 1180611.6179
35 | 2589083.4541 | 1181573.4282
36 | 2589082.327 | 1181583.3798
37 | 2587839.4025 | 1180872.5243
38 | 2587847.1565 | 1180896.1539
39 | 2587829.8288 | 1180859.1147
40 | 2587911.1399 | 1180855.5734
41 | 2587730.9448 | 1181329.7253
42 | 2587778.0927 | 1181340.1389
43 | 2587723.3033 | 1181327.3848
44 | 2587832.2175 | 1181368.3049
45 | 2587670.9086 | 1181270.9452
46 | 2587732.6054 | 1181319.3095
47 | 2587835.4702 | 1181369.8615
48 | 2587660.8036 | 1181255.944
49 | 2587233.5549 | 1181341.7554
50 | 2587251.4257 | 1181339.0409
51 | 2587261.7265 | 1181339.405
52 | 2587391.867 | 1181356.7741
53 | 2587944.1025 | 1181636.7985
54 | 2587937.7016 | 1181605.2556
55 | 2587952.3906 | 1181649.4449
56 | 2587926.3959 | 1181568.9492
57 | 2587983.0699 | 1181676.0288
58 | 2588094.388 | 1181385.2717
59 | 2587900.6532 | 1180864.2846
60 | 2587778.9391 | 1180839.8744
61 | 2587768.2027 | 1180816.8415
62 | 2587781.7314 | 1180859.4467
63 | 2587765.7378 | 1180802.6728
64 | 2587801.6801 | 1180857.7691
65 | 2587784.7224 | 1180881.6378
66 | 2587765.0846 | 1180798.9179
67 | 2587813.6265 | 1180856.5875
68 | 2587789.9244 | 1180899.6172
69 | 2587657.7883 | 1181229.9814
70 | 2587650.3432 | 1181214.2532
71 | 2587664.3755 | 1181243.897
72 | 2587649.9691 | 1181209.9896
73 | 2587650.0855 | 1181195.3367
74 | 2587631.4219 | 1181298.2561
75 | 2587898.258 | 1180917.9338
76 | 2587863.9274 | 1180916.3638
77 | 2587855.4827 | 1180912.0451
78 | 2587853.1194 | 1180955.2054
79 | 2588404.4591 | 1181253.059
80 | 2588407.3822 | 1181262.8783
81 | 2588377.783 | 1181238.8674
82 | 2587520.8199 | 1181008.26
83 | 2587640.1516 | 1181004.491
84 | 2587762.6699 | 1181028.509
85 | 2587762.1557 | 1181027.4885
86 | 2587783.6864 | 1180954.0273
87 | 2587789.7898 | 1180929.0992
88 | 2587475.8928 | 1181384.3556
89 | 2587508.244 | 1181395.7116
90 | 2587438.3836 | 1181554.7468
91 | 2587550.4967 | 1181362.111
92 | 2587587.7848 | 1181332.8663
93 | 2587437.5807 | 1181577.953
94 | 2588079.7802 | 1181308.3063
95 | 2587813.2474 | 1180886.5211
96 | 2587802.3883 | 1180892.3323
97 | 2587716.9824 | 1180946.8181
98 | 2588089.2996 | 1181357.7954
99 | 2588076.3857 | 1181302.5546
100 | 2588284.7838 | 1181581.1395
101 | 2587941.2016 | 1181199.6255
102 | 2588416.4466 | 1181900.6073
103 | 2588401.8501 | 1181895.3155
104 | 2588438.2143 | 1181902.2823
105 | 2588393.4341 | 1181896.0996
106 | 2588446.042 | 1181926.4684
107 | 2588443.4319 | 1181899.6263
108 | 2588389.2001 | 1181896.1033
109 | 2588422.0368 | 1181930.8075
110 | 2587437.3215 | 1181582.5712
111 | 2587437.1102 | 1181584.3896
112 | 2588295.6441 | 1181663.5604
113 | 2588201.6304 | 1181906.6376
114 | 2588416.1726 | 1181929.6262
115 | 2587436.4893 | 1181588.5573
116 | 2587764.9843 | 1180794.6447
117 | 2587715.3118 | 1180948.1511
118 | 2588210.104 | 1182072.7614
119 | 2587941.2016 | 1181199.6255

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98418 | -0.11251 | 0.00056028 | 0.00014042
1 | 0.9842 | -0.11243 | 0 | 0
2 | 0.98419 | -0.11249 | 0.00059342 | 0.00014872
3 | 0.98424 | -0.11213 | 0 | 0
4 | 0.9839 | -0.11454 | 0.0027465 | 0.00068835
5 | 0.98575 | -0.10125 | 0.00014817 | 3.7135e-05
6 | 0.98418 | -0.11252 | 0.00016231 | 4.068e-05
7 | 0.98362 | -0.1166 | 0.00033999 | 8.5209e-05
8 | 0.97975 | -0.14467 | 0.0010313 | 0.00025847
9 | 0.97996 | -0.14313 | 0 | 0
10 | 0.97938 | -0.14736 | 0 | 0
11 | 0.98088 | -0.1365 | 0 | 0
12 | 0.97936 | -0.14753 | 0.0016615 | 0.00041641
13 | 0.97932 | -0.1478 | 0 | 0
14 | 0.98102 | -0.13546 | 0.00037747 | 9.4602e-05
15 | 0.97891 | -0.15076 | 0 | 0
16 | 0.97932 | -0.14783 | 0.00033827 | 8.4778e-05
17 | 0.98625 | -0.097699 | 0 | 0
18 | 0.98656 | -0.095431 | 0 | 0
19 | 0.98605 | -0.099088 | 0.0010885 | 0.00027281
20 | 0.98876 | -0.07962 | 0 | 0
21 | 0.97851 | -0.15373 | 0.00012832 | 3.216e-05
22 | 0.97851 | -0.15374 | 0.00015581 | 3.905e-05
23 | 0.97499 | -0.17941 | 0.0019974 | 0.00050059
24 | 0.9789 | -0.15084 | 0.00045946 | 0.00011515
25 | 0.97459 | -0.18235 | 0.00051496 | 0.00012906
26 | 0.97382 | -0.18795 | 0.00063095 | 0.00015813
27 | 0.97362 | -0.18938 | 0.00011929 | 2.9898e-05
28 | 0.9733 | -0.19177 | 0.00079831 | 0.00020008
29 | 0.97269 | -0.1962 | 0 | 0
30 | 0.97264 | -0.19661 | 0.00066983 | 0.00016788
31 | 0.97038 | -0.21337 | 0.0020655 | 0.00051766
32 | 0.97067 | -0.21125 | 0.00011657 | 2.9214e-05
33 | 0.97031 | -0.21395 | 0 | 0
34 | 0.97021 | -0.21465 | 0.00068355 | 0.00017131
35 | 0.98362 | -0.11661 | 0 | 0
36 | 0.98361 | -0.11665 | 0.00031067 | 7.7861e-05
37 | 0.97173 | -0.20327 | 0 | 0
38 | 0.97188 | -0.20222 | 0 | 0
39 | 0.97164 | -0.20397 | 0.00040588 | 0.00010172
40 | 0.97238 | -0.19851 | 0.0019463 | 0.00048779
41 | 0.97404 | -0.18375 | 0.00063392 | 0.00015888
42 | 0.97496 | -0.17714 | 0.0013585 | 0.00034047
43 | 0.9739 | -0.18478 | 0 | 0
44 | 0.97621 | -0.16809 | 0.00081825 | 0.00020507
45 | 0.97259 | -0.1942 | 0.00038199 | 9.5737e-05
46 | 0.97389 | -0.18485 | 0.00058868 | 0.00014754
47 | 0.97629 | -0.16752 | 0.00014692 | 3.6823e-05
48 | 0.9723 | -0.19633 | 0 | 0
49 | 0.97013 | -0.21216 | 0.00030249 | 7.5812e-05
50 | 0.97013 | -0.2121 | 0.00021298 | 5.3377e-05
51 | 0.97014 | -0.21204 | 0.00024081 | 6.0352e-05
52 | 0.97029 | -0.21098 | 0.00067696 | 0.00016966
53 | 0.98268 | -0.12189 | 0.0020444 | 0.00051239
54 | 0.98195 | -0.12708 | 0.00032515 | 8.1491e-05
55 | 0.98306 | -0.11914 | 0.0004004 | 0.00010035
56 | 0.98111 | -0.13304 | 0 | 0
57 | 0.98293 | -0.12011 | 0.0023019 | 0.00057691
58 | 0.99187 | -0.057046 | 0.00056322 | 0.00014116
59 | 0.97229 | -0.19919 | 0.00029792 | 7.4665e-05
60 | 0.9713 | -0.20642 | 0.0015073 | 0.00037776
61 | 0.97126 | -0.20676 | 0.00020965 | 5.2542e-05
62 | 0.97138 | -0.20585 | 0 | 0
63 | 0.97124 | -0.20692 | 0.00010879 | 2.7266e-05
64 | 0.97148 | -0.20513 | 0.0012221 | 0.0003063
65 | 0.97131 | -0.20643 | 0.00040227 | 0.00010082
66 | 0.97123 | -0.20695 | 0.00027499 | 6.8918e-05
67 | 0.97155 | -0.20465 | 0.0002604 | 6.5263e-05
68 | 0.97125 | -0.20689 | 0 | 0
69 | 0.97213 | -0.19757 | 0.003194 | 0.0008005
70 | 0.9721 | -0.19776 | 0.00012436 | 3.1167e-05
71 | 0.97222 | -0.19689 | 0 | 0
72 | 0.9721 | -0.1978 | 0.00035835 | 8.9811e-05
73 | 0.97208 | -0.19788 | 0.00053002 | 0.00013284
74 | 0.97177 | -0.20015 | 0.00081927 | 0.00020533
75 | 0.97179 | -0.20288 | 0.00050628 | 0.00012688
76 | 0.97181 | -0.20268 | 0.00068942 | 0.00017279
77 | 0.97183 | -0.20256 | 0 | 0
78 | 0.97179 | -0.20285 | 0.00058449 | 0.00014649
79 | 0.98924 | -0.07617 | 0 | 0
80 | 0.98923 | -0.076253 | 0.00076321 | 0.00019128
81 | 0.98971 | -0.072805 | 0.0025091 | 0.00062884
82 | 0.97068 | -0.21116 | 0.00054387 | 0.00013631
83 | 0.97088 | -0.20966 | 0.00052689 | 0.00013205
84 | 0.97092 | -0.20927 | 0.00070523 | 0.00017675
85 | 0.97092 | -0.20926 | 0.00030162 | 7.5593e-05
86 | 0.97104 | -0.2084 | 0.00039509 | 9.9018e-05
87 | 0.97109 | -0.20801 | 0.00032975 | 8.2642e-05
88 | 0.97047 | -0.20961 | 0.00056331 | 0.00014118
89 | 0.97058 | -0.20887 | 0 | 0
90 | 0.97009 | -0.21242 | 0.0004506 | 0.00011293
91 | 0.97088 | -0.20665 | 0.0018802 | 0.00047121
92 | 0.97128 | -0.20375 | 0.00034171 | 8.5642e-05
93 | 0.97004 | -0.21276 | 0.00036092 | 9.0456e-05
94 | 0.99475 | -0.036894 | 0.00038056 | 9.5376e-05
95 | 0.97117 | -0.2074 | 0.00086479 | 0.00021674
96 | 0.97119 | -0.20728 | 0 | 0
97 | 0.97107 | -0.20821 | 0.00016368 | 4.1023e-05
98 | 0.99288 | -0.049976 | 0.00071027 | 0.00017801
99 | 0.99494 | -0.035523 | 0 | 0
100 | 0.99028 | -0.068554 | 0 | 0
101 | 1 | 0 | -0.061805 | -0.015304
102 | 0.98854 | -0.081064 | 0.00014291 | 3.5816e-05
103 | 0.98858 | -0.080768 | 7.842e-05 | 1.9654e-05
104 | 0.98848 | -0.081448 | 0 | 0
105 | 0.9886 | -0.080601 | 0 | 0
106 | 0.98843 | -0.081847 | 0 | 0
107 | 0.98848 | -0.081464 | 0.00026294 | 6.59e-05
108 | 0.98862 | -0.080517 | 0.00022149 | 5.5512e-05
109 | 0.98837 | -0.082252 | 0.00015358 | 3.849e-05
110 | 0.97003 | -0.21281 | 0.00054345 | 0.0001362
111 | 0.97003 | -0.21282 | 0.00023144 | 5.8004e-05
112 | 0.98979 | -0.07207 | 0.00080915 | 0.00020279
113 | 0.98832 | -0.082678 | 0 | 0
114 | 0.98836 | -0.082331 | 0.0012865 | 0.00032242
115 | 0.97003 | -0.21283 | 0.00025718 | 6.4455e-05
116 | 0.97123 | -0.20698 | 0.00064632 | 0.00016198
117 | 0.97107 | -0.20824 | 0 | 0
118 | 0.98805 | -0.084583 | 0.0011011 | 0.00027596
119 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00056028 | -0.00014042 | 0.00056029 | 0.00014025 | 6.0079e-09 | -1.682e-07 | 0.00084711 | 0.00084705 | 0.00084711 | 0.98418 | -0.11251 | 0.9842 | -0.11243 | 0.31374
1 | 0.00075574 | 0.0001891 | -0.00075573 | -0.00018919 | 5.7922e-09 | -8.8138e-08 | 0.0011425 | 0.0011425 | 0.0011425 | 0.9842 | -0.11243 | 0.98419 | -0.11249 | 0.42316
2 | -0.001316 | -0.00032935 | 0.0013161 | 0.00032909 | 5.4195e-08 | -2.5801e-07 | 0.0019895 | 0.0019894 | 0.0019895 | 0.9842 | -0.11243 | 0.98424 | -0.11213 | 0.73687
3 | 0.00016231 | 4.0461e-05 | -0.00016231 | -4.068e-05 | 6.4789e-10 | -2.189e-07 | 0.00024533 | 0.00024541 | 0.00024541 | 0.98419 | -0.11249 | 0.98418 | -0.11252 | 0.090892
4 | 0.0033985 | 0.00084706 | -0.0033974 | -0.00084749 | 1.1205e-06 | -4.3372e-07 | 0.0051363 | 0.0051367 | 0.0051367 | 0.98424 | -0.11213 | 0.9839 | -0.11454 | 1.9025
5 | -0.0047146 | -0.0011761 | 0.0047216 | 0.001176 | 7.0309e-06 | -1.2068e-07 | 0.0071258 | 0.0071248 | 0.0071258 | 0.98424 | -0.11213 | 0.98575 | -0.10125 | 2.6392
6 | 0.00065084 | 0.00015914 | -0.00065066 | -0.00016288 | 1.8077e-07 | -3.7325e-06 | 0.00098291 | 0.00098425 | 0.00098425 | 0.9839 | -0.11454 | 0.98362 | -0.1166 | 0.36454
7 | -0.0048698 | -0.0012132 | 0.0048721 | 0.0012132 | 2.3666e-06 | 1.4393e-08 | 0.0073485 | 0.0073481 | 0.0073485 | 0.98575 | -0.10125 | 0.98625 | -0.097699 | 2.7217
8 | 0.00031067 | 7.7666e-05 | -0.00031067 | -7.7735e-05 | 7.5056e-10 | -6.8849e-08 | 0.00046991 | 0.00046994 | 0.00046994 | 0.98362 | -0.1166 | 0.98362 | -0.11661 | 0.17405
9 | -0.024425 | -0.0060724 | 0.02443 | 0.0060736 | 5.128e-06 | 1.2947e-06 | 0.037079 | 0.037078 | 0.037079 | 0.97975 | -0.14467 | 0.97996 | -0.14313 | 4.5776
10 | 0.023394 | 0.0058139 | -0.023385 | -0.0058118 | 8.5674e-06 | 2.0617e-06 | 0.035512 | 0.035513 | 0.035513 | 0.97975 | -0.14467 | 0.97938 | -0.14736 | 4.3843
11 | -0.02443 | -0.0060736 | 0.024452 | 0.0060792 | 2.2101e-05 | 5.5763e-06 | 0.037078 | 0.037077 | 0.037078 | 0.97996 | -0.14313 | 0.98088 | -0.1365 | 4.5776
12 | 0.0016615 | 0.00041631 | -0.0016615 | -0.00041641 | 3.9055e-08 | -1.0856e-07 | 0.0025244 | 0.0025245 | 0.0025245 | 0.97938 | -0.14736 | 0.97936 | -0.14753 | 0.93499
13 | 0.021724 | 0.0053955 | -0.021722 | -0.0053952 | 1.2846e-06 | 2.7983e-07 | 0.032988 | 0.032988 | 0.032988 | 0.97938 | -0.14736 | 0.97932 | -0.1478 | 4.0726
14 | -0.024452 | -0.0060792 | 0.024456 | 0.0060801 | 3.4611e-06 | 8.7276e-07 | 0.037077 | 0.037077 | 0.037077 | 0.98088 | -0.1365 | 0.98102 | -0.13546 | 4.5775
15 | 0.021384 | 0.0053106 | -0.021376 | -0.0053087 | 8.6074e-06 | 1.83e-06 | 0.032475 | 0.032475 | 0.032475 | 0.97932 | -0.1478 | 0.97891 | -0.15076 | 4.0093
16 | 0.00033827 | 8.4671e-05 | -0.00033827 | -8.4778e-05 | 1.4081e-09 | -1.0694e-07 | 0.00051394 | 0.00051398 | 0.00051398 | 0.97932 | -0.1478 | 0.97932 | -0.14783 | 0.19036
17 | -0.024833 | -0.0061747 | 0.024957 | 0.0062062 | 0.00012343 | 3.1532e-05 | 0.03765 | 0.037644 | 0.03765 | 0.98102 | -0.13546 | 0.98605 | -0.099088 | 4.6481
18 | 0.00045946 | 0.00011495 | -0.00045946 | -0.00011515 | 4.8284e-09 | -1.9759e-07 | 0.00069834 | 0.00069841 | 0.00069841 | 0.97891 | -0.15076 | 0.9789 | -0.15084 | 0.25867
19 | 0.020916 | 0.0051938 | -0.020908 | -0.0051921 | 8.4513e-06 | 1.7335e-06 | 0.031777 | 0.031777 | 0.031777 | 0.97891 | -0.15076 | 0.97851 | -0.15373 | 3.9231
20 | -0.0048721 | -0.0012132 | 0.0048737 | 0.0012132 | 1.5103e-06 | 8.6753e-09 | 0.0073481 | 0.0073479 | 0.0073481 | 0.98625 | -0.097699 | 0.98656 | -0.095431 | 2.7215
21 | 0.026058 | 0.0064825 | -0.026045 | -0.006479 | 1.2999e-05 | 3.4492e-06 | 0.039286 | 0.039287 | 0.039287 | 0.98656 | -0.095431 | 0.98605 | -0.099088 | 4.8502
22 | -0.030932 | -0.0076957 | 0.030999 | 0.0077157 | 6.6833e-05 | 2.0032e-05 | 0.046634 | 0.046632 | 0.046634 | 0.98656 | -0.095431 | 0.98876 | -0.07962 | 5.7573
23 | -0.030999 | -0.0077157 | 0.031013 | 0.0077201 | 1.461e-05 | 4.3757e-06 | 0.046632 | 0.046632 | 0.046632 | 0.98876 | -0.07962 | 0.98924 | -0.07617 | 5.7571
24 | 0.020779 | 0.0051599 | -0.020779 | -0.0051599 | 2.1573e-08 | 4.3778e-09 | 0.031582 | 0.031582 | 0.031582 | 0.97851 | -0.15373 | 0.97851 | -0.15374 | 3.899
25 | 0.020624 | 0.0051208 | -0.020552 | -0.0051064 | 7.189e-05 | 1.4443e-05 | 0.031345 | 0.03135 | 0.03135 | 0.97851 | -0.15374 | 0.97499 | -0.17941 | 3.8704
26 | 0.018554 | 0.0046058 | -0.018547 | -0.0046046 | 7.3987e-06 | 1.1849e-06 | 0.028302 | 0.028302 | 0.028302 | 0.97499 | -0.17941 | 0.97459 | -0.18235 | 3.4941
27 | 0.018032 | 0.0044756 | -0.018018 | -0.0044735 | 1.3713e-05 | 2.0217e-06 | 0.027516 | 0.027517 | 0.027517 | 0.97459 | -0.18235 | 0.97382 | -0.18795 | 3.3972
28 | 0.017387 | 0.0043154 | -0.017384 | -0.004315 | 3.3849e-06 | 4.4058e-07 | 0.026553 | 0.026553 | 0.026553 | 0.97382 | -0.18795 | 0.97362 | -0.18938 | 3.2782
29 | 0.017265 | 0.0042851 | -0.017259 | -0.0042844 | 5.6084e-06 | 7.1101e-07 | 0.026371 | 0.026371 | 0.026371 | 0.97362 | -0.18938 | 0.9733 | -0.19177 | 3.2557
30 | 0.016461 | 0.0040843 | -0.016451 | -0.0040833 | 9.8889e-06 | 1.0031e-06 | 0.025151 | 0.025152 | 0.025152 | 0.9733 | -0.19177 | 0.97269 | -0.1962 | 3.1052
31 | 0.016451 | 0.0040833 | -0.01645 | -0.0040832 | 9.2485e-07 | 9.4e-08 | 0.025152 | 0.025152 | 0.025152 | 0.97269 | -0.1962 | 0.97264 | -0.19661 | 3.1052
32 | 0.01578 | 0.0039153 | -0.015776 | -0.003915 | 4.0663e-06 | 3.139e-07 | 0.024127 | 0.024128 | 0.024128 | 0.97264 | -0.19661 | 0.97238 | -0.19851 | 2.9787
33 | -0.0027491 | -0.00067942 | 0.0027499 | 0.00067192 | 7.7519e-07 | -7.4941e-06 | 0.0042122 | 0.0042094 | 0.0042122 | 0.97038 | -0.21337 | 0.97067 | -0.21125 | 0.52002
34 | 0.00068367 | 0.00016176 | -0.00068362 | -0.00017016 | 5.1745e-08 | -8.3991e-06 | 0.001045 | 0.0010479 | 0.0010479 | 0.97038 | -0.21337 | 0.97031 | -0.21395 | 0.12937
35 | -0.0028665 | -0.00070114 | 0.0028665 | 0.00070082 | 3.6011e-08 | -3.1958e-07 | 0.0043881 | 0.004388 | 0.0043881 | 0.97067 | -0.21125 | 0.97068 | -0.21116 | 0.54174
36 | 0.00068362 | 0.00017016 | -0.00068355 | -0.00017131 | 6.5408e-08 | -1.1532e-06 | 0.0010479 | 0.0010484 | 0.0010484 | 0.97031 | -0.21395 | 0.97021 | -0.21465 | 0.38828
37 | 0.00031067 | 7.7735e-05 | -0.00031067 | -7.7861e-05 | 1.3805e-09 | -1.2661e-07 | 0.00046994 | 0.00046998 | 0.00046998 | 0.98362 | -0.11661 | 0.98361 | -0.11665 | 0.17407
38 | -0.011743 | -0.0029082 | 0.011745 | 0.0029079 | 1.6702e-06 | -2.8196e-07 | 0.017969 | 0.017969 | 0.017969 | 0.97173 | -0.20327 | 0.97188 | -0.20222 | 2.2184
39 | 0.011743 | 0.0029082 | -0.011742 | -0.0029084 | 1.1084e-06 | -1.8696e-07 | 0.017969 | 0.01797 | 0.01797 | 0.97173 | -0.20327 | 0.97164 | -0.20397 | 2.2185
40 | -0.013525 | -0.0033527 | 0.01353 | 0.0033526 | 5.5593e-06 | -1.8297e-07 | 0.020694 | 0.020694 | 0.020694 | 0.97188 | -0.20222 | 0.97229 | -0.19919 | 2.5549
41 | 0.0017803 | 0.00044485 | -0.0017802 | -0.00044504 | 8.3479e-08 | -1.9107e-07 | 0.0027253 | 0.0027254 | 0.0027254 | 0.97188 | -0.20222 | 0.97183 | -0.20256 | 1.0094
42 | 0.011336 | 0.0028066 | -0.011335 | -0.0028069 | 1.0461e-06 | -2.1852e-07 | 0.017348 | 0.017348 | 0.017348 | 0.97164 | -0.20397 | 0.97155 | -0.20465 | 2.1418
43 | 0.01383 | 0.0034272 | -0.013828 | -0.0034272 | 1.2703e-06 | -1.9475e-08 | 0.021149 | 0.02115 | 0.02115 | 0.97238 | -0.19851 | 0.97229 | -0.19919 | 2.6111
44 | -0.012725 | -0.0031825 | 0.012737 | 0.0031864 | 1.1616e-05 | 3.8537e-06 | 0.019437 | 0.019437 | 0.019437 | 0.97404 | -0.18375 | 0.97496 | -0.17714 | 7.1989
45 | 0.012091 | 0.0030236 | -0.012089 | -0.0030231 | 1.7057e-06 | 5.563e-07 | 0.018469 | 0.018469 | 0.018469 | 0.97404 | -0.18375 | 0.9739 | -0.18478 | 6.8403
46 | -0.014095 | -0.0035268 | 0.014113 | 0.0035328 | 1.7621e-05 | 6.0153e-06 | 0.02151 | 0.02151 | 0.02151 | 0.97496 | -0.17714 | 0.97621 | -0.16809 | 7.9668
47 | 0.011501 | 0.0028757 | -0.011486 | -0.0028709 | 1.492e-05 | 4.776e-06 | 0.017569 | 0.01757 | 0.01757 | 0.9739 | -0.18478 | 0.97259 | -0.1942 | 6.5073
48 | 0.00058869 | 0.00014739 | -0.00058868 | -0.00014754 | 6.2182e-09 | -1.5089e-07 | 0.0008994 | 0.00089945 | 0.00089945 | 0.9739 | -0.18478 | 0.97389 | -0.18485 | 0.33313
49 | -0.014931 | -0.0037379 | 0.014932 | 0.0037383 | 1.1653e-06 | 4.0312e-07 | 0.022757 | 0.022757 | 0.022757 | 0.97621 | -0.16809 | 0.97629 | -0.16752 | 8.4286
50 | 0.011104 | 0.0027752 | -0.0111 | -0.0027741 | 3.2561e-06 | 1.028e-06 | 0.016985 | 0.016985 | 0.016985 | 0.97259 | -0.1942 | 0.9723 | -0.19633 | 6.2909
51 | -0.015079 | -0.0037751 | 0.015151 | 0.0038001 | 7.2126e-05 | 2.499e-05 | 0.022981 | 0.02298 | 0.022981 | 0.97629 | -0.16752 | 0.98111 | -0.13304 | 8.5115
52 | 0.0068929 | 0.0017203 | -0.0068893 | -0.0017196 | 3.6125e-06 | 7.4424e-07 | 0.010546 | 0.010547 | 0.010547 | 0.9723 | -0.19633 | 0.97177 | -0.20015 | 3.9061
53 | 0.0042075 | 0.0010538 | -0.0042072 | -0.0010538 | 3.2507e-07 | -3.0797e-08 | 0.006439 | 0.006439 | 0.006439 | 0.9723 | -0.19633 | 0.97222 | -0.19689 | 2.3848
54 | -0.00030249 | -7.5812e-05 | 0.00030249 | 7.5587e-05 | 2.4571e-09 | -2.2495e-07 | 0.00046397 | 0.00046389 | 0.00046397 | 0.97013 | -0.21216 | 0.97013 | -0.2121 | 0.17184
55 | -0.00051547 | -0.00012896 | 0.00051547 | 0.00012884 | 4.0195e-09 | -1.2572e-07 | 0.00079056 | 0.00079051 | 0.00079056 | 0.97013 | -0.2121 | 0.97014 | -0.21204 | 0.2928
56 | -0.00075628 | -0.00018919 | 0.00075639 | 0.00018761 | 1.1048e-07 | -1.5836e-06 | 0.0011599 | 0.0011593 | 0.0011599 | 0.97014 | -0.21204 | 0.97029 | -0.21098 | 0.42958
57 | -0.0014334 | -0.00035727 | 0.0014336 | 0.00035628 | 2.6672e-07 | -9.9111e-07 | 0.0021975 | 0.0021971 | 0.0021975 | 0.97029 | -0.21098 | 0.97047 | -0.20961 | 0.81387
58 | 0.0155 | 0.0038898 | -0.015489 | -0.003886 | 1.1147e-05 | 3.8768e-06 | 0.023473 | 0.023473 | 0.023473 | 0.98268 | -0.12189 | 0.98195 | -0.12708 | 8.6936
59 | -0.017544 | -0.0044022 | 0.017551 | 0.0044046 | 6.7069e-06 | 2.3866e-06 | 0.026568 | 0.026568 | 0.026568 | 0.98268 | -0.12189 | 0.98306 | -0.11914 | 9.8401
60 | 0.015164 | 0.0038045 | -0.015151 | -0.0038001 | 1.2539e-05 | 4.3417e-06 | 0.02298 | 0.02298 | 0.02298 | 0.98195 | -0.12708 | 0.98111 | -0.13304 | 8.5112
61 | 0.0023022 | 0.00057651 | -0.0023019 | -0.00057691 | 3.0772e-07 | -3.9648e-07 | 0.0034846 | 0.0034847 | 0.0034847 | 0.98306 | -0.11914 | 0.98293 | -0.12011 | 1.2906
62 | -0.020254 | -0.0050815 | 0.02043 | 0.0051453 | 0.00017591 | 6.382e-05 | 0.030659 | 0.030658 | 0.030659 | 0.98306 | -0.11914 | 0.99187 | -0.057046 | 11.3552
63 | 0.0040691 | 0.0010077 | -0.0040628 | -0.0010088 | 6.3443e-06 | -1.0798e-06 | 0.0061003 | 0.0061015 | 0.0061015 | 0.99187 | -0.057046 | 0.99028 | -0.068554 | 2.2598
64 | -0.025062 | -0.0062942 | 0.025087 | 0.0063033 | 2.4655e-05 | 9.1216e-06 | 0.037603 | 0.037603 | 0.037603 | 0.99187 | -0.057046 | 0.99288 | -0.049976 | 13.9269
65 | 0.0012398 | 0.00031015 | -0.0012398 | -0.00031044 | 5.7395e-08 | -2.9351e-07 | 0.0018992 | 0.0018993 | 0.0018993 | 0.9713 | -0.20642 | 0.97126 | -0.20676 | 0.70345
66 | -0.0027471 | -0.00068791 | 0.0027473 | 0.00068775 | 2.1937e-07 | -1.6135e-07 | 0.0042083 | 0.0042082 | 0.0042083 | 0.9713 | -0.20642 | 0.97138 | -0.20585 | 1.5586
67 | 0.0010301 | 0.0002579 | -0.0010301 | -0.00025807 | 2.235e-08 | -1.6938e-07 | 0.0015781 | 0.0015782 | 0.0015782 | 0.97126 | -0.20676 | 0.97124 | -0.20692 | 0.58451
68 | -0.0098507 | -0.0024358 | 0.0098516 | 0.0024355 | 9.4677e-07 | -3.795e-07 | 0.015078 | 0.015078 | 0.015078 | 0.97138 | -0.20585 | 0.97148 | -0.20513 | 1.8615
69 | 0.0071033 | 0.0017481 | -0.0071028 | -0.0017487 | 5.5197e-07 | -6.2174e-07 | 0.01087 | 0.01087 | 0.01087 | 0.97138 | -0.20585 | 0.97131 | -0.20643 | 1.342
70 | 0.00092132 | 0.0002308 | -0.00092131 | -0.00023085 | 4.7384e-09 | -4.5344e-08 | 0.0014115 | 0.0014115 | 0.0014115 | 0.97124 | -0.20692 | 0.97123 | -0.20695 | 0.52278
71 | -0.011074 | -0.0027418 | 0.011074 | 0.0027416 | 7.1735e-07 | -1.7004e-07 | 0.01695 | 0.016949 | 0.01695 | 0.97148 | -0.20513 | 0.97155 | -0.20465 | 2.0925
72 | 0.0067005 | 0.0016479 | -0.0067001 | -0.0016484 | 4.0933e-07 | -5.3751e-07 | 0.010254 | 0.010254 | 0.010254 | 0.97131 | -0.20643 | 0.97125 | -0.20689 | 1.2659
73 | 0.00064633 | 0.00016193 | -0.00064632 | -0.00016198 | 2.6243e-09 | -5.2069e-08 | 0.00099021 | 0.00099023 | 0.00099023 | 0.97123 | -0.20695 | 0.97123 | -0.20698 | 0.36675
74 | 0.0041031 | 0.00099965 | -0.0041024 | -0.0010026 | 7.1312e-07 | -2.9562e-06 | 0.006276 | 0.0062772 | 0.0062772 | 0.97125 | -0.20689 | 0.97107 | -0.20821 | 0.77496
75 | 0.002597 | 0.00064879 | -0.0025969 | -0.00064891 | 1.4226e-07 | -1.2356e-07 | 0.003978 | 0.0039781 | 0.0039781 | 0.97125 | -0.20689 | 0.97119 | -0.20728 | 1.4734
76 | 0.0010128 | 0.00025338 | -0.0010127 | -0.00025358 | 2.6091e-08 | -2.057e-07 | 0.0015501 | 0.0015501 | 0.0015501 | 0.97213 | -0.19757 | 0.9721 | -0.19776 | 0.57412
77 | -0.0042068 | -0.0010539 | 0.0042072 | 0.0010538 | 3.9832e-07 | -3.7699e-08 | 0.0064391 | 0.006439 | 0.0064391 | 0.97213 | -0.19757 | 0.97222 | -0.19689 | 2.3848
78 | 0.00088838 | 0.00022242 | -0.00088838 | -0.00022247 | 4.9732e-09 | -5.1524e-08 | 0.0013598 | 0.0013598 | 0.0013598 | 0.9721 | -0.19776 | 0.9721 | -0.1978 | 0.50363
79 | 0.00053003 | 0.00013266 | -0.00053002 | -0.00013284 | 6.0354e-09 | -1.7985e-07 | 0.00081126 | 0.00081133 | 0.00081133 | 0.9721 | -0.1978 | 0.97208 | -0.19788 | 0.30049
80 | 0.00607 | 0.0015143 | -0.006067 | -0.0015138 | 3.0012e-06 | 4.6456e-07 | 0.0092921 | 0.0092923 | 0.0092923 | 0.97177 | -0.20015 | 0.97128 | -0.20375 | 3.4416
81 | -0.00050628 | -0.00012688 | 0.00050629 | 0.00012644 | 1.3522e-08 | -4.4165e-07 | 0.00077522 | 0.00077506 | 0.00077522 | 0.97179 | -0.20288 | 0.97181 | -0.20268 | 0.28712
82 | -0.0011957 | -0.00029923 | 0.0011957 | 0.00029912 | 1.9835e-08 | -1.0989e-07 | 0.0018307 | 0.0018306 | 0.0018307 | 0.97181 | -0.20268 | 0.97183 | -0.20256 | 0.67803
83 | 0.00058451 | 0.00014593 | -0.00058449 | -0.00014649 | 2.2977e-08 | -5.6087e-07 | 0.00089477 | 0.00089497 | 0.00089497 | 0.97183 | -0.20256 | 0.97179 | -0.20285 | 0.33147
84 | 0.00076322 | 0.00019115 | -0.00076321 | -0.00019128 | 8.721e-09 | -1.3279e-07 | 0.001148 | 0.001148 | 0.001148 | 0.98924 | -0.07617 | 0.98923 | -0.076253 | 0.4252
85 | -0.031777 | -0.0079112 | 0.031791 | 0.0079157 | 1.4616e-05 | 4.4354e-06 | 0.04778 | 0.047779 | 0.04778 | 0.98924 | -0.07617 | 0.98971 | -0.072805 | 5.8987
86 | -0.0343 | -0.0085445 | 0.034469 | 0.0085977 | 0.00016913 | 5.3193e-05 | 0.051552 | 0.051548 | 0.051552 | 0.98971 | -0.072805 | 0.99475 | -0.036894 | 6.3644
87 | -0.0034104 | -0.00083712 | 0.0034111 | 0.00083296 | 6.7691e-07 | -4.168e-06 | 0.0052217 | 0.0052201 | 0.0052217 | 0.97068 | -0.21116 | 0.97088 | -0.20966 | 0.64465
88 | -0.003938 | -0.00096501 | 0.0039387 | 0.00096166 | 7.3981e-07 | -3.3487e-06 | 0.0060277 | 0.0060264 | 0.0060277 | 0.97088 | -0.20966 | 0.97107 | -0.20824 | 0.74416
89 | -0.00070523 | -0.00017675 | 0.00070523 | 0.00017673 | 8.3302e-10 | -1.3812e-08 | 0.0010808 | 0.0010808 | 0.0010808 | 0.97092 | -0.20927 | 0.97092 | -0.20926 | 0.40031
90 | -0.0010069 | -0.00025233 | 0.001007 | 0.00025137 | 1.2042e-07 | -9.5639e-07 | 0.0015431 | 0.0015427 | 0.0015431 | 0.97092 | -0.20926 | 0.97104 | -0.2084 | 0.57151
91 | -0.0014021 | -0.00035039 | 0.0014021 | 0.0003501 | 7.4647e-08 | -2.9201e-07 | 0.0021482 | 0.002148 | 0.0021482 | 0.97104 | -0.2084 | 0.97109 | -0.20801 | 0.79561
92 | -0.0017319 | -0.00043274 | 0.0017321 | 0.00043232 | 1.7251e-07 | -4.1956e-07 | 0.0026533 | 0.0026531 | 0.0026533 | 0.97109 | -0.20801 | 0.97119 | -0.20728 | 0.98271
93 | -0.0019969 | -0.00049746 | 0.0019971 | 0.00049711 | 2.0263e-07 | -3.5042e-07 | 0.0030608 | 0.0030606 | 0.0030608 | 0.97047 | -0.20961 | 0.97058 | -0.20887 | 1.1336
94 | 0.0018446 | 0.00045978 | -0.0018437 | -0.00046166 | 8.9948e-07 | -1.8813e-06 | 0.002827 | 0.0028278 | 0.0028278 | 0.97058 | -0.20887 | 0.97009 | -0.21242 | 1.0473
95 | -0.0038417 | -0.00095688 | 0.0038429 | 0.00095666 | 1.1677e-06 | -2.1829e-07 | 0.0058877 | 0.0058874 | 0.0058877 | 0.97058 | -0.20887 | 0.97088 | -0.20665 | 2.1806
96 | 0.0013931 | 0.00034873 | -0.001393 | -0.00034899 | 6.6158e-08 | -2.6124e-07 | 0.0021367 | 0.0021368 | 0.0021368 | 0.97009 | -0.21242 | 0.97004 | -0.21276 | 0.7914
97 | -0.005723 | -0.0014279 | 0.0057253 | 0.0014282 | 2.2738e-06 | 2.8827e-07 | 0.008769 | 0.0087688 | 0.008769 | 0.97088 | -0.20665 | 0.97128 | -0.20375 | 3.2478
98 | 0.0010321 | 0.00025853 | -0.0010321 | -0.00025859 | 7.234e-09 | -5.4318e-08 | 0.0015831 | 0.0015832 | 0.0015832 | 0.97004 | -0.21276 | 0.97003 | -0.21281 | 0.58635
99 | -0.060694 | -0.015192 | 0.060705 | 0.015196 | 1.1488e-05 | 4.1574e-06 | 0.090784 | 0.090784 | 0.090784 | 0.99475 | -0.036894 | 0.99494 | -0.035523 | 11.2079
100 | 0.025844 | 0.0064987 | -0.025797 | -0.0064813 | 4.7035e-05 | 1.7437e-05 | 0.038667 | 0.038667 | 0.038667 | 0.99475 | -0.036894 | 0.99288 | -0.049976 | 14.3211
101 | -0.00086479 | -0.00021674 | 0.0008648 | 0.00021659 | 1.3492e-08 | -1.4721e-07 | 0.001325 | 0.001325 | 0.001325 | 0.97117 | -0.2074 | 0.97119 | -0.20728 | 0.49074
102 | 0.0039387 | 0.00096159 | -0.0039387 | -0.00096166 | 1.6144e-08 | -7.311e-08 | 0.0060263 | 0.0060264 | 0.0060264 | 0.97107 | -0.20821 | 0.97107 | -0.20824 | 0.744
103 | -0.060705 | -0.015196 | 0.061005 | 0.015304 | 0.00029921 | 0.00010824 | 0.090784 | 0.090781 | 0.090784 | 0.99494 | -0.035523 | 1 | 0 | 11.2078
104 | 0.0040628 | 0.0010088 | -0.0040608 | -0.0010091 | 1.9423e-06 | -3.2805e-07 | 0.0061015 | 0.0061019 | 0.0061019 | 0.99028 | -0.068554 | 0.98979 | -0.07207 | 2.26
105 | -0.0018462 | -0.0004616 | 0.0018462 | 0.00046143 | 7.5206e-08 | -1.7122e-07 | 0.0027786 | 0.0027785 | 0.0027786 | 0.98854 | -0.081064 | 0.98858 | -0.080768 | 1.0291
106 | 0.0017033 | 0.00042578 | -0.0017032 | -0.00042603 | 9.0232e-08 | -2.4737e-07 | 0.0025635 | 0.0025636 | 0.0025636 | 0.98854 | -0.081064 | 0.98848 | -0.081448 | 0.94948
107 | -0.0019247 | -0.00048108 | 0.0019247 | 0.00048099 | 4.4376e-08 | -9.1613e-08 | 0.0028966 | 0.0028965 | 0.0028966 | 0.98858 | -0.080768 | 0.9886 | -0.080601 | 1.0728
108 | 0.0014402 | 0.0003602 | -0.0014402 | -0.00036052 | 7.9231e-08 | -3.1585e-07 | 0.0021678 | 0.0021679 | 0.0021679 | 0.98848 | -0.081448 | 0.98843 | -0.081847 | 0.80293
109 | 0.00026294 | 6.5825e-05 | -0.00026294 | -6.59e-05 | 5.7234e-10 | -7.4831e-08 | 0.0003958 | 0.00039582 | 0.00039582 | 0.98848 | -0.081448 | 0.98848 | -0.081464 | 0.1466
110 | -0.0019247 | -0.00048099 | 0.0019247 | 0.00048094 | 2.2166e-08 | -4.5763e-08 | 0.0028965 | 0.0028965 | 0.0028965 | 0.9886 | -0.080601 | 0.98862 | -0.080517 | 1.0728
111 | 0.0014402 | 0.00036052 | -0.0014401 | -0.00036084 | 8.0751e-08 | -3.2183e-07 | 0.0021679 | 0.002168 | 0.002168 | 0.98843 | -0.081847 | 0.98837 | -0.082252 | 0.80298
112 | -0.0032479 | -0.00080809 | 0.0032517 | 0.00080631 | 3.734e-06 | -1.7817e-06 | 0.0048866 | 0.0048854 | 0.0048866 | 0.98862 | -0.080517 | 0.98979 | -0.07207 | 1.8098
113 | 0.0011017 | 0.00027164 | -0.0011014 | -0.00027392 | 3.219e-07 | -2.2843e-06 | 0.0016567 | 0.0016575 | 0.0016575 | 0.98862 | -0.080517 | 0.98832 | -0.082678 | 0.61389
114 | 0.0012865 | 0.00032235 | -0.0012865 | -0.00032242 | 1.4003e-08 | -7.1278e-08 | 0.0019368 | 0.0019368 | 0.0019368 | 0.98837 | -0.082252 | 0.98836 | -0.082331 | 0.71735
115 | 0.00048862 | 0.00012238 | -0.00048862 | -0.00012241 | 6.4235e-10 | -2.2374e-08 | 0.00074951 | 0.00074951 | 0.00074951 | 0.97003 | -0.21281 | 0.97003 | -0.21282 | 0.2776
116 | 0.00025718 | 6.4404e-05 | -0.00025718 | -6.4455e-05 | 4.0923e-10 | -5.186e-08 | 0.00039449 | 0.00039451 | 0.00039451 | 0.97003 | -0.21282 | 0.97003 | -0.21283 | 0.14612
117 | 0.0011014 | 0.00027392 | -0.0011011 | -0.00027596 | 2.8825e-07 | -2.0422e-06 | 0.0016575 | 0.0016583 | 0.0016583 | 0.98832 | -0.082678 | 0.98805 | -0.084583 | 0.61418

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.062197 | 0.015403

## res_load
| p_mw | q_mvar
0 | 0.00056028 | 0.00014042
1 | 0.00059342 | 0.00014872
2 | 0.0027465 | 0.00068835
3 | 0.00014817 | 3.7135e-05
4 | 0.00016231 | 4.068e-05
5 | 0.00033999 | 8.5209e-05
6 | 0.0010313 | 0.00025847
7 | 0.0016615 | 0.00041641
8 | 0.00037747 | 9.4602e-05
9 | 0.00033827 | 8.4778e-05
10 | 0.0010885 | 0.00027281
11 | 0.00012832 | 3.216e-05
12 | 0.00015581 | 3.905e-05
13 | 0.0019974 | 0.00050059
14 | 0.00045946 | 0.00011515
15 | 0.00051496 | 0.00012906
16 | 0.00063095 | 0.00015813
17 | 0.00011929 | 2.9898e-05
18 | 0.00079831 | 0.00020008
19 | 0.00066983 | 0.00016788
20 | 0.0020655 | 0.00051766
21 | 0.00011657 | 2.9214e-05
22 | 0.00068355 | 0.00017131
23 | 0.00031067 | 7.7861e-05
24 | 0.00040588 | 0.00010172
25 | 0.0019463 | 0.00048779
26 | 0.00063392 | 0.00015888
27 | 0.0013585 | 0.00034047
28 | 0.00081825 | 0.00020507
29 | 0.00038199 | 9.5737e-05
30 | 0.00058868 | 0.00014754
31 | 0.00014692 | 3.6823e-05
32 | 0.00030249 | 7.5812e-05
33 | 0.00021298 | 5.3377e-05
34 | 0.00024081 | 6.0352e-05
35 | 0.00067696 | 0.00016966
36 | 0.0020444 | 0.00051239
37 | 0.00032515 | 8.1491e-05
38 | 0.0004004 | 0.00010035
39 | 0.0023019 | 0.00057691
40 | 0.00056322 | 0.00014116
41 | 0.00029792 | 7.4665e-05
42 | 0.0015073 | 0.00037776
43 | 0.00020965 | 5.2542e-05
44 | 0.00010879 | 2.7266e-05
45 | 0.0012221 | 0.0003063
46 | 0.00040227 | 0.00010082
47 | 0.00027499 | 6.8918e-05
48 | 0.0002604 | 6.5263e-05
49 | 0.003194 | 0.0008005
50 | 0.00012436 | 3.1167e-05
51 | 0.00035835 | 8.9811e-05
52 | 0.00053002 | 0.00013284
53 | 0.00081927 | 0.00020533
54 | 0.00050628 | 0.00012688
55 | 0.00068942 | 0.00017279
56 | 0.00058449 | 0.00014649
57 | 0.00076321 | 0.00019128
58 | 0.0025091 | 0.00062884
59 | 0.00054387 | 0.00013631
60 | 0.00052689 | 0.00013205
61 | 0.00070523 | 0.00017675
62 | 0.00030162 | 7.5593e-05
63 | 0.00039509 | 9.9018e-05
64 | 0.00032975 | 8.2642e-05
65 | 0.00056331 | 0.00014118
66 | 0.0004506 | 0.00011293
67 | 0.0018802 | 0.00047121
68 | 0.00034171 | 8.5642e-05
69 | 0.00036092 | 9.0456e-05
70 | 0.00038056 | 9.5376e-05
71 | 0.00086479 | 0.00021674
72 | 0.00016368 | 4.1023e-05
73 | 0.00071027 | 0.00017801
74 | 0.0003921 | 9.8269e-05
75 | 0.00014291 | 3.5816e-05
76 | 7.842e-05 | 1.9654e-05
77 | 0.00026294 | 6.59e-05
78 | 0.00022149 | 5.5512e-05
79 | 0.00015358 | 3.849e-05
80 | 0.00054345 | 0.0001362
81 | 0.00023144 | 5.8004e-05
82 | 0.00080915 | 0.00020279
83 | 0.0012865 | 0.00032242
84 | 0.00025718 | 6.4455e-05
85 | 0.00064632 | 0.00016198
86 | 0.0011011 | 0.00027596

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1