## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2306-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2306-3_0_4_node_194 | 0.4 | n |  | TRUE
2 | bus_LV_2306-3_0_4_node_10 | 0.4 | n |  | TRUE
3 | bus_LV_2306-3_0_4_node_11 | 0.4 | n |  | TRUE
4 | bus_LV_2306-3_0_4_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_2306-3_0_4_node_313 | 0.4 | n |  | TRUE
6 | bus_LV_2306-3_0_4_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_2306-3_0_4_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_2306-3_0_4_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_2306-3_0_4_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_2306-3_0_4_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_2306-3_0_4_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_2306-3_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_2306-3_0_4_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_2306-3_0_4_node_135 | 0.4 | n |  | TRUE
15 | bus_LV_2306-3_0_4_node_186 | 0.4 | n |  | TRUE
16 | bus_LV_2306-3_0_4_node_43 | 0.4 | n |  | TRUE
17 | bus_LV_2306-3_0_4_node_44 | 0.4 | n |  | TRUE
18 | bus_LV_2306-3_0_4_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_2306-3_0_4_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_2306-3_0_4_node_47 | 0.4 | n |  | TRUE
21 | bus_LV_2306-3_0_4_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_2306-3_0_4_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_2306-3_0_4_node_50 | 0.4 | n |  | TRUE
24 | bus_LV_2306-3_0_4_node_52 | 0.4 | n |  | TRUE
25 | bus_LV_2306-3_0_4_node_107 | 0.4 | n |  | TRUE
26 | bus_LV_2306-3_0_4_node_108 | 0.4 | n |  | TRUE
27 | bus_LV_2306-3_0_4_node_51 | 0.4 | n |  | TRUE
28 | bus_LV_2306-3_0_4_node_53 | 0.4 | n |  | TRUE
29 | bus_LV_2306-3_0_4_node_312 | 0.4 | n |  | TRUE
30 | bus_LV_2306-3_0_4_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_2306-3_0_4_node_88 | 0.4 | n |  | TRUE
32 | bus_LV_2306-3_0_4_node_83 | 0.4 | n |  | TRUE
33 | bus_LV_2306-3_0_4_node_84 | 0.4 | n |  | TRUE
34 | bus_LV_2306-3_0_4_node_85 | 0.4 | n |  | TRUE
35 | bus_LV_2306-3_0_4_node_86 | 0.4 | n |  | TRUE
36 | bus_LV_2306-3_0_4_node_87 | 0.4 | n |  | TRUE
37 | bus_LV_2306-3_0_4_node_89 | 0.4 | n |  | TRUE
38 | bus_LV_2306-3_0_4_node_90 | 0.4 | n |  | TRUE
39 | bus_LV_2306-3_0_4_node_103 | 0.4 | n |  | TRUE
40 | bus_LV_2306-3_0_4_node_100 | 0.4 | n |  | TRUE
41 | bus_LV_2306-3_0_4_node_101 | 0.4 | n |  | TRUE
42 | bus_LV_2306-3_0_4_node_287 | 0.4 | n |  | TRUE
43 | bus_LV_2306-3_0_4_node_102 | 0.4 | n |  | TRUE
44 | bus_LV_2306-3_0_4_node_104 | 0.4 | n |  | TRUE
45 | bus_LV_2306-3_0_4_node_185 | 0.4 | n |  | TRUE
46 | bus_LV_2306-3_0_4_node_105 | 0.4 | n |  | TRUE
47 | bus_LV_2306-3_0_4_node_121 | 0.4 | n |  | TRUE
48 | bus_LV_2306-3_0_4_node_177 | 0.4 | n |  | TRUE
49 | bus_LV_2306-3_0_4_node_113 | 0.4 | n |  | TRUE
50 | bus_LV_2306-3_0_4_node_118 | 0.4 | n |  | TRUE
51 | bus_LV_2306-3_0_4_node_119 | 0.4 | n |  | TRUE
52 | bus_LV_2306-3_0_4_node_120 | 0.4 | n |  | TRUE
53 | bus_LV_2306-3_0_4_node_122 | 0.4 | n |  | TRUE
54 | bus_LV_2306-3_0_4_node_123 | 0.4 | n |  | TRUE
55 | bus_LV_2306-3_0_4_node_124 | 0.4 | n |  | TRUE
56 | bus_LV_2306-3_0_4_node_136 | 0.4 | n |  | TRUE
57 | bus_LV_2306-3_0_4_node_192 | 0.4 | n |  | TRUE
58 | bus_LV_2306-3_0_4_node_125 | 0.4 | n |  | TRUE
59 | bus_LV_2306-3_0_4_node_126 | 0.4 | n |  | TRUE
60 | bus_LV_2306-3_0_4_node_127 | 0.4 | n |  | TRUE
61 | bus_LV_2306-3_0_4_node_128 | 0.4 | n |  | TRUE
62 | bus_LV_2306-3_0_4_node_129 | 0.4 | n |  | TRUE
63 | bus_LV_2306-3_0_4_node_130 | 0.4 | n |  | TRUE
64 | bus_LV_2306-3_0_4_node_131 | 0.4 | n |  | TRUE
65 | bus_LV_2306-3_0_4_node_132 | 0.4 | n |  | TRUE
66 | bus_LV_2306-3_0_4_node_133 | 0.4 | n |  | TRUE
67 | bus_LV_2306-3_0_4_node_134 | 0.4 | n |  | TRUE
68 | bus_LV_2306-3_0_4_node_167 | 0.4 | n |  | TRUE
69 | bus_LV_2306-3_0_4_node_190 | 0.4 | n |  | TRUE
70 | bus_LV_2306-3_0_4_node_142 | 0.4 | n |  | TRUE
71 | bus_LV_2306-3_0_4_node_143 | 0.4 | n |  | TRUE
72 | bus_LV_2306-3_0_4_node_168 | 0.4 | n |  | TRUE
73 | bus_LV_2306-3_0_4_node_147 | 0.4 | n |  | TRUE
74 | bus_LV_2306-3_0_4_node_144 | 0.4 | n |  | TRUE
75 | bus_LV_2306-3_0_4_node_145 | 0.4 | n |  | TRUE
76 | bus_LV_2306-3_0_4_node_146 | 0.4 | n |  | TRUE
77 | bus_LV_2306-3_0_4_node_148 | 0.4 | n |  | TRUE
78 | bus_LV_2306-3_0_4_node_149 | 0.4 | n |  | TRUE
79 | bus_LV_2306-3_0_4_node_150 | 0.4 | n |  | TRUE
80 | bus_LV_2306-3_0_4_node_152 | 0.4 | n |  | TRUE
81 | bus_LV_2306-3_0_4_node_153 | 0.4 | n |  | TRUE
82 | bus_LV_2306-3_0_4_node_180 | 0.4 | n |  | TRUE
83 | bus_LV_2306-3_0_4_node_151 | 0.4 | n |  | TRUE
84 | bus_LV_2306-3_0_4_node_188 | 0.4 | n |  | TRUE
85 | bus_LV_2306-3_0_4_node_178 | 0.4 | n |  | TRUE
86 | bus_LV_2306-3_0_4_node_154 | 0.4 | n |  | TRUE
87 | bus_LV_2306-3_0_4_node_155 | 0.4 | n |  | TRUE
88 | bus_LV_2306-3_0_4_node_156 | 0.4 | n |  | TRUE
89 | bus_LV_2306-3_0_4_node_157 | 0.4 | n |  | TRUE
90 | bus_LV_2306-3_0_4_node_158 | 0.4 | n |  | TRUE
91 | bus_LV_2306-3_0_4_node_159 | 0.4 | n |  | TRUE
92 | bus_LV_2306-3_0_4_node_160 | 0.4 | n |  | TRUE
93 | bus_LV_2306-3_0_4_node_161 | 0.4 | n |  | TRUE
94 | bus_LV_2306-3_0_4_node_162 | 0.4 | n |  | TRUE
95 | bus_LV_2306-3_0_4_node_182 | 0.4 | n |  | TRUE
96 | bus_LV_2306-3_0_4_node_163 | 0.4 | n |  | TRUE
97 | bus_LV_2306-3_0_4_node_164 | 0.4 | n |  | TRUE
98 | bus_LV_2306-3_0_4_node_165 | 0.4 | n |  | TRUE
99 | bus_LV_2306-3_0_4_node_166 | 0.4 | n |  | TRUE
100 | bus_LV_2306-3_0_4_node_172 | 0.4 | n |  | TRUE
101 | bus_LV_2306-3_0_4_node_169 | 0.4 | n |  | TRUE
102 | bus_LV_2306-3_0_4_node_170 | 0.4 | n |  | TRUE
103 | bus_LV_2306-3_0_4_node_171 | 0.4 | n |  | TRUE
104 | bus_LV_2306-3_0_4_node_173 | 0.4 | n |  | TRUE
105 | bus_LV_2306-3_0_4_node_174 | 0.4 | n |  | TRUE
106 | bus_LV_2306-3_0_4_node_183 | 0.4 | n |  | TRUE
107 | bus_LV_2306-3_0_4_node_175 | 0.4 | n |  | TRUE
108 | bus_LV_2306-3_0_4_node_176 | 0.4 | n |  | TRUE
109 | bus_LV_2306-3_0_4_node_179 | 0.4 | n |  | TRUE
110 | bus_LV_2306-3_0_4_node_184 | 0.4 | n |  | TRUE
111 | bus_LV_2306-3_0_4_node_193 | 0.4 | n |  | TRUE
112 | bus_LV_2306-3_0_4_node_187 | 0.4 | n |  | TRUE
113 | bus_LV_2306-3_0_4_node_189 | 0.4 | n |  | TRUE
114 | bus_LV_2306-3_0_4_node_191 | 0.4 | n |  | TRUE
115 | bus_LV_2306-3_0_4_node_286 | 0.4 | n |  | TRUE
116 | bus_LV_2306-3_0_4_node_288 | 0.4 | n |  | TRUE
117 | bus_LV_2306-3_0_4_node_289 | 0.4 | n |  | TRUE
118 | bus_LV_2306-3_0_4_node_303 | 0.4 | n |  | TRUE
119 | bus_LV_2306-3_0_4_node_300 | 0.4 | n |  | TRUE
120 | bus_LV_2306-3_0_4_node_301 | 0.4 | n |  | TRUE
121 | bus_LV_2306-3_0_4_node_302 | 0.4 | n |  | TRUE
122 | bus_LV_2306-3_0_4_node_304 | 0.4 | n |  | TRUE
123 | bus_LV_2306-3_0_4_node_305 | 0.4 | n |  | TRUE
124 | bus_MV_119_1_node_226 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2306-3_0_4_load_0 | 0 | 0.00044722 | 0.00011208 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2306-3_0_4_load_10 | 2 | 0.0009687 | 0.00024278 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2306-3_0_4_load_11 | 3 | 0.00020286 | 5.0841e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2306-3_0_4_load_313 | 5 | 0.00021352 | 5.3513e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2306-3_0_4_load_18 | 6 | 0.00078056 | 0.00019563 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2306-3_0_4_load_22 | 9 | 0.00069639 | 0.00017453 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2306-3_0_4_load_24 | 12 | 0.00053286 | 0.00013355 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2306-3_0_4_load_25 | 13 | 0.00055029 | 0.00013792 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2306-3_0_4_load_135 | 14 | 0.0005325 | 0.00013346 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2306-3_0_4_load_43 | 16 | 0.00074266 | 0.00018613 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2306-3_0_4_load_44 | 17 | 9.076e-05 | 2.2747e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2306-3_0_4_load_46 | 19 | 0.00051236 | 0.00012841 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2306-3_0_4_load_48 | 21 | 0.0001215 | 3.0451e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2306-3_0_4_load_50 | 23 | 0.00055726 | 0.00013966 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2306-3_0_4_load_52 | 24 | 6.9444e-05 | 1.7404e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2306-3_0_4_load_53 | 28 | 0.00033197 | 8.3198e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2306-3_0_4_load_312 | 29 | 0.00023332 | 5.8476e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2306-3_0_4_load_88 | 31 | 0.00033893 | 8.4944e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2306-3_0_4_load_83 | 32 | 0.0016567 | 0.00041521 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2306-3_0_4_load_86 | 35 | 0.00025895 | 6.49e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2306-3_0_4_load_87 | 36 | 0.00012908 | 3.2352e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2306-3_0_4_load_89 | 37 | 0.0012199 | 0.00030574 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2306-3_0_4_load_103 | 39 | 0.0016161 | 0.00040504 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2306-3_0_4_load_101 | 41 | 0.00032292 | 8.0931e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2306-3_0_4_load_185 | 45 | 0.00038469 | 9.6414e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2306-3_0_4_load_177 | 48 | 0.00077624 | 0.00019455 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2306-3_0_4_load_113 | 49 | 0.0004009 | 0.00010047 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2306-3_0_4_load_118 | 50 | 0.0019709 | 0.00049396 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2306-3_0_4_load_119 | 51 | 0.0010987 | 0.00027537 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2306-3_0_4_load_122 | 53 | 0.00039029 | 9.7816e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2306-3_0_4_load_123 | 54 | 0.00027829 | 6.9747e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2306-3_0_4_load_124 | 55 | 0.00069326 | 0.00017375 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2306-3_0_4_load_136 | 56 | 0.00032369 | 8.1124e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2306-3_0_4_load_192 | 57 | 0.00052961 | 0.00013273 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2306-3_0_4_load_125 | 58 | 0.0020808 | 0.00052149 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2306-3_0_4_load_126 | 59 | 0.00079404 | 0.00019901 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2306-3_0_4_load_128 | 61 | 0.00049489 | 0.00012403 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2306-3_0_4_load_129 | 62 | 0.00032917 | 8.2499e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2306-3_0_4_load_130 | 63 | 0.00027092 | 6.7898e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2306-3_0_4_load_131 | 64 | 0.00033633 | 8.4291e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2306-3_0_4_load_132 | 65 | 0.00083549 | 0.00020939 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2306-3_0_4_load_133 | 66 | 0.00063981 | 0.00016035 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2306-3_0_4_load_134 | 67 | 0.00041949 | 0.00010513 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2306-3_0_4_load_167 | 68 | 0.001731 | 0.00043383 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2306-3_0_4_load_190 | 69 | 0.0025979 | 0.0006511 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2306-3_0_4_load_142 | 70 | 0.002998 | 0.00075136 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2306-3_0_4_load_168 | 72 | 0.0028319 | 0.00070974 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2306-3_0_4_load_148 | 77 | 0.0003089 | 7.7418e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2306-3_0_4_load_149 | 78 | 0.00039793 | 9.9731e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2306-3_0_4_load_150 | 79 | 0.00068262 | 0.00017108 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2306-3_0_4_load_152 | 80 | 0.00071199 | 0.00017844 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2306-3_0_4_load_153 | 81 | 0.0036997 | 0.00092723 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2306-3_0_4_load_151 | 83 | 0.0014516 | 0.00036381 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2306-3_0_4_load_188 | 84 | 0.0044338 | 0.0011112 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2306-3_0_4_load_178 | 85 | 0.0012724 | 0.0003189 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2306-3_0_4_load_154 | 86 | 0.0013287 | 0.00033301 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2306-3_0_4_load_155 | 87 | 0.00021556 | 5.4024e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2306-3_0_4_load_156 | 88 | 0.00084768 | 0.00021245 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2306-3_0_4_load_159 | 91 | 0.00029824 | 7.4745e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2306-3_0_4_load_160 | 92 | 0.00041374 | 0.00010369 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2306-3_0_4_load_161 | 93 | 0.00018536 | 4.6455e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2306-3_0_4_load_162 | 94 | 0.0013701 | 0.00034338 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2306-3_0_4_load_182 | 95 | 0.00083627 | 0.00020959 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2306-3_0_4_load_163 | 96 | 0.00029182 | 7.3137e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2306-3_0_4_load_165 | 98 | 0.00056097 | 0.00014059 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2306-3_0_4_load_166 | 99 | 0.00032366 | 8.1116e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2306-3_0_4_load_172 | 100 | 0.00047268 | 0.00011846 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2306-3_0_4_load_169 | 101 | 0.00097127 | 0.00024342 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2306-3_0_4_load_170 | 102 | 0.00017979 | 4.5059e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2306-3_0_4_load_171 | 103 | 0.00030901 | 7.7446e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2306-3_0_4_load_173 | 104 | 0.001382 | 0.00034637 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2306-3_0_4_load_175 | 107 | 0.0023366 | 0.00058562 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2306-3_0_4_load_179 | 109 | 0.002042 | 0.00051176 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2306-3_0_4_load_184 | 110 | 0.0025546 | 0.00064024 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2306-3_0_4_load_193 | 111 | 0.0012771 | 0.00032006 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2306-3_0_4_load_187 | 112 | 0.0023388 | 0.00058616 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2306-3_0_4_load_189 | 113 | 0.0020269 | 0.000508 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2306-3_0_4_load_191 | 114 | 0.00069326 | 0.00017375 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2306-3_0_4_load_286 | 115 | 0.00093238 | 0.00023368 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2306-3_0_4_load_288 | 116 | 0.00014493 | 3.6324e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2306-3_0_4_load_300 | 119 | 0.00030058 | 7.5332e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2306-3_0_4_load_301 | 120 | 0.00015009 | 3.7617e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2306-3_0_4_load_304 | 122 | 0.0032298 | 0.00080946 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2306-3_0_4_load_305 | 123 | 0.0010555 | 0.00026452 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2306-3_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.27958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2306-3_0_4_line_1 | NAYY 4x150 SE | 1 | 111 | 0.11154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2306-3_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.014719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2306-3_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.070114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2306-3_0_4_line_4 | NAYY 4x150 SE | 4 | 5 | 0.20519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2306-3_0_4_line_5 | NAYY 4x150 SE | 5 | 26 | 0.07856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2306-3_0_4_line_6 | NAYY 4x150 SE | 6 | 7 | 0.021656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2306-3_0_4_line_7 | NAYY 4x150 SE | 7 | 8 | 0.10825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2306-3_0_4_line_8 | NAYY 4x150 SE | 8 | 9 | 0.046381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2306-3_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.081129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2306-3_0_4_line_10 | NAYY 4x150 SE | 10 | 11 | 0.14329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2306-3_0_4_line_11 | NAYY 4x150 SE | 11 | 12 | 0.050642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2306-3_0_4_line_12 | NAYY 4x150 SE | 11 | 13 | 0.026867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2306-3_0_4_line_13 | NAYY 4x150 SE | 12 | 14 | 0.0099736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2306-3_0_4_line_14 | NAYY 4x150 SE | 13 | 15 | 0.036585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2306-3_0_4_line_15 | NAYY 4x150 SE | 14 | 64 | 0.020057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2306-3_0_4_line_16 | NAYY 4x150 SE | 15 | 112 | 0.012712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2306-3_0_4_line_17 | NAYY 4x150 SE | 15 | 44 | 0.00989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2306-3_0_4_line_18 | NAYY 4x150 SE | 16 | 17 | 0.02681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2306-3_0_4_line_19 | NAYY 4x150 SE | 16 | 18 | 0.023113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2306-3_0_4_line_20 | NAYY 4x150 SE | 17 | 19 | 0.0050056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2306-3_0_4_line_21 | NAYY 4x150 SE | 18 | 20 | 0.006611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2306-3_0_4_line_22 | NAYY 4x150 SE | 18 | 21 | 0.020393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2306-3_0_4_line_23 | NAYY 4x150 SE | 19 | 22 | 0.089039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2306-3_0_4_line_24 | NAYY 4x150 SE | 20 | 23 | 0.045772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2306-3_0_4_line_25 | NAYY 4x150 SE | 21 | 24 | 0.00088928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2306-3_0_4_line_26 | NAYY 4x150 SE | 22 | 25 | 0.080354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2306-3_0_4_line_27 | NAYY 4x150 SE | 22 | 26 | 0.11312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2306-3_0_4_line_28 | NAYY 4x150 SE | 23 | 27 | 0.054508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2306-3_0_4_line_29 | NAYY 4x150 SE | 24 | 29 | 0.00097629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2306-3_0_4_line_30 | NAYY 4x150 SE | 25 | 49 | 0.13232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2306-3_0_4_line_31 | NAYY 4x150 SE | 27 | 28 | 0.088777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2306-3_0_4_line_32 | NAYY 4x150 SE | 28 | 30 | 0.16907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2306-3_0_4_line_33 | NAYY 4x150 SE | 30 | 31 | 0.038343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2306-3_0_4_line_34 | NAYY 4x150 SE | 31 | 34 | 0.01288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2306-3_0_4_line_35 | NAYY 4x150 SE | 32 | 33 | 0.062565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2306-3_0_4_line_36 | NAYY 4x150 SE | 32 | 34 | 0.044935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2306-3_0_4_line_37 | NAYY 4x150 SE | 33 | 35 | 0.020405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2306-3_0_4_line_38 | NAYY 4x150 SE | 33 | 36 | 0.074108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2306-3_0_4_line_39 | NAYY 4x150 SE | 34 | 37 | 0.033201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2306-3_0_4_line_40 | NAYY 4x150 SE | 35 | 38 | 0.2226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2306-3_0_4_line_41 | NAYY 4x150 SE | 36 | 39 | 0.27731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2306-3_0_4_line_42 | NAYY 4x150 SE | 38 | 40 | 0.013494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2306-3_0_4_line_43 | NAYY 4x150 SE | 39 | 43 | 0.23437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2306-3_0_4_line_44 | NAYY 4x150 SE | 40 | 41 | 0.058942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2306-3_0_4_line_45 | NAYY 4x150 SE | 41 | 42 | 0.16944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2306-3_0_4_line_46 | NAYY 4x150 SE | 42 | 116 | 0.0020205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2306-3_0_4_line_47 | NAYY 4x150 SE | 42 | 115 | 0.029258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2306-3_0_4_line_48 | NAYY 4x150 SE | 43 | 44 | 0.1368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2306-3_0_4_line_49 | NAYY 4x150 SE | 44 | 45 | 0.003682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2306-3_0_4_line_50 | NAYY 4x150 SE | 46 | 47 | 0.080934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2306-3_0_4_line_51 | NAYY 4x150 SE | 46 | 48 | 0.032968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2306-3_0_4_line_52 | NAYY 4x150 SE | 47 | 54 | 0.015951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_2306-3_0_4_line_53 | NAYY 4x150 SE | 47 | 51 | 0.024483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2306-3_0_4_line_54 | NAYY 4x150 SE | 48 | 108 | 0.15032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2306-3_0_4_line_55 | NAYY 4x150 SE | 50 | 51 | 0.0050181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2306-3_0_4_line_56 | NAYY 4x150 SE | 50 | 52 | 0.036034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2306-3_0_4_line_57 | NAYY 4x150 SE | 52 | 53 | 0.036211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2306-3_0_4_line_58 | NAYY 4x150 SE | 53 | 55 | 0.00049089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2306-3_0_4_line_59 | NAYY 4x150 SE | 54 | 56 | 0.004151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_2306-3_0_4_line_60 | NAYY 4x150 SE | 55 | 57 | 0.008498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2306-3_0_4_line_61 | NAYY 4x150 SE | 56 | 66 | 0.010576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_2306-3_0_4_line_62 | NAYY 4x150 SE | 57 | 114 | 0.00077403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2306-3_0_4_line_63 | NAYY 4x150 SE | 58 | 59 | 0.0063102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2306-3_0_4_line_64 | NAYY 4x150 SE | 58 | 60 | 0.021241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2306-3_0_4_line_65 | NAYY 4x150 SE | 59 | 61 | 0.0055222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2306-3_0_4_line_66 | NAYY 4x150 SE | 60 | 62 | 0.012957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
67 | LV_2306-3_0_4_line_67 | NAYY 4x150 SE | 60 | 63 | 0.011542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2306-3_0_4_line_68 | NAYY 4x150 SE | 60 | 64 | 0.05505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2306-3_0_4_line_69 | NAYY 4x150 SE | 61 | 65 | 0.029571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2306-3_0_4_line_70 | NAYY 4x150 SE | 62 | 66 | 0.013928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
71 | LV_2306-3_0_4_line_71 | NAYY 4x150 SE | 63 | 67 | 0.014986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2306-3_0_4_line_72 | NAYY 4x150 SE | 65 | 68 | 0.0035124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2306-3_0_4_line_73 | NAYY 4x150 SE | 67 | 69 | 0.017807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2306-3_0_4_line_74 | NAYY 4x150 SE | 68 | 93 | 0.016684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2306-3_0_4_line_75 | NAYY 4x150 SE | 69 | 113 | 0.012852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2306-3_0_4_line_76 | NAYY 4x150 SE | 70 | 71 | 0.017113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2306-3_0_4_line_77 | NAYY 4x150 SE | 70 | 72 | 0.25959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2306-3_0_4_line_78 | NAYY 4x150 SE | 71 | 73 | 0.0148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2306-3_0_4_line_79 | NAYY 4x150 SE | 72 | 79 | 0.0063973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2306-3_0_4_line_80 | NAYY 4x150 SE | 73 | 80 | 0.019687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2306-3_0_4_line_81 | NAYY 4x150 SE | 73 | 81 | 0.043992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2306-3_0_4_line_82 | NAYY 4x150 SE | 74 | 75 | 0.099528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2306-3_0_4_line_83 | NAYY 4x150 SE | 74 | 76 | 0.011135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2306-3_0_4_line_84 | NAYY 4x150 SE | 75 | 77 | 0.033406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2306-3_0_4_line_85 | NAYY 4x150 SE | 75 | 78 | 0.03563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2306-3_0_4_line_86 | NAYY 4x150 SE | 76 | 79 | 0.035684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2306-3_0_4_line_87 | NAYY 4x150 SE | 78 | 82 | 0.0018637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2306-3_0_4_line_88 | NAYY 4x150 SE | 81 | 85 | 0.0047513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2306-3_0_4_line_89 | NAYY 4x150 SE | 82 | 95 | 0.023057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2306-3_0_4_line_90 | NAYY 4x150 SE | 82 | 109 | 0.034729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2306-3_0_4_line_91 | NAYY 4x150 SE | 83 | 84 | 0.084087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2306-3_0_4_line_92 | NAYY 4x150 SE | 84 | 113 | 0.024611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2306-3_0_4_line_93 | NAYY 4x150 SE | 86 | 87 | 0.016328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2306-3_0_4_line_94 | NAYY 4x150 SE | 86 | 88 | 0.041138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2306-3_0_4_line_95 | NAYY 4x150 SE | 87 | 89 | 0.0019846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2306-3_0_4_line_96 | NAYY 4x150 SE | 88 | 90 | 0.024478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2306-3_0_4_line_97 | NAYY 4x150 SE | 89 | 91 | 0.012293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2306-3_0_4_line_98 | NAYY 4x150 SE | 89 | 92 | 0.018192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2306-3_0_4_line_99 | NAYY 4x150 SE | 90 | 93 | 0.0053345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2306-3_0_4_line_100 | NAYY 4x150 SE | 90 | 94 | 0.036528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2306-3_0_4_line_101 | NAYY 4x150 SE | 92 | 95 | 0.043468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2306-3_0_4_line_102 | NAYY 4x150 SE | 94 | 96 | 0.0041711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2306-3_0_4_line_103 | NAYY 4x150 SE | 96 | 97 | 0.016863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2306-3_0_4_line_104 | NAYY 4x150 SE | 97 | 98 | 0.032686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2306-3_0_4_line_105 | NAYY 4x150 SE | 97 | 99 | 0.0074591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2306-3_0_4_line_106 | NAYY 4x150 SE | 99 | 100 | 0.0030702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2306-3_0_4_line_107 | NAYY 4x150 SE | 100 | 102 | 0.013097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2306-3_0_4_line_108 | NAYY 4x150 SE | 101 | 102 | 0.01724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2306-3_0_4_line_109 | NAYY 4x150 SE | 101 | 103 | 0.020142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2306-3_0_4_line_110 | NAYY 4x150 SE | 103 | 104 | 0.043721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2306-3_0_4_line_111 | NAYY 4x150 SE | 104 | 105 | 0.022861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2306-3_0_4_line_112 | NAYY 4x150 SE | 105 | 106 | 0.059122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2306-3_0_4_line_113 | NAYY 4x150 SE | 106 | 110 | 0.06146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2306-3_0_4_line_114 | NAYY 4x150 SE | 107 | 108 | 0.015774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2306-3_0_4_line_115 | NAYY 4x150 SE | 110 | 111 | 0.027292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2306-3_0_4_line_116 | NAYY 4x150 SE | 116 | 117 | 0.03617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2306-3_0_4_line_117 | NAYY 4x150 SE | 117 | 118 | 0.027984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2306-3_0_4_line_118 | NAYY 4x150 SE | 118 | 122 | 0.01664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2306-3_0_4_line_119 | NAYY 4x150 SE | 118 | 121 | 0.019506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2306-3_0_4_line_120 | NAYY 4x150 SE | 119 | 120 | 0.0046246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2306-3_0_4_line_121 | NAYY 4x150 SE | 120 | 121 | 0.012727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2306-3_0_4_line_122 | NAYY 4x150 SE | 122 | 123 | 0.023945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2306-3_0_4_trafo_121 | 0.25 MVA 20/0.4 kV | 124 | 47 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2587678.1176 | 1184729.8876 | 2587833.0774 | 1184962.5883
1 | 2587678.1176 | 1184729.8876 | 2587675.8135 | 1184719.2424 | 2587703.5135 | 1184622.4817
2 | 2587250.9659 | 1184058.895 | 2587252.5756 | 1184057.1913 | 2587254.1881 | 1184054.5643 | 2587255.1053 | 1184051.5607 | 2587255.9683 | 1184045.4696
3 | 2587275.7064 | 1183980.0464 | 2587273.5639 | 1183981.1627 | 2587271.8877 | 1183982.5781 | 2587269.3828 | 1183985.5628 | 2587267.3155 | 1183989.7471 | 2587264.8281 | 1183997.323 | 2587257.519 | 1184034.5245 | 2587255.9683 | 1184045.4696
4 | 2587348.7365 | 1183788.2917 | 2587275.7064 | 1183980.0464
5 | 2587409.7009 | 1183754.5117 | 2587389.2033 | 1183757.112 | 2587378.3139 | 1183758.7359 | 2587376.6149 | 1183774.6588 | 2587348.7365 | 1183788.2917
6 | 2587768.5622 | 1184082.2995 | 2587767.3726 | 1184079.1114 | 2587764.0008 | 1184068.9242 | 2587761.2033 | 1184061.9409
7 | 2587768.5622 | 1184082.2995 | 2587754.7591 | 1184088.331 | 2587752.6271 | 1184090.87 | 2587751.0837 | 1184093.8414 | 2587750.4479 | 1184096.4663 | 2587750.2701 | 1184099.0569 | 2587750.9044 | 1184103.1355 | 2587752.2951 | 1184107.6016 | 2587754.1493 | 1184110.9995 | 2587785.4232 | 1184145.3864 | 2587793.5978 | 1184152.7401 | 2587802.3898 | 1184159.6812
8 | 2587802.3898 | 1184159.6812 | 2587823.7076 | 1184174.2673 | 2587839.9796 | 1184186.819
9 | 2587907.3867 | 1184230.837 | 2587902.4768 | 1184229.8465 | 2587899.0018 | 1184228.8419 | 2587896.1444 | 1184227.447 | 2587846.2599 | 1184191.6635 | 2587839.9796 | 1184186.819
10 | 2587987.229 | 1184349.9369 | 2587935.9861 | 1184272.0114 | 2587907.3867 | 1184230.837
11 | 2587987.229 | 1184349.9369 | 2588010.4767 | 1184394.9277
12 | 2587987.229 | 1184349.9369 | 2588003.5025 | 1184342.7448 | 2588009.8612 | 1184336.2699
13 | 2588015.0551 | 1184403.7883 | 2588010.4767 | 1184394.9277
14 | 2588014.0695 | 1184306.5826 | 2588018.5432 | 1184310.8869 | 2588021.9191 | 1184315.8049 | 2588020.9006 | 1184321.6878 | 2588019.122 | 1184325.3933 | 2588015.4916 | 1184330.5366 | 2588009.8612 | 1184336.2699
15 | 2588015.0551 | 1184403.7883 | 2588024.2626 | 1184421.6074
16 | 2588014.0695 | 1184306.5826 | 2588006.1287 | 1184316.526
17 | 2588008.1687 | 1184298.6348 | 2588014.0695 | 1184306.5826
18 | 2587552.7835 | 1183780.319 | 2587540.2078 | 1183772.4797 | 2587530.5825 | 1183765.3295
19 | 2587572.3709 | 1183792.5896 | 2587564.9491 | 1183787.9026 | 2587552.7835 | 1183780.319
20 | 2587530.5825 | 1183765.3295 | 2587530.5825 | 1183765.3295 | 2587526.8616 | 1183761.9812
21 | 2587577.9735 | 1183796.1241 | 2587572.3709 | 1183792.5896
22 | 2587572.3709 | 1183792.5896 | 2587569.0401 | 1183794.9533 | 2587567.4389 | 1183795.846 | 2587562.5389 | 1183796.123 | 2587553.0632 | 1183794.8032
23 | 2587495.0582 | 1183682.3834 | 2587495.8195 | 1183703.2037 | 2587497.5818 | 1183713.6165 | 2587500.0826 | 1183723.1273 | 2587504.6407 | 1183734.4791 | 2587509.9259 | 1183743.1614 | 2587515.5987 | 1183750.9757 | 2587522.0782 | 1183757.6767 | 2587526.8616 | 1183761.9812
24 | 2587577.9735 | 1183796.1241 | 2587582.3018 | 1183792.5799 | 2587587.6623 | 1183789.8562 | 2587619.5991 | 1183777.7213
25 | 2587552.1824 | 1183794.6806 | 2587553.0632 | 1183794.8032
26 | 2587500.2714 | 1183602.22 | 2587498.2372 | 1183633.1958 | 2587496.2705 | 1183659.9137 | 2587495.0582 | 1183682.3834
27 | 2587409.7009 | 1183754.5117 | 2587416.9882 | 1183753.2845 | 2587427.1637 | 1183746.1927 | 2587436.1005 | 1183738.0585 | 2587443.6639 | 1183730.2052 | 2587471.4269 | 1183701.3874 | 2587495.0582 | 1183682.3834
28 | 2587671.9964 | 1183768.3699 | 2587660.4282 | 1183766.6263 | 2587653.1609 | 1183766.4302 | 2587647.117 | 1183767.2654 | 2587619.5991 | 1183777.7213
29 | 2587551.2154 | 1183794.5459 | 2587552.1824 | 1183794.6806
30 | 2587500.2714 | 1183602.22 | 2587632.8478 | 1183608.1239
31 | 2587671.9964 | 1183768.3699 | 2587672.2435 | 1183766.0793 | 2587673.7707 | 1183762.6633 | 2587676.061 | 1183759.1123 | 2587678.4387 | 1183757.2286 | 2587683.4792 | 1183754.728 | 2587716.5093 | 1183743.9431 | 2587721.0854 | 1183742.0326 | 2587724.9048 | 1183739.6457 | 2587731.7177 | 1183734.1622 | 2587734.7672 | 1183732.2883 | 2587738.9473 | 1183730.8122 | 2587747.5443 | 1183728.5953
32 | 2587911.5831 | 1183692.9174 | 2587908.7126 | 1183692.7231 | 2587906.0493 | 1183693.1398 | 2587850.0803 | 1183711.4633 | 2587825.5837 | 1183718.4503 | 2587800.2673 | 1183723.9049 | 2587796.0399 | 1183724.6251 | 2587791.9113 | 1183725.1338 | 2587787.9648 | 1183725.1308 | 2587777.8031 | 1183724.3179 | 2587771.9253 | 1183724.2855 | 2587750.2463 | 1183727.8986 | 2587747.5443 | 1183728.5953
33 | 2587911.5831 | 1183692.9174 | 2587922.5358 | 1183688.504 | 2587947.3643 | 1183679.1424
34 | 2587959.5766 | 1183675.0776 | 2587953.0386 | 1183677.0029 | 2587947.3643 | 1183679.1424
35 | 2588060.5695 | 1183699.1087 | 2588054.3893 | 1183696.7199 | 2588036.151 | 1183691.9096 | 2588021.0113 | 1183686.8263 | 2588002.1775 | 1183677.2991
36 | 2587959.5766 | 1183675.0776 | 2587974.2393 | 1183670.7568 | 2587981.2599 | 1183669.6643 | 2587988.1469 | 1183670.4619 | 2587993.6939 | 1183673.0076 | 2588002.1775 | 1183677.2991
37 | 2588060.5695 | 1183699.1087 | 2588064.9814 | 1183698.9665 | 2588080.6436 | 1183702.1933
38 | 2588060.5695 | 1183699.1087 | 2588056.5955 | 1183700.5953 | 2588018.9816 | 1183721.3371 | 2588012.1716 | 1183724.5969 | 2588006.1372 | 1183726.41 | 2588001.9174 | 1183727.0967 | 2587995.4894 | 1183726.7984 | 2587993.1815 | 1183726.3537
39 | 2587959.5766 | 1183675.0776 | 2587954.5129 | 1183669.9963 | 2587948.967 | 1183664.2156 | 2587941.3828 | 1183654.6705 | 2587938.2677 | 1183649.7479
40 | 2588285.7762 | 1183787.1733 | 2588269.4712 | 1183779.3014 | 2588213.7137 | 1183750.4411 | 2588161.7182 | 1183728.9221 | 2588125.8036 | 1183717.6545 | 2588087.4253 | 1183703.5906 | 2588080.6436 | 1183702.1933
41 | 2587978.8731 | 1184003.2969 | 2587993.1815 | 1183726.3537
42 | 2588293.0512 | 1183775.7976 | 2588285.7762 | 1183787.1733
43 | 2587978.8731 | 1184003.2969 | 2587982.6495 | 1184006.1129 | 2587982.2558 | 1184011.4832 | 2587977.8215 | 1184019.2739 | 2587973.7175 | 1184028.0868 | 2587972.6361 | 1184036.8935 | 2587979.7541 | 1184050.2416 | 2588006.6307 | 1184084.7608 | 2588042.8285 | 1184127.7546 | 2588091.3147 | 1184193.6692
44 | 2588293.0512 | 1183775.7976 | 2588351.6377 | 1183782.2617
45 | 2588491.6398 | 1183866.5682 | 2588489.138 | 1183863.6159 | 2588487.2584 | 1183858.717 | 2588485.2945 | 1183853.6738 | 2588482.9438 | 1183849.8986 | 2588479.9448 | 1183846.3915 | 2588475.3642 | 1183842.0981 | 2588455.8005 | 1183826.5391 | 2588446.0855 | 1183819.799 | 2588438.3907 | 1183815.6229 | 2588422.3392 | 1183808.4059 | 2588414.0041 | 1183804.7202 | 2588408.4714 | 1183801.5405 | 2588395.8686 | 1183793.572 | 2588389.2746 | 1183790.261 | 2588381.7353 | 1183787.6076 | 2588373.7544 | 1183785.4999 | 2588359.8725 | 1183783.1703 | 2588351.6377 | 1183782.2617
46 | 2588491.6398 | 1183866.5682 | 2588493.1933 | 1183867.8601
47 | 2588491.6398 | 1183866.5682 | 2588491.1609 | 1183871.5606 | 2588490.5208 | 1183876.0864 | 2588486.007 | 1183895.2331
48 | 2588008.1687 | 1184298.6348 | 2588013.5301 | 1184285.117 | 2588022.8043 | 1184262.6423 | 2588039.0747 | 1184238.5972 | 2588065.8211 | 1184212.6078 | 2588091.3147 | 1184193.6692
49 | 2588008.1687 | 1184298.6348 | 2588005.3964 | 1184301.0579
50 | 2588098.3615 | 1184354.7161 | 2588103.6473 | 1184394.893 | 2588104.0805 | 1184401.6178 | 2588103.2967 | 1184418.0612 | 2588099.4529 | 1184434.822
51 | 2588098.3615 | 1184354.7161 | 2588109.8726 | 1184343.8653 | 2588124.0284 | 1184334.1859
52 | 2588099.4529 | 1184434.822 | 2588085.5631 | 1184442.6655
53 | 2588099.4529 | 1184434.822 | 2588114.4155 | 1184432.4464 | 2588123.4658 | 1184430.1664
54 | 2588228.7245 | 1184230.5704 | 2588225.926 | 1184231.9322 | 2588221.0876 | 1184236.1662 | 2588217.3739 | 1184249.4693 | 2588213.9896 | 1184255.6459 | 2588190.6093 | 1184281.8947 | 2588150.3923 | 1184316.159 | 2588124.0284 | 1184334.1859
55 | 2588123.4658 | 1184430.1664 | 2588128.3318 | 1184428.9404
56 | 2588161.6656 | 1184415.7992 | 2588157.6178 | 1184418.353 | 2588140.658 | 1184425.8351 | 2588128.3318 | 1184428.9404
57 | 2588161.6656 | 1184415.7992 | 2588170.2404 | 1184425.2203 | 2588173.9394 | 1184431.5273 | 2588173.4375 | 1184436.3197 | 2588170.8878 | 1184439.8933 | 2588164.6088 | 1184442.877
58 | 2588164.1655 | 1184443.0876 | 2588164.6088 | 1184442.877
59 | 2588081.9486 | 1184444.7066 | 2588085.5631 | 1184442.6655
60 | 2588164.1655 | 1184443.0876 | 2588156.49 | 1184446.7349
61 | 2588073.7131 | 1184451.3424 | 2588081.9486 | 1184444.7066 | 2588081.9486 | 1184444.7066
62 | 2588155.7909 | 1184447.0671 | 2588156.49 | 1184446.7349
63 | 2588028.869 | 1184481.7602 | 2588029.7782 | 1184481.4303 | 2588034.5678 | 1184479.0624
64 | 2588052.7787 | 1184468.2105 | 2588041.9932 | 1184475.3915 | 2588034.5678 | 1184479.0624
65 | 2588028.869 | 1184481.7602 | 2588023.6779 | 1184483.6435
66 | 2588052.7787 | 1184468.2105 | 2588062.8678 | 1184460.0811
67 | 2588052.7787 | 1184468.2105 | 2588062.6355 | 1184474.2147
68 | 2588052.7787 | 1184468.2105 | 2588043.0113 | 1184457.8915 | 2588024.2626 | 1184421.6074
69 | 2588023.6779 | 1184483.6435 | 2588005.8681 | 1184490.1051 | 2587995.4468 | 1184492.1778
70 | 2588073.7131 | 1184451.3424 | 2588062.8678 | 1184460.0811
71 | 2588075.2246 | 1184482.3314 | 2588070.1866 | 1184478.8144 | 2588062.6355 | 1184474.2147
72 | 2587992.002 | 1184492.863 | 2587995.4468 | 1184492.1778
73 | 2588088.6756 | 1184493.8384 | 2588083.2869 | 1184487.9596 | 2588075.2246 | 1184482.3314
74 | 2587992.002 | 1184492.863 | 2587975.6389 | 1184496.1175
75 | 2588088.6756 | 1184493.8384 | 2588097.3597 | 1184503.3126
76 | 2588416.4043 | 1184825.2874 | 2588403.2313 | 1184821.2776 | 2588399.9399 | 1184820.6904
77 | 2588172.137 | 1184696.2183 | 2588399.9399 | 1184820.6904
78 | 2588430.6006 | 1184829.6064 | 2588416.4043 | 1184825.2874
79 | 2588172.137 | 1184696.2183 | 2588168.1085 | 1184701.1878
80 | 2588430.6006 | 1184829.6064 | 2588449.4348 | 1184835.338
81 | 2588430.6006 | 1184829.6064 | 2588431.8671 | 1184849.0362 | 2588430.5758 | 1184860.0111 | 2588425.0036 | 1184867.3924 | 2588423.4635 | 1184871.3236
82 | 2588144.7262 | 1184732.1854 | 2588130.986 | 1184723.3415 | 2588118.8524 | 1184712.5935 | 2588103.171 | 1184702.4307 | 2588079.299 | 1184684.0579 | 2588066.6106 | 1184670.8209
83 | 2588144.7262 | 1184732.1854 | 2588139.9971 | 1184722.1007
84 | 2588066.6106 | 1184670.8209 | 2588063.3705 | 1184687.8029 | 2588059.3034 | 1184703.3969
85 | 2588066.6106 | 1184670.8209 | 2588064.3663 | 1184666.7566 | 2588058.824 | 1184662.2988 | 2588043.0096 | 1184658.2618 | 2588039.1949 | 1184651.7424
86 | 2588139.9971 | 1184722.1007 | 2588159.8117 | 1184711.4224 | 2588168.1085 | 1184701.1878
87 | 2588038.2537 | 1184650.1338 | 2588039.1949 | 1184651.7424
88 | 2588421.7305 | 1184875.7475 | 2588423.4635 | 1184871.3236
89 | 2588038.2537 | 1184650.1338 | 2588028.9915 | 1184629.0193
90 | 2588038.2537 | 1184650.1338 | 2588032.2414 | 1184654.8706 | 2588027.397 | 1184663.4625 | 2588021.34 | 1184668.7552 | 2588018.8156 | 1184677.5686
91 | 2588134.4868 | 1184601.7425 | 2588129.954 | 1184584.8164 | 2588128.0619 | 1184573.7033 | 2588127.8791 | 1184550.9586 | 2588124.6979 | 1184540.2038 | 2588112.1753 | 1184522.9359
92 | 2588112.1753 | 1184522.9359 | 2588100.1609 | 1184506.3687 | 2588097.3597 | 1184503.3126
93 | 2587988.3337 | 1184560.1536 | 2587996.6364 | 1184574.2127
94 | 2587976.7719 | 1184520.7945 | 2587986.5637 | 1184557.1565 | 2587988.3337 | 1184560.1536
95 | 2587997.6456 | 1184575.9216 | 2587996.6364 | 1184574.2127
96 | 2587970.4069 | 1184497.1581 | 2587976.7719 | 1184520.7945
97 | 2587997.6456 | 1184575.9216 | 2587989.2985 | 1184584.8208 | 2587989.2209 | 1184584.8699
98 | 2587997.6456 | 1184575.9216 | 2588006.8936 | 1184591.5872
99 | 2587970.4069 | 1184497.1581 | 2587975.6389 | 1184496.1175
100 | 2587970.4069 | 1184497.1581 | 2587951.2871 | 1184500.6208 | 2587935.1012 | 1184506.1266
101 | 2588006.8936 | 1184591.5872 | 2588028.9915 | 1184629.0193
102 | 2587935.1012 | 1184506.1266 | 2587931.1523 | 1184507.4699
103 | 2587915.1879 | 1184512.9003 | 2587931.1523 | 1184507.4699
104 | 2587915.1879 | 1184512.9003 | 2587925.402 | 1184543.9512
105 | 2587915.1879 | 1184512.9003 | 2587908.1219 | 1184515.2899
106 | 2587905.2135 | 1184516.2735 | 2587908.1219 | 1184515.2899
107 | 2587905.2135 | 1184516.2735 | 2587892.807 | 1184520.4691
108 | 2587876.4046 | 1184525.7398 | 2587878.8751 | 1184525.1805 | 2587892.807 | 1184520.4691
109 | 2587856.5193 | 1184528.137 | 2587866.2876 | 1184528.0299 | 2587876.4046 | 1184525.7398
110 | 2587856.5193 | 1184528.137 | 2587835.1482 | 1184528.3714 | 2587812.9918 | 1184531.2964
111 | 2587790.3279 | 1184534.2885 | 2587812.9918 | 1184531.2964
112 | 2587790.3279 | 1184534.2885 | 2587731.1622 | 1184538.1899
113 | 2587731.1622 | 1184538.1899 | 2587724.7015 | 1184554.8563 | 2587711.1771 | 1184596.2904
114 | 2588228.7245 | 1184230.5704 | 2588231.7649 | 1184231.8428 | 2588234.5156 | 1184233.3271 | 2588240.0844 | 1184239.4526 | 2588241.1051 | 1184239.7874
115 | 2587703.5135 | 1184622.4817 | 2587709.8286 | 1184600.4217 | 2587711.1771 | 1184596.2904
116 | 2588524.0358 | 1183886.716 | 2588494.6139 | 1183869.0415 | 2588493.1933 | 1183867.8601
117 | 2588524.0358 | 1183886.716 | 2588546.266 | 1183903.7931
118 | 2588546.266 | 1183903.7931 | 2588559.6085 | 1183913.7365
119 | 2588544.8531 | 1183923.2281 | 2588545.5287 | 1183917.2904 | 2588546.0823 | 1183911.4641 | 2588546.266 | 1183903.7931
120 | 2588529.023 | 1183916.1225 | 2588533.2421 | 1183918.0163
121 | 2588544.8531 | 1183923.2281 | 2588533.2421 | 1183918.0163
122 | 2588578.8081 | 1183928.0447 | 2588559.6085 | 1183913.7365

## bus_geodata
| x | y | coords
0 | 2587833.0774 | 1184962.5883
1 | 2587678.1176 | 1184729.8876
2 | 2587250.9659 | 1184058.895
3 | 2587255.9683 | 1184045.4696
4 | 2587275.7064 | 1183980.0464
5 | 2587348.7365 | 1183788.2917
6 | 2587761.2033 | 1184061.9409
7 | 2587768.5622 | 1184082.2995
8 | 2587802.3898 | 1184159.6812
9 | 2587839.9796 | 1184186.819
10 | 2587907.3867 | 1184230.837
11 | 2587987.229 | 1184349.9369
12 | 2588010.4767 | 1184394.9277
13 | 2588009.8612 | 1184336.2699
14 | 2588015.0551 | 1184403.7883
15 | 2588014.0695 | 1184306.5826
16 | 2587552.7835 | 1183780.319
17 | 2587530.5825 | 1183765.3295
18 | 2587572.3709 | 1183792.5896
19 | 2587526.8616 | 1183761.9812
20 | 2587577.9735 | 1183796.1241
21 | 2587553.0632 | 1183794.8032
22 | 2587495.0582 | 1183682.3834
23 | 2587619.5991 | 1183777.7213
24 | 2587552.1824 | 1183794.6806
25 | 2587500.2714 | 1183602.22
26 | 2587409.7009 | 1183754.5117
27 | 2587671.9964 | 1183768.3699
28 | 2587747.5443 | 1183728.5953
29 | 2587551.2154 | 1183794.5459
30 | 2587911.5831 | 1183692.9174
31 | 2587947.3643 | 1183679.1424
32 | 2588002.1775 | 1183677.2991
33 | 2588060.5695 | 1183699.1087
34 | 2587959.5766 | 1183675.0776
35 | 2588080.6436 | 1183702.1933
36 | 2587993.1815 | 1183726.3537
37 | 2587938.2677 | 1183649.7479
38 | 2588285.7762 | 1183787.1733
39 | 2587978.8731 | 1184003.2969
40 | 2588293.0512 | 1183775.7976
41 | 2588351.6377 | 1183782.2617
42 | 2588491.6398 | 1183866.5682
43 | 2588091.3147 | 1184193.6692
44 | 2588008.1687 | 1184298.6348
45 | 2588005.3964 | 1184301.0579
46 | 2588098.3615 | 1184354.7161
47 | 2588099.4529 | 1184434.822
48 | 2588124.0284 | 1184334.1859
49 | 2587632.8478 | 1183608.1239
50 | 2588128.3318 | 1184428.9404
51 | 2588123.4658 | 1184430.1664
52 | 2588161.6656 | 1184415.7992
53 | 2588164.6088 | 1184442.877
54 | 2588085.5631 | 1184442.6655
55 | 2588164.1655 | 1184443.0876
56 | 2588081.9486 | 1184444.7066
57 | 2588156.49 | 1184446.7349
58 | 2588034.5678 | 1184479.0624
59 | 2588028.869 | 1184481.7602
60 | 2588052.7787 | 1184468.2105
61 | 2588023.6779 | 1184483.6435
62 | 2588062.8678 | 1184460.0811
63 | 2588062.6355 | 1184474.2147
64 | 2588024.2626 | 1184421.6074
65 | 2587995.4468 | 1184492.1778
66 | 2588073.7131 | 1184451.3424
67 | 2588075.2246 | 1184482.3314
68 | 2587992.002 | 1184492.863
69 | 2588088.6756 | 1184493.8384
70 | 2588399.9399 | 1184820.6904
71 | 2588416.4043 | 1184825.2874
72 | 2588172.137 | 1184696.2183
73 | 2588430.6006 | 1184829.6064
74 | 2588144.7262 | 1184732.1854
75 | 2588066.6106 | 1184670.8209
76 | 2588139.9971 | 1184722.1007
77 | 2588059.3034 | 1184703.3969
78 | 2588039.1949 | 1184651.7424
79 | 2588168.1085 | 1184701.1878
80 | 2588449.4348 | 1184835.338
81 | 2588423.4635 | 1184871.3236
82 | 2588038.2537 | 1184650.1338
83 | 2588134.4868 | 1184601.7425
84 | 2588112.1753 | 1184522.9359
85 | 2588421.7305 | 1184875.7475
86 | 2587988.3337 | 1184560.1536
87 | 2587996.6364 | 1184574.2127
88 | 2587976.7719 | 1184520.7945
89 | 2587997.6456 | 1184575.9216
90 | 2587970.4069 | 1184497.1581
91 | 2587989.2209 | 1184584.8699
92 | 2588006.8936 | 1184591.5872
93 | 2587975.6389 | 1184496.1175
94 | 2587935.1012 | 1184506.1266
95 | 2588028.9915 | 1184629.0193
96 | 2587931.1523 | 1184507.4699
97 | 2587915.1879 | 1184512.9003
98 | 2587925.402 | 1184543.9512
99 | 2587908.1219 | 1184515.2899
100 | 2587905.2135 | 1184516.2735
101 | 2587876.4046 | 1184525.7398
102 | 2587892.807 | 1184520.4691
103 | 2587856.5193 | 1184528.137
104 | 2587812.9918 | 1184531.2964
105 | 2587790.3279 | 1184534.2885
106 | 2587731.1622 | 1184538.1899
107 | 2588241.1051 | 1184239.7874
108 | 2588228.7245 | 1184230.5704
109 | 2588018.8156 | 1184677.5686
110 | 2587711.1771 | 1184596.2904
111 | 2587703.5135 | 1184622.4817
112 | 2588006.1287 | 1184316.526
113 | 2588097.3597 | 1184503.3126
114 | 2588155.7909 | 1184447.0671
115 | 2588486.007 | 1183895.2331
116 | 2588493.1933 | 1183867.8601
117 | 2588524.0358 | 1183886.716
118 | 2588546.266 | 1183903.7931
119 | 2588529.023 | 1183916.1225
120 | 2588533.2421 | 1183918.0163
121 | 2588544.8531 | 1183923.2281
122 | 2588559.6085 | 1183913.7365
123 | 2588578.8081 | 1183928.0447
124 | 2588052.7787 | 1184468.2105

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99011 | -0.069699 | 0.00044722 | 0.00011208
1 | 0.99029 | -0.068388 | 0 | 0
2 | 0.97004 | -0.21405 | 0.0009687 | 0.00024278
3 | 0.97006 | -0.2139 | 0.00020286 | 5.0841e-05
4 | 0.97018 | -0.21302 | 0 | 0
5 | 0.97054 | -0.21044 | 0.00021352 | 5.3513e-05
6 | 0.99224 | -0.054471 | 0.00078056 | 0.00019563
7 | 0.99226 | -0.0543 | 0 | 0
8 | 0.99238 | -0.053435 | 0 | 0
9 | 0.99244 | -0.053062 | 0.00069639 | 0.00017453
10 | 0.99261 | -0.051831 | 0 | 0
11 | 0.99291 | -0.049641 | 0 | 0
12 | 0.99443 | -0.038963 | 0.00053286 | 0.00013355
13 | 0.99216 | -0.054906 | 0.00055029 | 0.00013792
14 | 0.99474 | -0.036809 | 0.0005325 | 0.00013346
15 | 0.99117 | -0.061882 | 0 | 0
16 | 0.97127 | -0.20498 | 0.00074266 | 0.00018613
17 | 0.97118 | -0.20568 | 9.076e-05 | 2.2747e-05
18 | 0.97138 | -0.2042 | 0 | 0
19 | 0.97116 | -0.20581 | 0.00051236 | 0.00012841
20 | 0.97141 | -0.20394 | 0 | 0
21 | 0.97136 | -0.20429 | 0.0001215 | 3.0451e-05
22 | 0.97093 | -0.20755 | 0 | 0
23 | 0.97165 | -0.20218 | 0.00055726 | 0.00013966
24 | 0.97136 | -0.20429 | 6.9444e-05 | 1.7404e-05
25 | 0.97088 | -0.20791 | 0 | 0
26 | 0.9707 | -0.20926 | 0 | 0
27 | 0.97198 | -0.19976 | 0 | 0
28 | 0.97251 | -0.19582 | 0.00033197 | 8.3198e-05
29 | 0.97136 | -0.20429 | 0.00023332 | 5.8476e-05
30 | 0.97362 | -0.18771 | 0 | 0
31 | 0.97387 | -0.18587 | 0.00033893 | 8.4944e-05
32 | 0.97435 | -0.18231 | 0.0016567 | 0.00041521
33 | 0.97505 | -0.17719 | 0 | 0
34 | 0.97396 | -0.18521 | 0 | 0
35 | 0.97486 | -0.17857 | 0.00025895 | 6.49e-05
36 | 0.97658 | -0.16612 | 0.00012908 | 3.2352e-05
37 | 0.9739 | -0.18563 | 0.0012199 | 0.00030574
38 | 0.97286 | -0.19306 | 0 | 0
39 | 0.98235 | -0.12459 | 0.0016161 | 0.00040504
40 | 0.97274 | -0.19394 | 0 | 0
41 | 0.9722 | -0.19778 | 0.00032292 | 8.0931e-05
42 | 0.97076 | -0.20824 | 0 | 0
43 | 0.98777 | -0.085929 | 0 | 0
44 | 0.99094 | -0.063535 | 0 | 0
45 | 0.99094 | -0.06355 | 0.00038469 | 9.6414e-05
46 | 0.99964 | -0.0025342 | 0 | 0
47 | 1 | 0 | -0.080071 | -0.019916
48 | 0.99949 | -0.0035652 | 0.00077624 | 0.00019455
49 | 0.9708 | -0.20848 | 0.0004009 | 0.00010047
50 | 0.99978 | -0.001531 | 0.0019709 | 0.00049396
51 | 0.99981 | -0.0013163 | 0.0010987 | 0.00027537
52 | 0.99966 | -0.0023632 | 0 | 0
53 | 0.99954 | -0.0031983 | 0.00039029 | 9.7816e-05
54 | 0.9992 | -0.0056065 | 0.00027829 | 6.9747e-05
55 | 0.99954 | -0.0032077 | 0.00069326 | 0.00017375
56 | 0.99899 | -0.0070611 | 0.00032369 | 8.1124e-05
57 | 0.99953 | -0.0033116 | 0.00052961 | 0.00013273
58 | 0.99605 | -0.027582 | 0.0020808 | 0.00052149
59 | 0.99575 | -0.029691 | 0.00079404 | 0.00019901
60 | 0.99713 | -0.020047 | 0 | 0
61 | 0.99549 | -0.031494 | 0.00049489 | 0.00012403
62 | 0.99777 | -0.015576 | 0.00032917 | 8.2499e-05
63 | 0.99694 | -0.021346 | 0.00027092 | 6.7898e-05
64 | 0.99537 | -0.032375 | 0.00033633 | 8.4291e-05
65 | 0.99414 | -0.041016 | 0.00083549 | 0.00020939
66 | 0.99846 | -0.010753 | 0.00063981 | 0.00016035
67 | 0.99671 | -0.022994 | 0.00041949 | 0.00010513
68 | 0.99398 | -0.042119 | 0.001731 | 0.00043383
69 | 0.99644 | -0.024877 | 0.0025979 | 0.0006511
70 | 0.98231 | -0.12479 | 0.002998 | 0.00075136
71 | 0.98216 | -0.1258 | 0 | 0
72 | 0.98558 | -0.1015 | 0.0028319 | 0.00070974
73 | 0.98204 | -0.12667 | 0 | 0
74 | 0.98651 | -0.09486 | 0 | 0
75 | 0.98827 | -0.082389 | 0 | 0
76 | 0.98631 | -0.096258 | 0 | 0
77 | 0.98826 | -0.082495 | 0.0003089 | 7.7418e-05
78 | 0.98892 | -0.077819 | 0.00039793 | 9.9731e-05
79 | 0.98568 | -0.10074 | 0.00068262 | 0.00017108
80 | 0.98202 | -0.12681 | 0.00071199 | 0.00017844
81 | 0.98172 | -0.12893 | 0.0036997 | 0.00092723
82 | 0.98895 | -0.077573 | 0 | 0
83 | 0.99591 | -0.028591 | 0.0014516 | 0.00036381
84 | 0.99609 | -0.027359 | 0.0044338 | 0.0011112
85 | 0.98172 | -0.129 | 0.0012724 | 0.0003189
86 | 0.99131 | -0.060904 | 0.0013287 | 0.00033301
87 | 0.99092 | -0.063687 | 0.00021556 | 5.4024e-05
88 | 0.99239 | -0.053346 | 0.00084768 | 0.00021245
89 | 0.99087 | -0.064022 | 0 | 0
90 | 0.99306 | -0.048646 | 0 | 0
91 | 0.99087 | -0.064059 | 0.00029824 | 7.4745e-05
92 | 0.99044 | -0.06703 | 0.00041374 | 0.00010369
93 | 0.99328 | -0.047071 | 0.00018536 | 4.6455e-05
94 | 0.99252 | -0.052423 | 0.0013701 | 0.00034338
95 | 0.98945 | -0.074044 | 0.00083627 | 0.00020959
96 | 0.99247 | -0.052796 | 0.00029182 | 7.3137e-05
97 | 0.99226 | -0.054257 | 0 | 0
98 | 0.99224 | -0.054443 | 0.00056097 | 0.00014059
99 | 0.99218 | -0.05486 | 0.00032366 | 8.1116e-05
100 | 0.99215 | -0.055099 | 0.00047268 | 0.00011846
101 | 0.99184 | -0.057277 | 0.00097127 | 0.00024342
102 | 0.99201 | -0.056053 | 0.00017979 | 4.5059e-05
103 | 0.99167 | -0.058509 | 0.00030901 | 7.7446e-05
104 | 0.99131 | -0.061047 | 0.001382 | 0.00034637
105 | 0.99117 | -0.062053 | 0 | 0
106 | 0.99081 | -0.064653 | 0 | 0
107 | 0.99894 | -0.0074582 | 0.0023366 | 0.00058562
108 | 0.99899 | -0.0070894 | 0 | 0
109 | 0.98885 | -0.078297 | 0.002042 | 0.00051176
110 | 0.99043 | -0.067354 | 0.0025546 | 0.00064024
111 | 0.99036 | -0.067844 | 0.0012771 | 0.00032006
112 | 0.99113 | -0.062185 | 0.0023388 | 0.00058616
113 | 0.9963 | -0.0259 | 0.0020269 | 0.000508
114 | 0.99953 | -0.003317 | 0.00069326 | 0.00017375
115 | 0.97072 | -0.20853 | 0.00093238 | 0.00023368
116 | 0.97074 | -0.20834 | 0.00014493 | 3.6324e-05
117 | 0.97049 | -0.21016 | 0 | 0
118 | 0.9703 | -0.21157 | 0 | 0
119 | 0.97027 | -0.21174 | 0.00030058 | 7.5332e-05
120 | 0.97028 | -0.21172 | 0.00015009 | 3.7617e-05
121 | 0.97028 | -0.21166 | 0 | 0
122 | 0.97019 | -0.21233 | 0.0032298 | 0.00080946
123 | 0.97015 | -0.21259 | 0.0010555 | 0.00026452
124 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00044722 | -0.00011208 | 0.0004473 | 0.00010852 | 7.8661e-08 | -3.566e-06 | 0.00067212 | 0.00067086 | 0.00067212 | 0.99011 | -0.069699 | 0.99029 | -0.068388 | 0.24893
1 | -0.0004473 | -0.00010852 | 0.00044733 | 0.00010709 | 3.1301e-08 | -1.4231e-06 | 0.00067086 | 0.00067037 | 0.00067086 | 0.99029 | -0.068388 | 0.99036 | -0.067844 | 0.24847
2 | -0.0009687 | -0.00024278 | 0.00096872 | 0.0002426 | 2.0279e-08 | -1.7391e-07 | 0.001486 | 0.0014859 | 0.001486 | 0.97004 | -0.21405 | 0.97006 | -0.2139 | 0.55035
3 | -0.0011716 | -0.00029345 | 0.0011717 | 0.00029263 | 1.4127e-07 | -8.1138e-07 | 0.0017971 | 0.0017967 | 0.0017971 | 0.97006 | -0.2139 | 0.97018 | -0.21302 | 0.66558
4 | -0.0011717 | -0.00029263 | 0.0011721 | 0.00029026 | 4.1314e-07 | -2.3758e-06 | 0.0017967 | 0.0017958 | 0.0017967 | 0.97018 | -0.21302 | 0.97054 | -0.21044 | 0.66546
5 | -0.0013856 | -0.00034377 | 0.0013859 | 0.00034288 | 2.2095e-07 | -8.8599e-07 | 0.0021232 | 0.0021229 | 0.0021232 | 0.97054 | -0.21044 | 0.9707 | -0.20926 | 0.78637
6 | -0.00078056 | -0.00019563 | 0.00078058 | 0.00019536 | 1.8515e-08 | -2.7261e-07 | 0.0011706 | 0.0011705 | 0.0011706 | 0.99224 | -0.054471 | 0.99226 | -0.0543 | 0.43355
7 | -0.00078058 | -0.00019536 | 0.00078068 | 0.00019399 | 9.2501e-08 | -1.3628e-06 | 0.0011705 | 0.00117 | 0.0011705 | 0.99226 | -0.0543 | 0.99238 | -0.053435 | 0.43351
8 | -0.00078068 | -0.00019399 | 0.00078071 | 0.00019341 | 3.961e-08 | -5.8405e-07 | 0.00117 | 0.0011698 | 0.00117 | 0.99238 | -0.053435 | 0.99244 | -0.053062 | 0.43333
9 | -0.0014771 | -0.00036794 | 0.0014774 | 0.00036699 | 2.4809e-07 | -9.5308e-07 | 0.0022139 | 0.0022135 | 0.0022139 | 0.99244 | -0.053062 | 0.99261 | -0.051831 | 0.81997
10 | -0.0014774 | -0.00036699 | 0.0014778 | 0.0003653 | 4.3798e-07 | -1.6843e-06 | 0.0022135 | 0.0022129 | 0.0022135 | 0.99261 | -0.051831 | 0.99291 | -0.049641 | 0.81983
11 | -0.020877 | -0.0052345 | 0.020908 | 0.0052458 | 3.0934e-05 | 1.1242e-05 | 0.031288 | 0.031287 | 0.031288 | 0.99291 | -0.049641 | 0.99443 | -0.038963 | 11.588
12 | 0.019399 | 0.0048692 | -0.019385 | -0.0048641 | 1.4172e-05 | 5.1036e-06 | 0.029075 | 0.029075 | 0.029075 | 0.99291 | -0.049641 | 0.99216 | -0.054906 | 10.7684
13 | -0.021441 | -0.0053793 | 0.021447 | 0.0053817 | 6.4066e-06 | 2.3346e-06 | 0.032085 | 0.032085 | 0.032085 | 0.99443 | -0.038963 | 0.99474 | -0.036809 | 11.8832
14 | 0.018834 | 0.0047262 | -0.018816 | -0.0047197 | 1.8218e-05 | 6.5351e-06 | 0.028249 | 0.02825 | 0.02825 | 0.99216 | -0.054906 | 0.99117 | -0.061882 | 10.4628
15 | -0.021979 | -0.0055151 | 0.021993 | 0.0055201 | 1.3532e-05 | 4.944e-06 | 0.032881 | 0.032881 | 0.032881 | 0.99474 | -0.036809 | 0.99537 | -0.032375 | 12.1782
16 | 0.0023389 | 0.00058603 | -0.0023388 | -0.00058616 | 9.7797e-08 | -1.2622e-07 | 0.0035112 | 0.0035113 | 0.0035113 | 0.99117 | -0.061882 | 0.99113 | -0.062185 | 1.3005
17 | 0.016477 | 0.0041336 | -0.016474 | -0.0041323 | 3.7768e-06 | 1.3252e-06 | 0.024738 | 0.024738 | 0.024738 | 0.99117 | -0.061882 | 0.99094 | -0.063535 | 9.1624
18 | 0.0023909 | 0.00058939 | -0.0023907 | -0.00058964 | 2.2404e-07 | -2.456e-07 | 0.0036595 | 0.0036596 | 0.0036596 | 0.97127 | -0.20498 | 0.97118 | -0.20568 | 1.3554
19 | -0.0031336 | -0.00077552 | 0.0031339 | 0.00077536 | 3.3191e-07 | -1.5843e-07 | 0.0047972 | 0.0047971 | 0.0047972 | 0.97127 | -0.20498 | 0.97138 | -0.2042 | 1.7768
20 | 0.0022999 | 0.00056689 | -0.0022999 | -0.00056694 | 3.8713e-08 | -4.7048e-08 | 0.0035205 | 0.0035205 | 0.0035205 | 0.97118 | -0.20568 | 0.97116 | -0.20581 | 1.3039
21 | -0.0035582 | -0.00088142 | 0.0035583 | 0.00088139 | 1.2239e-07 | -3.4766e-08 | 0.005447 | 0.0054469 | 0.005447 | 0.97138 | -0.2042 | 0.97141 | -0.20394 | 2.0174
22 | 0.00042427 | 0.00010606 | -0.00042427 | -0.00010631 | 5.3742e-09 | -2.5037e-07 | 0.00064983 | 0.00064992 | 0.00064992 | 0.97138 | -0.2042 | 0.97136 | -0.20429 | 0.24071
23 | 0.0017875 | 0.00043853 | -0.0017871 | -0.00043947 | 4.1582e-07 | -9.4153e-07 | 0.0027355 | 0.0027359 | 0.0027359 | 0.97116 | -0.20581 | 0.97093 | -0.20755 | 1.0133
24 | -0.0035583 | -0.00088139 | 0.0035592 | 0.00088115 | 8.4736e-07 | -2.4088e-07 | 0.0054469 | 0.0054467 | 0.0054469 | 0.97141 | -0.20394 | 0.97165 | -0.20218 | 2.0174
25 | 0.00030277 | 7.5857e-05 | -0.00030277 | -7.5868e-05 | 1.1932e-10 | -1.0962e-08 | 0.00046379 | 0.0004638 | 0.0004638 | 0.97136 | -0.20429 | 0.97136 | -0.20429 | 0.17178
26 | 0.00040095 | 9.7864e-05 | -0.00040093 | -9.885e-05 | 1.8886e-08 | -9.8647e-07 | 0.00061354 | 0.0006139 | 0.0006139 | 0.97093 | -0.20755 | 0.97088 | -0.20791 | 0.22737
27 | 0.0013862 | 0.00034161 | -0.0013859 | -0.00034288 | 3.1803e-07 | -1.2764e-06 | 0.0021224 | 0.0021229 | 0.0021229 | 0.97093 | -0.20755 | 0.9707 | -0.20926 | 0.78624
28 | -0.0041164 | -0.0010208 | 0.0041178 | 0.0010207 | 1.35e-06 | -1.5614e-07 | 0.0063001 | 0.0062999 | 0.0063001 | 0.97165 | -0.20218 | 0.97198 | -0.19976 | 2.3334
29 | 0.00023332 | 5.8464e-05 | -0.00023332 | -5.8476e-05 | 7.7803e-11 | -1.2055e-08 | 0.00035742 | 0.00035742 | 0.00035742 | 0.97136 | -0.20429 | 0.97136 | -0.20429 | 0.13238
30 | 0.00040093 | 9.885e-05 | -0.0004009 | -0.00010047 | 3.1148e-08 | -1.6242e-06 | 0.0006139 | 0.00061448 | 0.00061448 | 0.97088 | -0.20791 | 0.9708 | -0.20848 | 0.22759
31 | -0.0041178 | -0.0010207 | 0.00412 | 0.0010204 | 2.1985e-06 | -2.5537e-07 | 0.0062999 | 0.0062995 | 0.0062999 | 0.97198 | -0.19976 | 0.97251 | -0.19582 | 2.3333
32 | -0.0044519 | -0.0011036 | 0.0044568 | 0.0011034 | 4.8884e-06 | -2.2004e-07 | 0.0068074 | 0.0068067 | 0.0068074 | 0.97251 | -0.19582 | 0.97362 | -0.18771 | 2.5213
33 | -0.0044568 | -0.0011034 | 0.0044579 | 0.0011033 | 1.1085e-06 | -5.0623e-08 | 0.0068067 | 0.0068065 | 0.0068067 | 0.97362 | -0.18771 | 0.97387 | -0.18587 | 2.521
34 | -0.0047969 | -0.0011883 | 0.0047973 | 0.0011883 | 4.3115e-07 | 5.5553e-09 | 0.0073244 | 0.0073243 | 0.0073244 | 0.97387 | -0.18587 | 0.97396 | -0.18521 | 2.7127
35 | -0.0076764 | -0.0019092 | 0.0076817 | 0.0019105 | 5.3605e-06 | 1.2819e-06 | 0.011718 | 0.011718 | 0.011718 | 0.97435 | -0.18231 | 0.97505 | -0.17719 | 4.34
36 | 0.0060197 | 0.001494 | -0.0060173 | -0.0014936 | 2.367e-06 | 3.5097e-07 | 0.0091879 | 0.0091881 | 0.0091881 | 0.97435 | -0.18231 | 0.97396 | -0.18521 | 3.403
37 | 0.0064237 | 0.0016056 | -0.0064225 | -0.0016054 | 1.2233e-06 | 2.1603e-07 | 0.0098016 | 0.0098017 | 0.0098017 | 0.97505 | -0.17719 | 0.97486 | -0.17857 | 3.6303
38 | -0.014105 | -0.0035161 | 0.014127 | 0.0035234 | 2.1414e-05 | 7.3104e-06 | 0.021519 | 0.021519 | 0.021519 | 0.97505 | -0.17719 | 0.97658 | -0.16612 | 7.9701
39 | 0.00122 | 0.00030536 | -0.0012199 | -0.00030574 | 7.1971e-08 | -3.8548e-07 | 0.0018638 | 0.0018639 | 0.0018639 | 0.97396 | -0.18521 | 0.9739 | -0.18563 | 0.69034
40 | 0.0061636 | 0.0015405 | -0.0061513 | -0.0015385 | 1.2292e-05 | 1.9579e-06 | 0.0094065 | 0.0094075 | 0.0094075 | 0.97486 | -0.17857 | 0.97286 | -0.19306 | 3.4842
41 | -0.014256 | -0.0035558 | 0.014338 | 0.0035837 | 8.1597e-05 | 2.7893e-05 | 0.021716 | 0.021714 | 0.021716 | 0.97658 | -0.16612 | 0.98235 | -0.12459 | 8.0428
42 | 0.0061513 | 0.0015385 | -0.0061505 | -0.0015384 | 7.452e-07 | 1.1908e-07 | 0.0094075 | 0.0094075 | 0.0094075 | 0.97286 | -0.19306 | 0.97274 | -0.19394 | 3.4843
43 | -0.015954 | -0.0039887 | 0.016039 | 0.0040185 | 8.5378e-05 | 2.9854e-05 | 0.024162 | 0.024161 | 0.024162 | 0.98235 | -0.12459 | 0.98777 | -0.085929 | 8.9491
44 | 0.0061505 | 0.0015384 | -0.0061473 | -0.0015379 | 3.2552e-06 | 5.207e-07 | 0.0094075 | 0.0094078 | 0.0094078 | 0.97274 | -0.19394 | 0.9722 | -0.19778 | 3.4844
45 | 0.0058244 | 0.001457 | -0.005816 | -0.0014558 | 8.4009e-06 | 1.1332e-06 | 0.0089135 | 0.0089143 | 0.0089143 | 0.9722 | -0.19778 | 0.97076 | -0.20824 | 3.3016
46 | 0.0048835 | 0.0012225 | -0.0048835 | -0.0012225 | 7.0639e-08 | 2.1895e-09 | 0.0074852 | 0.0074852 | 0.0074852 | 0.97076 | -0.20824 | 0.97074 | -0.20834 | 2.7723
47 | 0.00093242 | 0.00023333 | -0.00093238 | -0.00023368 | 3.7291e-08 | -3.4736e-07 | 0.0014291 | 0.0014293 | 0.0014293 | 0.97076 | -0.20824 | 0.97072 | -0.20853 | 0.52935
48 | -0.016039 | -0.0040185 | 0.016089 | 0.004036 | 4.9832e-05 | 1.7409e-05 | 0.024161 | 0.024161 | 0.024161 | 0.98777 | -0.085929 | 0.99094 | -0.063535 | 8.9487
49 | 0.0003847 | 9.6367e-05 | -0.00038469 | -9.6414e-05 | 7.6665e-10 | -4.7138e-08 | 0.00057765 | 0.00057767 | 0.00057767 | 0.99094 | -0.063535 | 0.99094 | -0.06355 | 0.21395
50 | -0.0031146 | -0.00077821 | 0.0031157 | 0.00077756 | 1.0851e-06 | -6.4409e-07 | 0.0046354 | 0.004635 | 0.0046354 | 0.99964 | -0.0025342 | 1 | 0 | 1.7168
51 | 0.0031146 | 0.00077821 | -0.0031141 | -0.00077847 | 4.4204e-07 | -2.6213e-07 | 0.0046354 | 0.0046355 | 0.0046355 | 0.99964 | -0.0025342 | 0.99949 | -0.0035652 | 1.7169
52 | 0.070777 | 0.017792 | -0.070722 | -0.017771 | 5.5222e-05 | 2.0821e-05 | 0.10534 | 0.10534 | 0.10534 | 1 | 0 | 0.9992 | -0.0056065 | 19.5068
53 | 0.0053777 | 0.0013465 | -0.0053768 | -0.0013465 | 9.7819e-07 | 5.5087e-08 | 0.0080017 | 0.0080018 | 0.0080018 | 1 | 0 | 0.99981 | -0.0013163 | 2.9636
54 | 0.0023379 | 0.00058392 | -0.0023368 | -0.00058546 | 1.1361e-06 | -1.5321e-06 | 0.0034799 | 0.0034806 | 0.0034806 | 0.99949 | -0.0035652 | 0.99899 | -0.0070894 | 1.2891
55 | -0.0042779 | -0.0010711 | 0.004278 | 0.0010711 | 1.2692e-07 | -1.699e-08 | 0.0063666 | 0.0063666 | 0.0063666 | 0.99978 | -0.001531 | 0.99981 | -0.0013163 | 2.358
56 | 0.002307 | 0.00057718 | -0.0023067 | -0.00057755 | 2.6505e-07 | -3.7054e-07 | 0.0034332 | 0.0034334 | 0.0034334 | 0.99978 | -0.001531 | 0.99966 | -0.0023632 | 1.2716
57 | 0.0023067 | 0.00057755 | -0.0023064 | -0.00057792 | 2.6637e-07 | -3.7224e-07 | 0.0034334 | 0.0034335 | 0.0034335 | 0.99966 | -0.0023632 | 0.99954 | -0.0031983 | 1.2717
58 | 0.0019162 | 0.00048011 | -0.0019162 | -0.00048011 | 2.4926e-09 | -5.4756e-09 | 0.0028525 | 0.0028525 | 0.0028525 | 0.99954 | -0.0031983 | 0.99954 | -0.0032077 | 1.0565
59 | 0.070444 | 0.017701 | -0.07043 | -0.017696 | 1.4258e-05 | 5.3749e-06 | 0.10492 | 0.10492 | 0.10492 | 0.9992 | -0.0056065 | 0.99899 | -0.0070611 | 19.4301
60 | 0.0012229 | 0.00030637 | -0.0012229 | -0.00030647 | 1.7574e-08 | -1.0462e-07 | 0.0018205 | 0.0018205 | 0.0018205 | 0.99954 | -0.0032077 | 0.99953 | -0.0033116 | 0.67426
61 | 0.070106 | 0.017615 | -0.07007 | -0.017601 | 3.5993e-05 | 1.3567e-05 | 0.10444 | 0.10444 | 0.10444 | 0.99899 | -0.0070611 | 0.99846 | -0.010753 | 19.3408
62 | 0.00069326 | 0.00017374 | -0.00069326 | -0.00017375 | 5.1445e-10 | -9.9473e-09 | 0.0010321 | 0.0010321 | 0.0010321 | 0.99953 | -0.0033116 | 0.99953 | -0.003317 | 0.38225
63 | 0.033316 | 0.0083623 | -0.033306 | -0.0083586 | 9.7556e-06 | 3.67e-06 | 0.049775 | 0.049775 | 0.049775 | 0.99605 | -0.027582 | 0.99575 | -0.029691 | 18.4353
64 | -0.035396 | -0.0088838 | 0.035434 | 0.0088977 | 3.7068e-05 | 1.398e-05 | 0.052884 | 0.052884 | 0.052884 | 0.99605 | -0.027582 | 0.99713 | -0.020047 | 19.5866
65 | 0.032512 | 0.0081596 | -0.032504 | -0.0081565 | 8.1352e-06 | 3.0571e-06 | 0.048589 | 0.048589 | 0.048589 | 0.99575 | -0.029691 | 0.99549 | -0.031494 | 17.9958
66 | -0.069012 | -0.017325 | 0.069054 | 0.017341 | 4.2884e-05 | 1.6156e-05 | 0.103 | 0.103 | 0.103 | 0.99713 | -0.020047 | 0.99777 | -0.015576 | 19.0734
67 | 0.01121 | 0.0028088 | -0.011208 | -0.0028081 | 2.0155e-06 | 6.2469e-07 | 0.016729 | 0.016729 | 0.016729 | 0.99713 | -0.020047 | 0.99694 | -0.021346 | 6.196
68 | 0.022368 | 0.0056184 | -0.022329 | -0.0056043 | 3.8284e-05 | 1.4008e-05 | 0.033384 | 0.033384 | 0.033384 | 0.99713 | -0.020047 | 0.99537 | -0.032375 | 12.3644
69 | 0.032009 | 0.0080325 | -0.031967 | -0.0080166 | 4.2247e-05 | 1.5865e-05 | 0.047849 | 0.047849 | 0.047849 | 0.99549 | -0.031494 | 0.99414 | -0.041016 | 17.7219
70 | -0.069384 | -0.017424 | 0.06943 | 0.017441 | 4.6538e-05 | 1.7535e-05 | 0.10349 | 0.10349 | 0.10349 | 0.99777 | -0.015576 | 0.99846 | -0.010753 | 19.1643
71 | 0.010938 | 0.0027402 | -0.010935 | -0.0027395 | 2.4921e-06 | 7.6314e-07 | 0.016325 | 0.016325 | 0.016325 | 0.99694 | -0.021346 | 0.99671 | -0.022994 | 6.0462
72 | 0.031131 | 0.0078072 | -0.031126 | -0.0078055 | 4.7591e-06 | 1.7849e-06 | 0.046599 | 0.046599 | 0.046599 | 0.99414 | -0.041016 | 0.99398 | -0.042119 | 17.2587
73 | 0.010516 | 0.0026343 | -0.010513 | -0.0026335 | 2.7385e-06 | 8.2123e-07 | 0.015699 | 0.015699 | 0.015699 | 0.99671 | -0.022994 | 0.99644 | -0.024877 | 5.8143
74 | 0.029395 | 0.0073716 | -0.029375 | -0.0073641 | 2.0161e-05 | 7.5383e-06 | 0.044007 | 0.044007 | 0.044007 | 0.99398 | -0.042119 | 0.99328 | -0.047071 | 16.299
75 | 0.0079149 | 0.0019824 | -0.0079138 | -0.0019822 | 1.1203e-06 | 2.6349e-07 | 0.011819 | 0.011819 | 0.011819 | 0.99644 | -0.024877 | 0.9963 | -0.0259 | 4.3775
76 | 0.0056872 | 0.0014245 | -0.0056864 | -0.0014244 | 7.9251e-07 | 8.8204e-08 | 0.0086148 | 0.0086148 | 0.0086148 | 0.98231 | -0.12479 | 0.98216 | -0.1258 | 3.1907
77 | -0.0086852 | -0.0021758 | 0.0087132 | 0.0021833 | 2.8034e-05 | 7.4853e-06 | 0.013156 | 0.013155 | 0.013156 | 0.98231 | -0.12479 | 0.98558 | -0.1015 | 4.8726
78 | 0.0056864 | 0.0014244 | -0.0056857 | -0.0014243 | 6.854e-07 | 7.6337e-08 | 0.0086148 | 0.0086149 | 0.0086149 | 0.98216 | -0.1258 | 0.98204 | -0.12667 | 3.1907
79 | -0.011545 | -0.0028931 | 0.011546 | 0.0028935 | 1.2128e-06 | 3.8494e-07 | 0.017431 | 0.017431 | 0.017431 | 0.98558 | -0.1015 | 0.98568 | -0.10074 | 6.4558
80 | 0.000712 | 0.0001782 | -0.00071199 | -0.00017844 | 1.4297e-08 | -2.4358e-07 | 0.0010788 | 0.0010788 | 0.0010788 | 0.98204 | -0.12667 | 0.98202 | -0.12681 | 0.39957
81 | 0.0049737 | 0.0012461 | -0.0049721 | -0.0012461 | 1.5591e-06 | 4.3224e-08 | 0.0075361 | 0.0075363 | 0.0075363 | 0.98204 | -0.12667 | 0.98172 | -0.12893 | 2.7912
82 | -0.012239 | -0.0030678 | 0.01226 | 0.0030746 | 2.1165e-05 | 6.8674e-06 | 0.018461 | 0.01846 | 0.018461 | 0.98651 | -0.09486 | 0.98827 | -0.082389 | 6.8373
83 | 0.012239 | 0.0030678 | -0.012237 | -0.003067 | 2.368e-06 | 7.6862e-07 | 0.018461 | 0.018461 | 0.018461 | 0.98651 | -0.09486 | 0.98631 | -0.096258 | 6.8374
84 | 0.0003089 | 7.6991e-05 | -0.0003089 | -7.7418e-05 | 4.508e-09 | -4.263e-07 | 0.00046496 | 0.00046511 | 0.00046511 | 0.98827 | -0.082389 | 0.98826 | -0.082495 | 0.17226
85 | -0.012569 | -0.0031516 | 0.012577 | 0.0031542 | 7.9632e-06 | 2.6059e-06 | 0.018925 | 0.018925 | 0.018925 | 0.98827 | -0.082389 | 0.98892 | -0.077819 | 7.0094
86 | 0.012237 | 0.003067 | -0.012229 | -0.0030645 | 7.5886e-06 | 2.4636e-06 | 0.018461 | 0.018461 | 0.018461 | 0.98631 | -0.096258 | 0.98568 | -0.10074 | 6.8374
87 | -0.012975 | -0.003254 | 0.012975 | 0.0032541 | 4.4329e-07 | 1.4658e-07 | 0.019524 | 0.019524 | 0.019524 | 0.98892 | -0.077819 | 0.98895 | -0.077573 | 7.2311
88 | 0.0012725 | 0.00031885 | -0.0012724 | -0.0003189 | 1.1028e-08 | -5.5834e-08 | 0.0019287 | 0.0019287 | 0.0019287 | 0.98172 | -0.12893 | 0.98172 | -0.129 | 0.71433
89 | -0.015017 | -0.0037655 | 0.015025 | 0.003768 | 7.3462e-06 | 2.5295e-06 | 0.022596 | 0.022596 | 0.022596 | 0.98895 | -0.077573 | 0.98945 | -0.074044 | 8.3691
90 | 0.0020422 | 0.0005114 | -0.002042 | -0.00051176 | 2.046e-07 | -3.6687e-07 | 0.0030726 | 0.0030727 | 0.0030727 | 0.98895 | -0.077573 | 0.98885 | -0.078297 | 1.138
91 | -0.0014516 | -0.00036381 | 0.0014518 | 0.00036281 | 2.4678e-07 | -9.9944e-07 | 0.0021689 | 0.0021685 | 0.0021689 | 0.99591 | -0.028591 | 0.99609 | -0.027359 | 0.80328
92 | -0.0058856 | -0.001474 | 0.0058868 | 0.0014742 | 1.1871e-06 | 1.3614e-07 | 0.0087919 | 0.0087918 | 0.0087919 | 0.99609 | -0.027359 | 0.9963 | -0.0259 | 3.2563
93 | 0.016818 | 0.0042202 | -0.016812 | -0.004218 | 6.4941e-06 | 2.2873e-06 | 0.025247 | 0.025247 | 0.025247 | 0.99131 | -0.060904 | 0.99092 | -0.063687 | 9.3507
94 | -0.018147 | -0.0045533 | 0.018166 | 0.0045601 | 1.9049e-05 | 6.7957e-06 | 0.027241 | 0.027241 | 0.027241 | 0.99131 | -0.060904 | 0.99239 | -0.053346 | 10.0893
95 | 0.016596 | 0.0041639 | -0.016595 | -0.0041637 | 7.6926e-07 | 2.703e-07 | 0.024923 | 0.024923 | 0.024923 | 0.99092 | -0.063687 | 0.99087 | -0.064022 | 9.2308
96 | -0.019014 | -0.0047725 | 0.019026 | 0.004777 | 1.2417e-05 | 4.4594e-06 | 0.028512 | 0.028512 | 0.028512 | 0.99239 | -0.053346 | 0.99306 | -0.048646 | 10.56
97 | 0.00029824 | 7.4587e-05 | -0.00029824 | -7.4745e-05 | 1.5385e-09 | -1.5775e-07 | 0.00044782 | 0.00044787 | 0.00044787 | 0.99087 | -0.064022 | 0.99087 | -0.064059 | 0.16588
98 | 0.016297 | 0.0040891 | -0.01629 | -0.0040867 | 6.8001e-06 | 2.3812e-06 | 0.024475 | 0.024475 | 0.024475 | 0.99087 | -0.064022 | 0.99044 | -0.06703 | 9.065
99 | -0.029184 | -0.0073153 | 0.02919 | 0.0073176 | 6.3655e-06 | 2.3792e-06 | 0.04373 | 0.04373 | 0.04373 | 0.99306 | -0.048646 | 0.99328 | -0.047071 | 16.1962
100 | 0.010158 | 0.0025383 | -0.010152 | -0.0025367 | 5.2784e-06 | 1.5578e-06 | 0.015218 | 0.015218 | 0.015218 | 0.99306 | -0.048646 | 0.99252 | -0.052423 | 5.6362
101 | 0.015877 | 0.003983 | -0.015861 | -0.0039776 | 1.5434e-05 | 5.3772e-06 | 0.023854 | 0.023854 | 0.023854 | 0.99044 | -0.06703 | 0.98945 | -0.074044 | 8.8348
102 | 0.0087822 | 0.0021934 | -0.0087817 | -0.0021932 | 4.5102e-07 | 1.1956e-07 | 0.013164 | 0.013164 | 0.013164 | 0.99252 | -0.052423 | 0.99247 | -0.052796 | 4.8755
103 | 0.0084899 | 0.0021201 | -0.0084882 | -0.0021197 | 1.7042e-06 | 4.3759e-07 | 0.012726 | 0.012726 | 0.012726 | 0.99247 | -0.052796 | 0.99226 | -0.054257 | 4.7135
104 | 0.00056099 | 0.00014018 | -0.00056097 | -0.00014059 | 1.4432e-08 | -4.1665e-07 | 0.00084112 | 0.00084127 | 0.00084127 | 0.99226 | -0.054257 | 0.99224 | -0.054443 | 0.31158
105 | 0.0079272 | 0.0019795 | -0.0079265 | -0.0019793 | 6.5749e-07 | 1.5654e-07 | 0.011885 | 0.011885 | 0.011885 | 0.99226 | -0.054257 | 0.99218 | -0.05486 | 4.4019
106 | 0.0076029 | 0.0018982 | -0.0076026 | -0.0018982 | 2.4897e-07 | 5.6108e-08 | 0.0114 | 0.0114 | 0.0114 | 0.99218 | -0.05486 | 0.99215 | -0.055099 | 4.2222
107 | 0.00713 | 0.0017797 | -0.007129 | -0.0017795 | 9.3407e-07 | 1.9015e-07 | 0.010691 | 0.010691 | 0.010691 | 0.99215 | -0.055099 | 0.99201 | -0.056053 | 3.9596
108 | -0.0069481 | -0.0017342 | 0.0069492 | 0.0017344 | 1.1683e-06 | 2.2682e-07 | 0.010421 | 0.010421 | 0.010421 | 0.99184 | -0.057277 | 0.99201 | -0.056053 | 3.8598
109 | 0.0059768 | 0.0014908 | -0.0059758 | -0.0014907 | 1.01e-06 | 1.2855e-07 | 0.0089642 | 0.0089643 | 0.0089643 | 0.99184 | -0.057277 | 0.99167 | -0.058509 | 3.3201
110 | 0.0056668 | 0.0014132 | -0.0056648 | -0.001413 | 1.9715e-06 | 1.9439e-07 | 0.0085006 | 0.0085008 | 0.0085008 | 0.99167 | -0.058509 | 0.99131 | -0.061047 | 3.1485
111 | 0.0042828 | 0.0010667 | -0.0042822 | -0.0010667 | 5.8913e-07 | -6.8097e-08 | 0.0064264 | 0.0064265 | 0.0064265 | 0.99131 | -0.061047 | 0.99117 | -0.062053 | 2.3802
112 | 0.0042822 | 0.0010667 | -0.0042807 | -0.0010669 | 1.5237e-06 | -1.7569e-07 | 0.0064265 | 0.0064267 | 0.0064267 | 0.99117 | -0.062053 | 0.99081 | -0.064653 | 2.3803
113 | 0.0042807 | 0.0010669 | -0.0042791 | -0.0010671 | 1.5841e-06 | -1.8199e-07 | 0.0064267 | 0.006427 | 0.006427 | 0.99081 | -0.064653 | 0.99043 | -0.067354 | 2.3804
114 | -0.0023366 | -0.00058562 | 0.0023368 | 0.00058546 | 1.1925e-07 | -1.6065e-07 | 0.0034806 | 0.0034806 | 0.0034806 | 0.99894 | -0.0074582 | 0.99899 | -0.0070894 | 1.2891
115 | 0.0017245 | 0.00042685 | -0.0017244 | -0.00042716 | 1.1416e-07 | -3.073e-07 | 0.002589 | 0.0025891 | 0.0025891 | 0.99043 | -0.067354 | 0.99036 | -0.067844 | 0.95894
116 | 0.0047385 | 0.0011862 | -0.0047373 | -0.0011862 | 1.1906e-06 | 1.0886e-08 | 0.007263 | 0.0072632 | 0.0072632 | 0.97074 | -0.20834 | 0.97049 | -0.21016 | 2.6901
117 | 0.0047373 | 0.0011862 | -0.0047364 | -0.0011862 | 9.212e-07 | 8.5953e-09 | 0.0072632 | 0.0072633 | 0.0072633 | 0.97049 | -0.21016 | 0.9703 | -0.21157 | 2.6901
118 | 0.0042857 | 0.0010737 | -0.0042853 | -0.0010737 | 4.4852e-07 | -3.3e-08 | 0.0065723 | 0.0065724 | 0.0065724 | 0.9703 | -0.21157 | 0.97019 | -0.21233 | 2.4342
119 | 0.00045068 | 0.0001125 | -0.00045068 | -0.00011274 | 5.8123e-09 | -2.3869e-07 | 0.00069099 | 0.00069108 | 0.00069108 | 0.9703 | -0.21157 | 0.97028 | -0.21166 | 0.25595
120 | -0.00030058 | -7.5332e-05 | 0.00030058 | 7.5275e-05 | 6.1318e-10 | -5.6883e-08 | 0.00046097 | 0.00046095 | 0.00046097 | 0.97027 | -0.21174 | 0.97028 | -0.21172 | 0.17073
121 | -0.00045067 | -0.00011289 | 0.00045068 | 0.00011274 | 3.7932e-09 | -1.5573e-07 | 0.00069113 | 0.00069108 | 0.00069113 | 0.97028 | -0.21172 | 0.97028 | -0.21166 | 0.25598
122 | 0.0010555 | 0.00026424 | -0.0010555 | -0.00026452 | 3.9154e-08 | -2.8062e-07 | 0.0016187 | 0.0016188 | 0.0016188 | 0.97019 | -0.21233 | 0.97015 | -0.21259 | 0.59957

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.080071 | 0.019916

## res_load
| p_mw | q_mvar
0 | 0.00044722 | 0.00011208
1 | 0.0009687 | 0.00024278
2 | 0.00020286 | 5.0841e-05
3 | 0.00021352 | 5.3513e-05
4 | 0.00078056 | 0.00019563
5 | 0.00069639 | 0.00017453
6 | 0.00053286 | 0.00013355
7 | 0.00055029 | 0.00013792
8 | 0.0005325 | 0.00013346
9 | 0.00074266 | 0.00018613
10 | 9.076e-05 | 2.2747e-05
11 | 0.00051236 | 0.00012841
12 | 0.0001215 | 3.0451e-05
13 | 0.00055726 | 0.00013966
14 | 6.9444e-05 | 1.7404e-05
15 | 0.00033197 | 8.3198e-05
16 | 0.00023332 | 5.8476e-05
17 | 0.00033893 | 8.4944e-05
18 | 0.0016567 | 0.00041521
19 | 0.00025895 | 6.49e-05
20 | 0.00012908 | 3.2352e-05
21 | 0.0012199 | 0.00030574
22 | 0.0016161 | 0.00040504
23 | 0.00032292 | 8.0931e-05
24 | 0.00038469 | 9.6414e-05
25 | 0.00077624 | 0.00019455
26 | 0.0004009 | 0.00010047
27 | 0.0019709 | 0.00049396
28 | 0.0010987 | 0.00027537
29 | 0.00039029 | 9.7816e-05
30 | 0.00027829 | 6.9747e-05
31 | 0.00069326 | 0.00017375
32 | 0.00032369 | 8.1124e-05
33 | 0.00052961 | 0.00013273
34 | 0.0020808 | 0.00052149
35 | 0.00079404 | 0.00019901
36 | 0.00049489 | 0.00012403
37 | 0.00032917 | 8.2499e-05
38 | 0.00027092 | 6.7898e-05
39 | 0.00033633 | 8.4291e-05
40 | 0.00083549 | 0.00020939
41 | 0.00063981 | 0.00016035
42 | 0.00041949 | 0.00010513
43 | 0.001731 | 0.00043383
44 | 0.0025979 | 0.0006511
45 | 0.002998 | 0.00075136
46 | 0.0028319 | 0.00070974
47 | 0.0003089 | 7.7418e-05
48 | 0.00039793 | 9.9731e-05
49 | 0.00068262 | 0.00017108
50 | 0.00071199 | 0.00017844
51 | 0.0036997 | 0.00092723
52 | 0.0014516 | 0.00036381
53 | 0.0044338 | 0.0011112
54 | 0.0012724 | 0.0003189
55 | 0.0013287 | 0.00033301
56 | 0.00021556 | 5.4024e-05
57 | 0.00084768 | 0.00021245
58 | 0.00029824 | 7.4745e-05
59 | 0.00041374 | 0.00010369
60 | 0.00018536 | 4.6455e-05
61 | 0.0013701 | 0.00034338
62 | 0.00083627 | 0.00020959
63 | 0.00029182 | 7.3137e-05
64 | 0.00056097 | 0.00014059
65 | 0.00032366 | 8.1116e-05
66 | 0.00047268 | 0.00011846
67 | 0.00097127 | 0.00024342
68 | 0.00017979 | 4.5059e-05
69 | 0.00030901 | 7.7446e-05
70 | 0.001382 | 0.00034637
71 | 0.0023366 | 0.00058562
72 | 0.002042 | 0.00051176
73 | 0.0025546 | 0.00064024
74 | 0.0012771 | 0.00032006
75 | 0.0023388 | 0.00058616
76 | 0.0020269 | 0.000508
77 | 0.00069326 | 0.00017375
78 | 0.00093238 | 0.00023368
79 | 0.00014493 | 3.6324e-05
80 | 0.00030058 | 7.5332e-05
81 | 0.00015009 | 3.7617e-05
82 | 0.0032298 | 0.00080946
83 | 0.0010555 | 0.00026452

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1