## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2306-42_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2306-42_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2306-42_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2306-42_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2306-42_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2306-42_0_3_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_2306-42_0_3_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_2306-42_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2306-42_0_3_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_2306-42_0_3_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_2306-42_0_3_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_2306-42_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2306-42_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2306-42_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2306-42_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2306-42_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2306-42_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2306-42_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2306-42_0_3_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_2306-42_0_3_node_58 | 0.4 | n |  | TRUE
20 | bus_LV_2306-42_0_3_node_36 | 0.4 | n |  | TRUE
21 | bus_LV_2306-42_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2306-42_0_3_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_2306-42_0_3_node_126 | 0.4 | n |  | TRUE
24 | bus_LV_2306-42_0_3_node_46 | 0.4 | n |  | TRUE
25 | bus_LV_2306-42_0_3_node_49 | 0.4 | n |  | TRUE
26 | bus_LV_2306-42_0_3_node_43 | 0.4 | n |  | TRUE
27 | bus_LV_2306-42_0_3_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_2306-42_0_3_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_2306-42_0_3_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_2306-42_0_3_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_2306-42_0_3_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_2306-42_0_3_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_2306-42_0_3_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_2306-42_0_3_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2306-42_0_3_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_2306-42_0_3_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_2306-42_0_3_node_93 | 0.4 | n |  | TRUE
38 | bus_LV_2306-42_0_3_node_100 | 0.4 | n |  | TRUE
39 | bus_LV_2306-42_0_3_node_74 | 0.4 | n |  | TRUE
40 | bus_LV_2306-42_0_3_node_125 | 0.4 | n |  | TRUE
41 | bus_LV_2306-42_0_3_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_2306-42_0_3_node_127 | 0.4 | n |  | TRUE
43 | bus_LV_2306-42_0_3_node_21 | 0.4 | n |  | TRUE
44 | bus_LV_2306-42_0_3_node_101 | 0.4 | n |  | TRUE
45 | bus_LV_2306-42_0_3_node_99 | 0.4 | n |  | TRUE
46 | bus_LV_2306-42_0_3_node_104 | 0.4 | n |  | TRUE
47 | bus_LV_2306-42_0_3_node_117 | 0.4 | n |  | TRUE
48 | bus_LV_2306-42_0_3_node_23 | 0.4 | n |  | TRUE
49 | bus_LV_2306-42_0_3_node_48 | 0.4 | n |  | TRUE
50 | bus_LV_2306-42_0_3_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_2306-42_0_3_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_2306-42_0_3_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_2306-42_0_3_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_2306-42_0_3_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_2306-42_0_3_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_2306-42_0_3_node_57 | 0.4 | n |  | TRUE
57 | bus_LV_2306-42_0_3_node_56 | 0.4 | n |  | TRUE
58 | bus_LV_2306-42_0_3_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_2306-42_0_3_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_2306-42_0_3_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_2306-42_0_3_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_2306-42_0_3_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_2306-42_0_3_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_2306-42_0_3_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_2306-42_0_3_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_2306-42_0_3_node_61 | 0.4 | n |  | TRUE
67 | bus_LV_2306-42_0_3_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_2306-42_0_3_node_63 | 0.4 | n |  | TRUE
69 | bus_LV_2306-42_0_3_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_2306-42_0_3_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_2306-42_0_3_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_2306-42_0_3_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_2306-42_0_3_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_2306-42_0_3_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_2306-42_0_3_node_80 | 0.4 | n |  | TRUE
76 | bus_LV_2306-42_0_3_node_78 | 0.4 | n |  | TRUE
77 | bus_LV_2306-42_0_3_node_69 | 0.4 | n |  | TRUE
78 | bus_LV_2306-42_0_3_node_85 | 0.4 | n |  | TRUE
79 | bus_LV_2306-42_0_3_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_2306-42_0_3_node_82 | 0.4 | n |  | TRUE
81 | bus_LV_2306-42_0_3_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_2306-42_0_3_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_2306-42_0_3_node_72 | 0.4 | n |  | TRUE
84 | bus_LV_2306-42_0_3_node_73 | 0.4 | n |  | TRUE
85 | bus_LV_2306-42_0_3_node_83 | 0.4 | n |  | TRUE
86 | bus_LV_2306-42_0_3_node_89 | 0.4 | n |  | TRUE
87 | bus_LV_2306-42_0_3_node_84 | 0.4 | n |  | TRUE
88 | bus_LV_2306-42_0_3_node_90 | 0.4 | n |  | TRUE
89 | bus_LV_2306-42_0_3_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_2306-42_0_3_node_102 | 0.4 | n |  | TRUE
91 | bus_LV_2306-42_0_3_node_116 | 0.4 | n |  | TRUE
92 | bus_LV_2306-42_0_3_node_118 | 0.4 | n |  | TRUE
93 | bus_LV_2306-42_0_3_node_119 | 0.4 | n |  | TRUE
94 | bus_LV_2306-42_0_3_node_107 | 0.4 | n |  | TRUE
95 | bus_LV_2306-42_0_3_node_108 | 0.4 | n |  | TRUE
96 | bus_LV_2306-42_0_3_node_109 | 0.4 | n |  | TRUE
97 | bus_LV_2306-42_0_3_node_110 | 0.4 | n |  | TRUE
98 | bus_LV_2306-42_0_3_node_111 | 0.4 | n |  | TRUE
99 | bus_LV_2306-42_0_3_node_112 | 0.4 | n |  | TRUE
100 | bus_LV_2306-42_0_3_node_122 | 0.4 | n |  | TRUE
101 | bus_LV_2306-42_0_3_node_114 | 0.4 | n |  | TRUE
102 | bus_LV_2306-42_0_3_node_115 | 0.4 | n |  | TRUE
103 | bus_LV_2306-42_0_3_node_86 | 0.4 | n |  | TRUE
104 | bus_LV_2306-42_0_3_node_87 | 0.4 | n |  | TRUE
105 | bus_LV_2306-42_0_3_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_2306-42_0_3_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_2306-42_0_3_node_88 | 0.4 | n |  | TRUE
108 | bus_LV_2306-42_0_3_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_2306-42_0_3_node_95 | 0.4 | n |  | TRUE
110 | bus_LV_2306-42_0_3_node_96 | 0.4 | n |  | TRUE
111 | bus_LV_2306-42_0_3_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_2306-42_0_3_node_103 | 0.4 | n |  | TRUE
113 | bus_LV_2306-42_0_3_node_105 | 0.4 | n |  | TRUE
114 | bus_LV_2306-42_0_3_node_106 | 0.4 | n |  | TRUE
115 | bus_LV_2306-42_0_3_node_98 | 0.4 | n |  | TRUE
116 | bus_LV_2306-42_0_3_node_124 | 0.4 | n |  | TRUE
117 | bus_LV_2306-42_0_3_node_123 | 0.4 | n |  | TRUE
118 | bus_LV_2306-42_0_3_node_121 | 0.4 | n |  | TRUE
119 | bus_MV_0_node_127 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2306-42_0_3_load_0 | 0 | 0.0020095 | 0.00050363 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2306-42_0_3_load_1 | 1 | 0.0018886 | 0.00047333 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2306-42_0_3_load_3 | 3 | 0.0019923 | 0.00049932 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2306-42_0_3_load_40 | 5 | 0.00014596 | 3.6581e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2306-42_0_3_load_6 | 7 | 0.00031798 | 7.9694e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2306-42_0_3_load_22 | 10 | 0.0019435 | 0.00048708 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2306-42_0_3_load_7 | 11 | 0.00028487 | 7.1394e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2306-42_0_3_load_9 | 12 | 0.00034428 | 8.6285e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2306-42_0_3_load_10 | 13 | 0.00037254 | 9.3368e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2306-42_0_3_load_11 | 14 | 0.00027905 | 6.9935e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2306-42_0_3_load_14 | 17 | 0.001965 | 0.00049247 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2306-42_0_3_load_58 | 19 | 0.00045908 | 0.00011506 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2306-42_0_3_load_15 | 21 | 0.00034434 | 8.63e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2306-42_0_3_load_126 | 23 | 0.00017938 | 4.4956e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2306-42_0_3_load_49 | 25 | 0.00048135 | 0.00012064 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2306-42_0_3_load_38 | 28 | 0.00021922 | 5.4943e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2306-42_0_3_load_34 | 29 | 0.0018681 | 0.00046819 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2306-42_0_3_load_27 | 30 | 0.00053081 | 0.00013303 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2306-42_0_3_load_16 | 31 | 0.00047675 | 0.00011949 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2306-42_0_3_load_100 | 38 | 0.00028504 | 7.1438e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2306-42_0_3_load_74 | 39 | 0.0017734 | 0.00044445 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2306-42_0_3_load_125 | 40 | 0.0019114 | 0.00047905 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2306-42_0_3_load_35 | 41 | 0.00076153 | 0.00019086 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2306-42_0_3_load_127 | 42 | 0.00030166 | 7.5602e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2306-42_0_3_load_99 | 45 | 0.0009379 | 0.00023506 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2306-42_0_3_load_104 | 46 | 0.00024957 | 6.2548e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2306-42_0_3_load_23 | 48 | 0.00078083 | 0.0001957 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2306-42_0_3_load_48 | 49 | 0.00027976 | 7.0115e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2306-42_0_3_load_44 | 50 | 0.00068627 | 0.000172 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2306-42_0_3_load_30 | 52 | 0.00049697 | 0.00012455 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2306-42_0_3_load_31 | 53 | 0.00184 | 0.00046114 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2306-42_0_3_load_32 | 54 | 0.00021899 | 5.4884e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2306-42_0_3_load_33 | 55 | 0.00018406 | 4.6129e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2306-42_0_3_load_57 | 56 | 0.0003763 | 9.4309e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2306-42_0_3_load_56 | 57 | 0.0011769 | 0.00029497 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2306-42_0_3_load_41 | 58 | 0.00013058 | 3.2726e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2306-42_0_3_load_42 | 59 | 0.00015018 | 3.764e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2306-42_0_3_load_55 | 61 | 0.00074903 | 0.00018773 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2306-42_0_3_load_53 | 62 | 0.00064129 | 0.00016072 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2306-42_0_3_load_54 | 63 | 0.00098793 | 0.0002476 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2306-42_0_3_load_61 | 66 | 0.00037537 | 9.4077e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2306-42_0_3_load_60 | 67 | 0.0013236 | 0.00033172 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2306-42_0_3_load_62 | 69 | 0.00088166 | 0.00022096 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2306-42_0_3_load_64 | 70 | 0.00034295 | 8.5951e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2306-42_0_3_load_67 | 73 | 0.00147 | 0.00036841 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2306-42_0_3_load_68 | 74 | 0.0021203 | 0.0005314 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2306-42_0_3_load_78 | 76 | 0.00047559 | 0.00011919 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2306-42_0_3_load_69 | 77 | 0.00014043 | 3.5194e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2306-42_0_3_load_82 | 80 | 7.3679e-05 | 1.8466e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2306-42_0_3_load_70 | 81 | 0.0008951 | 0.00022433 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2306-42_0_3_load_72 | 83 | 7.205e-05 | 1.8057e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2306-42_0_3_load_73 | 84 | 0.00069886 | 0.00017515 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2306-42_0_3_load_83 | 85 | 0.00028109 | 7.0448e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2306-42_0_3_load_89 | 86 | 0.00028984 | 7.2641e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2306-42_0_3_load_90 | 88 | 0.00060259 | 0.00015102 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2306-42_0_3_load_76 | 89 | 0.00033342 | 8.3564e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2306-42_0_3_load_102 | 90 | 0.0012655 | 0.00031716 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2306-42_0_3_load_118 | 92 | 0.00061153 | 0.00015326 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2306-42_0_3_load_119 | 93 | 0.00026832 | 6.7248e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2306-42_0_3_load_107 | 94 | 0.0005901 | 0.00014789 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2306-42_0_3_load_108 | 95 | 0.0014306 | 0.00035853 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2306-42_0_3_load_110 | 97 | 0.00074454 | 0.0001866 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2306-42_0_3_load_111 | 98 | 0.0005025 | 0.00012594 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2306-42_0_3_load_112 | 99 | 0.00072003 | 0.00018046 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2306-42_0_3_load_122 | 100 | 0.00067955 | 0.00017031 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2306-42_0_3_load_114 | 101 | 0.0019908 | 0.00049895 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2306-42_0_3_load_115 | 102 | 0.00027031 | 6.7747e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2306-42_0_3_load_86 | 103 | 0.00014935 | 3.7431e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2306-42_0_3_load_87 | 104 | 0.00034809 | 8.724e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2306-42_0_3_load_91 | 105 | 8.4676e-05 | 2.1222e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2306-42_0_3_load_88 | 107 | 0.00059488 | 0.00014909 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2306-42_0_3_load_94 | 108 | 0.00060456 | 0.00015152 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2306-42_0_3_load_95 | 109 | 0.00020706 | 5.1895e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2306-42_0_3_load_105 | 113 | 0.00028633 | 7.1761e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2306-42_0_3_load_106 | 114 | 0.0018837 | 0.0004721 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2306-42_0_3_load_98 | 115 | 0.00015298 | 3.834e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2306-42_0_3_load_124 | 116 | 0.00028582 | 7.1633e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2306-42_0_3_load_123 | 117 | 0.00030691 | 7.6919e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2306-42_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.087094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2306-42_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0081341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2306-42_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0014651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2306-42_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.011826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2306-42_0_3_line_4 | NAYY 4x150 SE | 3 | 7 | 0.018496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2306-42_0_3_line_5 | NAYY 4x150 SE | 4 | 11 | 0.0062313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2306-42_0_3_line_6 | NAYY 4x150 SE | 4 | 5 | 0.40305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2306-42_0_3_line_7 | NAYY 4x150 SE | 5 | 6 | 0.019286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2306-42_0_3_line_8 | NAYY 4x150 SE | 6 | 48 | 0.014139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2306-42_0_3_line_9 | NAYY 4x150 SE | 7 | 12 | 0.0098323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2306-42_0_3_line_10 | NAYY 4x150 SE | 8 | 9 | 0.03902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2306-42_0_3_line_11 | NAYY 4x150 SE | 8 | 10 | 0.030875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2306-42_0_3_line_12 | NAYY 4x150 SE | 9 | 49 | 0.051293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2306-42_0_3_line_13 | NAYY 4x150 SE | 10 | 48 | 0.0084212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2306-42_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.15028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_2306-42_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.008841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_2306-42_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.048053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_2306-42_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.092553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_2306-42_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.082861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_2306-42_0_3_line_19 | NAYY 4x150 SE | 16 | 19 | 0.037459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2306-42_0_3_line_20 | NAYY 4x150 SE | 17 | 20 | 0.023809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_2306-42_0_3_line_21 | NAYY 4x150 SE | 18 | 23 | 0.096207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2306-42_0_3_line_22 | NAYY 4x150 SE | 18 | 24 | 0.10875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_2306-42_0_3_line_23 | NAYY 4x150 SE | 20 | 27 | 0.020109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2306-42_0_3_line_24 | NAYY 4x150 SE | 20 | 28 | 0.04609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2306-42_0_3_line_25 | NAYY 4x150 SE | 20 | 29 | 0.0075655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_2306-42_0_3_line_26 | NAYY 4x150 SE | 21 | 22 | 0.020874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2306-42_0_3_line_27 | NAYY 4x150 SE | 22 | 30 | 0.025052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2306-42_0_3_line_28 | NAYY 4x150 SE | 24 | 25 | 0.39662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2306-42_0_3_line_29 | NAYY 4x150 SE | 24 | 26 | 0.20735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_2306-42_0_3_line_30 | NAYY 4x150 SE | 26 | 60 | 0.14358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2306-42_0_3_line_31 | NAYY 4x150 SE | 26 | 58 | 0.056414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2306-42_0_3_line_32 | NAYY 4x150 SE | 27 | 56 | 0.031021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2306-42_0_3_line_33 | NAYY 4x150 SE | 27 | 57 | 0.017324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2306-42_0_3_line_34 | NAYY 4x150 SE | 28 | 52 | 0.0046216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2306-42_0_3_line_35 | NAYY 4x150 SE | 29 | 54 | 0.032108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_2306-42_0_3_line_36 | NAYY 4x150 SE | 30 | 51 | 0.0062799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2306-42_0_3_line_37 | NAYY 4x150 SE | 31 | 32 | 0.16807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_2306-42_0_3_line_38 | NAYY 4x150 SE | 31 | 33 | 0.012248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_2306-42_0_3_line_39 | NAYY 4x150 SE | 32 | 34 | 0.14583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2306-42_0_3_line_40 | NAYY 4x150 SE | 32 | 35 | 0.56353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_2306-42_0_3_line_41 | NAYY 4x150 SE | 33 | 36 | 0.014918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_2306-42_0_3_line_42 | NAYY 4x150 SE | 34 | 40 | 0.034147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2306-42_0_3_line_43 | NAYY 4x150 SE | 35 | 41 | 0.017266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_2306-42_0_3_line_44 | NAYY 4x150 SE | 36 | 42 | 0.014418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_2306-42_0_3_line_45 | NAYY 4x150 SE | 36 | 43 | 0.048427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2306-42_0_3_line_46 | NAYY 4x150 SE | 37 | 38 | 0.27088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2306-42_0_3_line_47 | NAYY 4x150 SE | 37 | 39 | 0.060969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2306-42_0_3_line_48 | NAYY 4x150 SE | 38 | 45 | 0.051891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2306-42_0_3_line_49 | NAYY 4x150 SE | 39 | 82 | 0.016738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2306-42_0_3_line_50 | NAYY 4x150 SE | 41 | 55 | 0.07701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_2306-42_0_3_line_51 | NAYY 4x150 SE | 43 | 44 | 0.32009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2306-42_0_3_line_52 | NAYY 4x150 SE | 43 | 45 | 0.1745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2306-42_0_3_line_53 | NAYY 4x150 SE | 44 | 46 | 0.064351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2306-42_0_3_line_54 | NAYY 4x150 SE | 44 | 47 | 0.29647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2306-42_0_3_line_55 | NAYY 4x150 SE | 46 | 113 | 0.0070805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2306-42_0_3_line_56 | NAYY 4x150 SE | 47 | 91 | 0.1141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2306-42_0_3_line_57 | NAYY 4x150 SE | 49 | 50 | 0.011924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2306-42_0_3_line_58 | NAYY 4x150 SE | 50 | 59 | 0.031418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2306-42_0_3_line_59 | NAYY 4x150 SE | 51 | 52 | 0.10908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2306-42_0_3_line_60 | NAYY 4x150 SE | 53 | 54 | 0.0086756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_2306-42_0_3_line_61 | NAYY 4x150 SE | 53 | 55 | 0.020132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_2306-42_0_3_line_62 | NAYY 4x150 SE | 58 | 59 | 0.0048192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2306-42_0_3_line_63 | NAYY 4x150 SE | 60 | 61 | 0.048409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2306-42_0_3_line_64 | NAYY 4x150 SE | 60 | 62 | 0.0027672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2306-42_0_3_line_65 | NAYY 4x150 SE | 62 | 63 | 0.024516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2306-42_0_3_line_66 | NAYY 4x150 SE | 63 | 64 | 0.019927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2306-42_0_3_line_67 | NAYY 4x150 SE | 64 | 65 | 0.11385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2306-42_0_3_line_68 | NAYY 4x150 SE | 65 | 66 | 0.042134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2306-42_0_3_line_69 | NAYY 4x150 SE | 65 | 67 | 0.14799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2306-42_0_3_line_70 | NAYY 4x150 SE | 66 | 68 | 0.0095102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2306-42_0_3_line_71 | NAYY 4x150 SE | 68 | 69 | 0.0046518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2306-42_0_3_line_72 | NAYY 4x150 SE | 70 | 71 | 0.029066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2306-42_0_3_line_73 | NAYY 4x150 SE | 70 | 72 | 0.043846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2306-42_0_3_line_74 | NAYY 4x150 SE | 71 | 73 | 0.040126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2306-42_0_3_line_75 | NAYY 4x150 SE | 72 | 74 | 0.026807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2306-42_0_3_line_76 | NAYY 4x150 SE | 73 | 75 | 0.033183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2306-42_0_3_line_77 | NAYY 4x150 SE | 74 | 76 | 0.0010824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2306-42_0_3_line_78 | NAYY 4x150 SE | 75 | 79 | 0.033801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2306-42_0_3_line_79 | NAYY 4x150 SE | 75 | 80 | 0.0064664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2306-42_0_3_line_80 | NAYY 4x150 SE | 77 | 78 | 0.020465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2306-42_0_3_line_81 | NAYY 4x150 SE | 78 | 79 | 0.005597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2306-42_0_3_line_82 | NAYY 4x150 SE | 79 | 103 | 0.023458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2306-42_0_3_line_83 | NAYY 4x150 SE | 81 | 82 | 0.033255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2306-42_0_3_line_84 | NAYY 4x150 SE | 82 | 83 | 0.16163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2306-42_0_3_line_85 | NAYY 4x150 SE | 82 | 84 | 0.020499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2306-42_0_3_line_86 | NAYY 4x150 SE | 83 | 85 | 0.024481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2306-42_0_3_line_87 | NAYY 4x150 SE | 84 | 86 | 0.044972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2306-42_0_3_line_88 | NAYY 4x150 SE | 85 | 87 | 0.014802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2306-42_0_3_line_89 | NAYY 4x150 SE | 86 | 88 | 0.32162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2306-42_0_3_line_90 | NAYY 4x150 SE | 87 | 105 | 0.010979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2306-42_0_3_line_91 | NAYY 4x150 SE | 88 | 90 | 0.30739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2306-42_0_3_line_92 | NAYY 4x150 SE | 88 | 89 | 0.18953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2306-42_0_3_line_93 | NAYY 4x150 SE | 90 | 112 | 0.026757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2306-42_0_3_line_94 | NAYY 4x150 SE | 91 | 99 | 0.041447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2306-42_0_3_line_95 | NAYY 4x150 SE | 91 | 101 | 0.11681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2306-42_0_3_line_96 | NAYY 4x150 SE | 92 | 93 | 0.010514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2306-42_0_3_line_97 | NAYY 4x150 SE | 93 | 118 | 0.011579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2306-42_0_3_line_98 | NAYY 4x150 SE | 94 | 95 | 0.0035893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2306-42_0_3_line_99 | NAYY 4x150 SE | 94 | 96 | 0.022045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2306-42_0_3_line_100 | NAYY 4x150 SE | 95 | 97 | 0.026214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2306-42_0_3_line_101 | NAYY 4x150 SE | 96 | 98 | 0.025233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2306-42_0_3_line_102 | NAYY 4x150 SE | 96 | 99 | 0.031532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2306-42_0_3_line_103 | NAYY 4x150 SE | 98 | 100 | 0.02166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2306-42_0_3_line_104 | NAYY 4x150 SE | 101 | 102 | 0.014867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2306-42_0_3_line_105 | NAYY 4x150 SE | 103 | 104 | 0.0043887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2306-42_0_3_line_106 | NAYY 4x150 SE | 104 | 107 | 0.029753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2306-42_0_3_line_107 | NAYY 4x150 SE | 105 | 106 | 0.023132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2306-42_0_3_line_108 | NAYY 4x150 SE | 106 | 107 | 0.0095694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2306-42_0_3_line_109 | NAYY 4x150 SE | 108 | 109 | 0.027246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2306-42_0_3_line_110 | NAYY 4x150 SE | 108 | 110 | 0.104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2306-42_0_3_line_111 | NAYY 4x150 SE | 109 | 111 | 0.017573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2306-42_0_3_line_112 | NAYY 4x150 SE | 110 | 115 | 0.19466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2306-42_0_3_line_113 | NAYY 4x150 SE | 110 | 116 | 0.40208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2306-42_0_3_line_114 | NAYY 4x150 SE | 111 | 112 | 0.04739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2306-42_0_3_line_115 | NAYY 4x150 SE | 113 | 114 | 0.018161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2306-42_0_3_line_116 | NAYY 4x150 SE | 116 | 117 | 0.015852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2306-42_0_3_line_117 | NAYY 4x150 SE | 117 | 118 | 0.008497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2306-42_0_3_trafo_127 | 0.25 MVA 20/0.4 kV | 119 | 42 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2588308.4753 | 1185078.863 | 2588303.535 | 1185069.7903 | 2588297.8728 | 1185066.1662 | 2588281.6494 | 1185066.9207 | 2588267.6122 | 1185069.4942 | 2588252.6567 | 1185066.9779 | 2588236.2199 | 1185052.4696 | 2588234.8368 | 1185050.4612
1 | 2588316.4535 | 1185080.4482 | 2588308.4753 | 1185078.863
2 | 2588234.8368 | 1185050.4612 | 2588234.0058 | 1185049.2546
3 | 2588316.4535 | 1185080.4482 | 2588318.2928 | 1185092.1284
4 | 2588228.5457 | 1185032.4045 | 2588228.7193 | 1185041.5788 | 2588234.0058 | 1185049.2546
5 | 2588318.2928 | 1185092.1284 | 2588324.3093 | 1185093.7504
6 | 2588127.2823 | 1185447.038 | 2588318.2928 | 1185092.1284
7 | 2588108.4779 | 1185444.2042 | 2588117.4367 | 1185444.0751 | 2588123.2465 | 1185445.3308 | 2588127.2823 | 1185447.038
8 | 2588108.4779 | 1185444.2042 | 2588095.7815 | 1185437.9827
9 | 2588228.5457 | 1185032.4045 | 2588228.5233 | 1185031.2182 | 2588230.1283 | 1185022.7227
10 | 2588063.7781 | 1185415.6344 | 2588052.2001 | 1185452.8992
11 | 2588063.7781 | 1185415.6344 | 2588071.9365 | 1185423.5332 | 2588081.2445 | 1185430.118 | 2588088.2554 | 1185434.2101
12 | 2588052.2001 | 1185452.8992 | 2588048.3655 | 1185462.434 | 2588030.7025 | 1185499.4519
13 | 2588095.7815 | 1185437.9827 | 2588089.1597 | 1185434.7379 | 2588088.2554 | 1185434.2101
14 | 2588123.9402 | 1185809.4878 | 2588127.4949 | 1185811.1342 | 2588141.5084 | 1185816.7425 | 2588171.1662 | 1185826.8331 | 2588189.7033 | 1185831.7321 | 2588208.5129 | 1185835.5635 | 2588224.7423 | 1185838.8664 | 2588242.8708 | 1185841.6987 | 2588260.7672 | 1185842.9418 | 2588269.4887 | 1185842.7244
15 | 2588278.2696 | 1185841.6955 | 2588269.4887 | 1185842.7244 | 2588269.4887 | 1185842.7244
16 | 2588082.8328 | 1185784.7542 | 2588094.936 | 1185792.8008 | 2588114.7092 | 1185805.2122 | 2588123.9402 | 1185809.4878
17 | 2588278.2696 | 1185841.6955 | 2588283.1121 | 1185840.2185 | 2588287.8689 | 1185837.7634 | 2588294.2249 | 1185833.7044 | 2588303.6428 | 1185826.7934 | 2588310.0261 | 1185821.0779 | 2588315.4765 | 1185814.3859 | 2588319.4177 | 1185808.4862 | 2588325.9872 | 1185796.5671 | 2588329.4869 | 1185791.2353 | 2588333.2483 | 1185787.0813 | 2588338.2451 | 1185782.4914 | 2588343.3892 | 1185778.952
18 | 2588023.8067 | 1185726.8316 | 2588038.2416 | 1185740.7209 | 2588058.9065 | 1185763.8247 | 2588069.7864 | 1185774.4417 | 2588082.8328 | 1185784.7542
19 | 2588082.8328 | 1185784.7542 | 2588080.1069 | 1185799.156 | 2588081.1798 | 1185812.861 | 2588083.8341 | 1185821.5174
20 | 2588363.0041 | 1185765.4563 | 2588343.3892 | 1185778.952
21 | 2588023.8067 | 1185726.8316 | 2588050.1739 | 1185652.251 | 2588056.7582 | 1185636.4518
22 | 2587951.2256 | 1185747.3777 | 2587991.9903 | 1185736.4896 | 2588009.6944 | 1185736.7652 | 2588038.2416 | 1185740.7209 | 2588023.8067 | 1185726.8316
23 | 2588363.0041 | 1185765.4563 | 2588359.246 | 1185763.5182 | 2588355.1451 | 1185761.9142 | 2588351.9546 | 1185761.4869 | 2588347.9796 | 1185761.8394 | 2588343.8923 | 1185763.237
24 | 2588363.0041 | 1185765.4563 | 2588377.823 | 1185781.0243 | 2588381.2699 | 1185783.7856 | 2588384.3654 | 1185786.3698 | 2588387.7472 | 1185790.9878 | 2588391.836 | 1185798.1391 | 2588393.1322 | 1185799.899
25 | 2588363.0041 | 1185765.4563 | 2588370.203 | 1185763.1299 | 2588370.203 | 1185763.1299
26 | 2588419.817 | 1185903.4503 | 2588410.9663 | 1185903.8677 | 2588401.6837 | 1185901.9182 | 2588399.2566 | 1185901.2111
27 | 2588419.817 | 1185903.4503 | 2588431.6753 | 1185899.7364 | 2588444.0794 | 1185897.3811
28 | 2587951.2256 | 1185747.3777 | 2587654.8907 | 1186010.9895
29 | 2587941.3301 | 1185544.9705 | 2587936.3611 | 1185555.6306 | 2587933.0638 | 1185574.1135 | 2587937.081 | 1185590.8029 | 2587946.5577 | 1185616.6304 | 2587947.4714 | 1185630.7137 | 2587941.6571 | 1185668.6118 | 2587941.6384 | 1185689.4671 | 2587951.3725 | 1185740.7628 | 2587951.2256 | 1185747.3777
30 | 2587941.3301 | 1185544.9705 | 2587926.3839 | 1185550.2147 | 2587918.9048 | 1185553.6316 | 2587904.1382 | 1185560.8765 | 2587889.0126 | 1185567.9665 | 2587881.7537 | 1185570.8161 | 2587849.5112 | 1185581.3428 | 2587806.169 | 1185593.5045
31 | 2587941.3301 | 1185544.9705 | 2587964.6142 | 1185538.231 | 2587984.6239 | 1185531.2203 | 2587994.9637 | 1185527.5508
32 | 2588343.8923 | 1185763.237 | 2588330.6703 | 1185772.1231 | 2588319.0907 | 1185781.8842
33 | 2588343.8923 | 1185763.237 | 2588339.0681 | 1185754.6864 | 2588338.6964 | 1185747.189
34 | 2588393.1322 | 1185799.899 | 2588395.0494 | 1185802.5018 | 2588395.9988 | 1185803.5157
35 | 2588370.203 | 1185763.1299 | 2588398.1574 | 1185756.7609 | 2588401.3394 | 1185755.4622
36 | 2588450.249 | 1185896.2096 | 2588444.0794 | 1185897.3811
37 | 2588915.2434 | 1185306.9306 | 2588917.9376 | 1185290.7283 | 2588926.6706 | 1185267.6001 | 2588931.5428 | 1185253.0279 | 2588938.9526 | 1185187.2578 | 2588940.2548 | 1185169.3462 | 2588939.8196 | 1185148.6918 | 2588938.4371 | 1185142.0782
38 | 2588935.931 | 1185130.0894 | 2588938.4371 | 1185142.0782
39 | 2588915.2434 | 1185306.9306 | 2588944.4237 | 1185334.5906 | 2588976.2605 | 1185358.6662 | 2588991.9803 | 1185362.4502 | 2589017.8414 | 1185361.702 | 2589014.8981 | 1185338.2175
40 | 2588510.6079 | 1185699.1572 | 2588915.2434 | 1185306.9306
41 | 2588921.0766 | 1185128.305 | 2588935.931 | 1185130.0894
42 | 2588991.5559 | 1185314.5595 | 2588995.6539 | 1185322.8006 | 2589006.1501 | 1185328.6175 | 2589014.8981 | 1185338.2175
43 | 2588510.6079 | 1185699.1572 | 2588495.3708 | 1185707.2778
44 | 2588921.0766 | 1185128.305 | 2588906.8408 | 1185130.8329
45 | 2588921.0766 | 1185128.305 | 2588925.9219 | 1185119.7249 | 2588927.8477 | 1185108.8379 | 2588929.8707 | 1185105.0433 | 2588932.574 | 1185101.87 | 2588938.5159 | 1185083.7718
46 | 2589103.2809 | 1184637.0366 | 2588986.2889 | 1184881.345
47 | 2589103.2809 | 1184637.0366 | 2589104.5157 | 1184632.0317 | 2589104.9482 | 1184626.4503 | 2589104.6711 | 1184621.0035 | 2589102.9708 | 1184613.6362 | 2589100.4686 | 1184605.9145 | 2589095.1645 | 1184593.6401 | 2589088.3327 | 1184579.49
48 | 2588986.2889 | 1184881.345 | 2588974.9588 | 1184878.987 | 2588967.7435 | 1184881.4128 | 2588962.7629 | 1184887.1806 | 2588954.8963 | 1184904.5819 | 2588953.6123 | 1184910.4316
49 | 2589080.2821 | 1184564.8303 | 2589085.7103 | 1184574.0585 | 2589088.3327 | 1184579.49
50 | 2588427.4005 | 1185743.2138 | 2588429.522 | 1185742.1366 | 2588444.9014 | 1185732.046 | 2588456.2294 | 1185726.1542 | 2588485.0251 | 1185712.7915 | 2588495.3708 | 1185707.2778
51 | 2588938.5159 | 1185083.7718 | 2588942.1742 | 1185089.3345 | 2588945.2779 | 1185092.1858 | 2588950.4801 | 1185094.8775 | 2588960.7935 | 1185092.4682 | 2588975.3737 | 1185090.3512 | 2588995.4561 | 1185088.1462 | 2589008.0971 | 1185085.6548 | 2589021.972 | 1185081.8384 | 2589047.8673 | 1185074.1311 | 2589057.4037 | 1185072.4126 | 2589067.4083 | 1185072.1608 | 2589076.4079 | 1185073.1559 | 2589084.2496 | 1185075.3092 | 2589093.171 | 1185079.4617 | 2589111.6876 | 1185089.0327 | 2589129.3542 | 1185097.0267 | 2589147.2779 | 1185103.7197 | 2589169.4735 | 1185109.4822 | 2589233.6863 | 1185122.3278 | 2589239.6954 | 1185115.5912
52 | 2588938.5159 | 1185083.7718 | 2588942.8712 | 1184963.5014 | 2588950.8929 | 1184922.821 | 2588953.6123 | 1184910.4316
53 | 2589239.6954 | 1185115.5912 | 2589233.7096 | 1185101.4614 | 2589209.4933 | 1185067.2209 | 2589204.9401 | 1185061.8163
54 | 2589239.6954 | 1185115.5912 | 2589495.5474 | 1184965.8007
55 | 2589204.9401 | 1185061.8163 | 2589200.3781 | 1185056.4014
56 | 2589596.6517 | 1185017.0939 | 2589547.746 | 1184998.8591 | 2589535.1215 | 1184993.6231 | 2589525.5091 | 1184987.0366 | 2589513.5565 | 1184977.6528 | 2589502.4145 | 1184969.2459 | 2589495.5474 | 1184965.8007
57 | 2588025.5221 | 1185510.1916 | 2588026.3205 | 1185508.6356 | 2588030.7025 | 1185499.4519
58 | 2587999.5054 | 1185525.939 | 2588011.4966 | 1185521.6834 | 2588018.7087 | 1185518.2226 | 2588021.2765 | 1185516.2831 | 2588024.0477 | 1185513.0647 | 2588025.5221 | 1185510.1916
59 | 2588450.249 | 1185896.2096 | 2588445.0693 | 1185877.3098 | 2588437.6689 | 1185858.3811 | 2588425.1064 | 1185837.5614 | 2588411.5277 | 1185819.9676 | 2588399.1327 | 1185806.8627 | 2588395.9988 | 1185803.5157
60 | 2588409.3048 | 1185752.03 | 2588405.9575 | 1185753.5773 | 2588401.3394 | 1185755.4622
61 | 2588409.3048 | 1185752.03 | 2588417.4773 | 1185748.2521 | 2588427.4005 | 1185743.2138
62 | 2587994.9637 | 1185527.5508 | 2587999.5054 | 1185525.939
63 | 2587806.169 | 1185593.5045 | 2587809.7864 | 1185597.3768 | 2587812.3845 | 1185599.1391 | 2587831.7652 | 1185605.5583 | 2587851.0415 | 1185609.4988
64 | 2587806.169 | 1185593.5045 | 2587803.4272 | 1185593.8789
65 | 2587803.4272 | 1185593.8789 | 2587783.8546 | 1185596.5518 | 2587779.3481 | 1185598.0898
66 | 2587760.4896 | 1185604.5262 | 2587779.3481 | 1185598.0898
67 | 2587650.9866 | 1185572.269 | 2587746.1422 | 1185600.2646 | 2587760.4896 | 1185604.5262
68 | 2587650.9866 | 1185572.269 | 2587610.6615 | 1185560.0543
69 | 2587650.9866 | 1185572.269 | 2587656.7421 | 1185558.4054 | 2587672.8756 | 1185536.9831 | 2587677.6069 | 1185525.9898 | 2587676.2016 | 1185499.6235 | 2587680.936 | 1185475.3456 | 2587691.0896 | 1185451.5122 | 2587705.7509 | 1185442.6121
70 | 2587601.5597 | 1185557.2974 | 2587610.6615 | 1185560.0543
71 | 2587601.5597 | 1185557.2974 | 2587596.9415 | 1185556.7396
72 | 2588701.1103 | 1184477.2265 | 2588710.5642 | 1184459.7551 | 2588714.0973 | 1184455.335 | 2588717.1169 | 1184453.4825
73 | 2588756.4602 | 1184464.8708 | 2588745.1255 | 1184456.5435 | 2588738.4548 | 1184452.543 | 2588731.384 | 1184450.8666 | 2588723.5384 | 1184451.2039 | 2588718.9688 | 1184452.3464 | 2588717.1169 | 1184453.4825
74 | 2588701.1103 | 1184477.2265 | 2588712.9191 | 1184490.0663 | 2588719.5548 | 1184495.7011 | 2588727.738 | 1184500.3991 | 2588732.0034 | 1184501.9548
75 | 2588756.4602 | 1184464.8708 | 2588772.3186 | 1184463.9182 | 2588783.1394 | 1184465.3871
76 | 2588764.3971 | 1184508.8563 | 2588745.4857 | 1184505.6905 | 2588735.8339 | 1184503.352 | 2588732.0034 | 1184501.9548
77 | 2588783.1394 | 1184465.3871 | 2588784.2119 | 1184465.5327
78 | 2588796.9137 | 1184518.3666 | 2588778.1056 | 1184513.3328 | 2588764.3971 | 1184508.8563
79 | 2588764.3971 | 1184508.8563 | 2588758.6981 | 1184511.9119
80 | 2588797.8573 | 1184512.8509 | 2588796.1505 | 1184510.2972 | 2588794.4453 | 1184508.5995 | 2588781.5668 | 1184500.9343
81 | 2588796.9137 | 1184518.3666 | 2588797.8573 | 1184512.8509
82 | 2588796.9137 | 1184518.3666 | 2588815.6136 | 1184522.7448 | 2588819.824 | 1184523.339
83 | 2589080.2821 | 1184564.8303 | 2589084.8717 | 1184562.0871 | 2589088.4339 | 1184560.9467 | 2589111.9859 | 1184560.2143 | 2589112.5899 | 1184560.2208
84 | 2589080.2821 | 1184564.8303 | 2589071.6943 | 1184559.888 | 2589054.491 | 1184547.4243 | 2589041.1628 | 1184537.955 | 2589032.2094 | 1184533.5026 | 2589025.3289 | 1184531.4809 | 2589016.8474 | 1184530.3849 | 2589007.7267 | 1184530.3684 | 2588996.3192 | 1184531.9458 | 2588980.4976 | 1184536.1884 | 2588966.9256 | 1184539.3819 | 2588958.3802 | 1184540.9319 | 2588950.8556 | 1184541.3683 | 2588942.2002 | 1184541.2177 | 2588934.9474 | 1184540.0972 | 2588929.7909 | 1184539.2662
85 | 2589080.2821 | 1184564.8303 | 2589088.6735 | 1184546.1271
86 | 2588929.7909 | 1184539.2662 | 2588927.9922 | 1184538.9763 | 2588920.0883 | 1184536.5786 | 2588913.7104 | 1184533.9558 | 2588908.0872 | 1184530.8758 | 2588907.2236 | 1184530.207
87 | 2589088.6735 | 1184546.1271 | 2589098.3274 | 1184524.6098 | 2589103.7795 | 1184509.3252 | 2589105.7986 | 1184504.5759
88 | 2588895.7728 | 1184520.8381 | 2588900.7266 | 1184525.1755 | 2588907.2236 | 1184530.207
89 | 2589290.4736 | 1184313.5961 | 2589277.0588 | 1184298.5458 | 2589272.8239 | 1184294.9961 | 2589259.8797 | 1184286.982 | 2589250.6888 | 1184282.096 | 2589247.7027 | 1184281.1676 | 2589244.5735 | 1184281.2845 | 2589242.0945 | 1184282.1561 | 2589239.6175 | 1184284.1505 | 2589235.5287 | 1184289.6385 | 2589191.5912 | 1184367.2805 | 2589156.6896 | 1184426.9971 | 2589125.3911 | 1184469.9653 | 2589109.692 | 1184495.4183 | 2589105.7986 | 1184504.5759
90 | 2588895.7728 | 1184520.8381 | 2588887.2039 | 1184517.9526 | 2588885.3264 | 1184517.4762
91 | 2589290.4736 | 1184313.5961 | 2589060.5087 | 1184109.6204
92 | 2589290.4736 | 1184313.5961 | 2589456.7895 | 1184404.4792
93 | 2589037.7376 | 1184095.9886 | 2589048.0799 | 1184104.1627 | 2589060.5087 | 1184109.6204
94 | 2589596.6517 | 1185017.0939 | 2589613.0128 | 1185025.0583 | 2589621.7895 | 1185029.6009 | 2589629.0014 | 1185033.9127 | 2589633.1114 | 1185036.6981
95 | 2589596.6517 | 1185017.0939 | 2589595.3618 | 1185003.9338 | 2589595.8618 | 1184997.4629 | 2589597.9374 | 1184993.0236 | 2589606.7143 | 1184984.4816 | 2589613.2651 | 1184977.3443 | 2589620.695 | 1184966.6146 | 2589625.8506 | 1184951.509 | 2589627.7941 | 1184941.2447 | 2589627.2334 | 1184926.0934 | 2589626.4008 | 1184916.8901 | 2589624.1852 | 1184911.2132 | 2589623.9802 | 1184910.9827
96 | 2589462.0923 | 1184127.9603 | 2589460.162 | 1184128.3973 | 2589457.9707 | 1184128.0566 | 2589456.5638 | 1184126.6583 | 2589456.1247 | 1184124.3913 | 2589456.8052 | 1184122.4846
97 | 2589465.3059 | 1184115.1147 | 2589461.9809 | 1184116.777 | 2589458.8327 | 1184119.1393 | 2589456.9982 | 1184121.944 | 2589456.8052 | 1184122.4846
98 | 2589657.1388 | 1185077.8384 | 2589656.9709 | 1185081.4238
99 | 2589658.1698 | 1185055.8177 | 2589657.1388 | 1185077.8384
100 | 2589656.9709 | 1185081.4238 | 2589656.6025 | 1185089.2933 | 2589655.6816 | 1185107.6058
101 | 2589658.1698 | 1185055.8177 | 2589674.5412 | 1185036.6164
102 | 2589658.1698 | 1185055.8177 | 2589638.4912 | 1185040.344 | 2589633.1114 | 1185036.6981
103 | 2589689.627 | 1185021.1444 | 2589681.7113 | 1185028.207 | 2589674.5412 | 1185036.6164
104 | 2589623.9802 | 1184910.9827 | 2589620.6906 | 1184907.284 | 2589614.1699 | 1184901.1477 | 2589613.2931 | 1184900.7502
105 | 2588819.824 | 1184523.339 | 2588820.7439 | 1184523.4688 | 2588824.2032 | 1184523.5159
106 | 2588853.1696 | 1184517.0501 | 2588845.7313 | 1184518.9085 | 2588836.646 | 1184521.4824 | 2588830.3292 | 1184522.9506 | 2588825.0563 | 1184523.5274 | 2588824.2032 | 1184523.5159
107 | 2588862.4537 | 1184514.7305 | 2588871.8037 | 1184514.9242 | 2588879.7664 | 1184516.0655 | 2588885.3264 | 1184517.4762
108 | 2588862.4537 | 1184514.7305 | 2588853.1696 | 1184517.0501
109 | 2589098.2154 | 1184026.9465 | 2589097.4391 | 1184027.7103 | 2589086.715 | 1184036.201 | 2589080.1777 | 1184042.6275 | 2589078.0706 | 1184045.1818
110 | 2589086.198 | 1183929.1578 | 2589101.9417 | 1183968.9718 | 2589105.2363 | 1183979.8936 | 2589106.9298 | 1183987.6389 | 2589107.753 | 1183995.3191 | 2589107.5842 | 1184003.2013 | 2589106.8331 | 1184009.8283 | 2589105.4312 | 1184015.4227 | 2589103.8213 | 1184019.9391 | 2589100.6087 | 1184024.5918 | 2589098.2154 | 1184026.9465
111 | 2589066.8878 | 1184058.738 | 2589078.0706 | 1184045.1818
112 | 2589086.198 | 1183929.1578 | 2589061.168 | 1183887.1377 | 2589037.3487 | 1183860.2566 | 2589009.2434 | 1183831.4491 | 2588992.0095 | 1183820.1418 | 2588956.1898 | 1183801.3096 | 2588948.7626 | 1183797.1553
113 | 2589452.8275 | 1184094.2491 | 2589086.198 | 1183929.1578
114 | 2589066.8878 | 1184058.738 | 2589058.1655 | 1184068.1922 | 2589048.9112 | 1184078.8814 | 2589037.7376 | 1184095.9886
115 | 2589200.3781 | 1185056.4014 | 2589193.914 | 1185048.7285 | 2589187.8928 | 1185043.2689
116 | 2589461.4545 | 1184107.5406 | 2589461.1774 | 1184106.9956 | 2589454.6722 | 1184097.3021 | 2589452.8275 | 1184094.2491
117 | 2589465.3059 | 1184115.1147 | 2589461.4545 | 1184107.5406

## bus_geodata
| x | y | coords
0 | 2588308.4753 | 1185078.863
1 | 2588234.8368 | 1185050.4612
2 | 2588316.4535 | 1185080.4482
3 | 2588234.0058 | 1185049.2546
4 | 2588318.2928 | 1185092.1284
5 | 2588127.2823 | 1185447.038
6 | 2588108.4779 | 1185444.2042
7 | 2588228.5457 | 1185032.4045
8 | 2588063.7781 | 1185415.6344
9 | 2588052.2001 | 1185452.8992
10 | 2588088.2554 | 1185434.2101
11 | 2588324.3093 | 1185093.7504
12 | 2588230.1283 | 1185022.7227
13 | 2588269.4887 | 1185842.7244
14 | 2588123.9402 | 1185809.4878
15 | 2588278.2696 | 1185841.6955
16 | 2588082.8328 | 1185784.7542
17 | 2588343.3892 | 1185778.952
18 | 2588023.8067 | 1185726.8316
19 | 2588083.8341 | 1185821.5174
20 | 2588363.0041 | 1185765.4563
21 | 2588399.2566 | 1185901.2111
22 | 2588419.817 | 1185903.4503
23 | 2588056.7582 | 1185636.4518
24 | 2587951.2256 | 1185747.3777
25 | 2587654.8907 | 1186010.9895
26 | 2587941.3301 | 1185544.9705
27 | 2588343.8923 | 1185763.237
28 | 2588393.1322 | 1185799.899
29 | 2588370.203 | 1185763.1299
30 | 2588444.0794 | 1185897.3811
31 | 2588938.4371 | 1185142.0782
32 | 2588915.2434 | 1185306.9306
33 | 2588935.931 | 1185130.0894
34 | 2589014.8981 | 1185338.2175
35 | 2588510.6079 | 1185699.1572
36 | 2588921.0766 | 1185128.305
37 | 2589103.2809 | 1184637.0366
38 | 2588986.2889 | 1184881.345
39 | 2589088.3327 | 1184579.49
40 | 2588991.5559 | 1185314.5595
41 | 2588495.3708 | 1185707.2778
42 | 2588906.8408 | 1185130.8329
43 | 2588938.5159 | 1185083.7718
44 | 2589239.6954 | 1185115.5912
45 | 2588953.6123 | 1184910.4316
46 | 2589204.9401 | 1185061.8163
47 | 2589495.5474 | 1184965.8007
48 | 2588095.7815 | 1185437.9827
49 | 2588030.7025 | 1185499.4519
50 | 2588025.5221 | 1185510.1916
51 | 2588450.249 | 1185896.2096
52 | 2588395.9988 | 1185803.5157
53 | 2588409.3048 | 1185752.03
54 | 2588401.3394 | 1185755.4622
55 | 2588427.4005 | 1185743.2138
56 | 2588319.0907 | 1185781.8842
57 | 2588338.6964 | 1185747.189
58 | 2587994.9637 | 1185527.5508
59 | 2587999.5054 | 1185525.939
60 | 2587806.169 | 1185593.5045
61 | 2587851.0415 | 1185609.4988
62 | 2587803.4272 | 1185593.8789
63 | 2587779.3482 | 1185598.0898
64 | 2587760.4896 | 1185604.5262
65 | 2587650.9866 | 1185572.269
66 | 2587610.6615 | 1185560.0543
67 | 2587705.7509 | 1185442.6121
68 | 2587601.5597 | 1185557.2974
69 | 2587596.9415 | 1185556.7396
70 | 2588717.1169 | 1184453.4825
71 | 2588701.1103 | 1184477.2265
72 | 2588756.4602 | 1184464.8708
73 | 2588732.0034 | 1184501.9548
74 | 2588783.1394 | 1184465.3871
75 | 2588764.3971 | 1184508.8563
76 | 2588784.2119 | 1184465.5327
77 | 2588781.5668 | 1184500.9343
78 | 2588797.8573 | 1184512.8509
79 | 2588796.9137 | 1184518.3666
80 | 2588758.6981 | 1184511.9119
81 | 2589112.5899 | 1184560.2208
82 | 2589080.2821 | 1184564.8303
83 | 2588929.7909 | 1184539.2662
84 | 2589088.6735 | 1184546.1271
85 | 2588907.2236 | 1184530.207
86 | 2589105.7986 | 1184504.5759
87 | 2588895.7728 | 1184520.8381
88 | 2589290.4736 | 1184313.5961
89 | 2589456.7895 | 1184404.4792
90 | 2589060.5087 | 1184109.6204
91 | 2589596.6517 | 1185017.0939
92 | 2589462.0923 | 1184127.9603
93 | 2589456.8052 | 1184122.4846
94 | 2589657.1388 | 1185077.8384
95 | 2589656.9709 | 1185081.4238
96 | 2589658.1698 | 1185055.8177
97 | 2589655.6816 | 1185107.6058
98 | 2589674.5412 | 1185036.6164
99 | 2589633.1114 | 1185036.6981
100 | 2589689.627 | 1185021.1444
101 | 2589623.9802 | 1184910.9827
102 | 2589613.2931 | 1184900.7502
103 | 2588819.824 | 1184523.339
104 | 2588824.2032 | 1184523.5158
105 | 2588885.3264 | 1184517.4762
106 | 2588862.4537 | 1184514.7305
107 | 2588853.1696 | 1184517.0501
108 | 2589098.2154 | 1184026.9466
109 | 2589078.0706 | 1184045.1818
110 | 2589086.198 | 1183929.1578
111 | 2589066.8878 | 1184058.738
112 | 2589037.7376 | 1184095.9886
113 | 2589200.3781 | 1185056.4014
114 | 2589187.8928 | 1185043.2689
115 | 2588948.7626 | 1183797.1553
116 | 2589452.8275 | 1184094.2491
117 | 2589461.4545 | 1184107.5406
118 | 2589465.3059 | 1184115.1147
119 | 2588906.8408 | 1185130.8329

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97245 | -0.19659 | 0.0020095 | 0.00050363
1 | 0.97187 | -0.20077 | 0.0018886 | 0.00047333
2 | 0.97253 | -0.19602 | 0 | 0
3 | 0.97187 | -0.20081 | 0.0019923 | 0.00049932
4 | 0.97265 | -0.1952 | 0 | 0
5 | 0.97669 | -0.16612 | 0.00014596 | 3.6581e-05
6 | 0.97688 | -0.1647 | 0 | 0
7 | 0.97185 | -0.20094 | 0.00031798 | 7.9694e-05
8 | 0.97756 | -0.15982 | 0 | 0
9 | 0.97812 | -0.15584 | 0 | 0
10 | 0.97712 | -0.16297 | 0.0019435 | 0.00048708
11 | 0.97264 | -0.19522 | 0.00028487 | 7.1394e-05
12 | 0.97185 | -0.20098 | 0.00034428 | 8.6285e-05
13 | 0.9861 | -0.098667 | 0.00037254 | 9.3368e-05
14 | 0.98483 | -0.10774 | 0.00027905 | 6.9935e-05
15 | 0.98618 | -0.098122 | 0 | 0
16 | 0.98444 | -0.11059 | 0 | 0
17 | 0.98697 | -0.092419 | 0.001965 | 0.00049247
18 | 0.98377 | -0.11538 | 0 | 0
19 | 0.98441 | -0.11077 | 0.00045908 | 0.00011506
20 | 0.9872 | -0.090792 | 0 | 0
21 | 0.98692 | -0.092827 | 0.00034434 | 8.63e-05
22 | 0.98693 | -0.092753 | 0 | 0
23 | 0.98374 | -0.11557 | 0.00017938 | 4.4956e-05
24 | 0.9829 | -0.1216 | 0 | 0
25 | 0.98262 | -0.12365 | 0.00048135 | 0.00012064
26 | 0.98049 | -0.13884 | 0 | 0
27 | 0.98715 | -0.091113 | 0 | 0
28 | 0.98709 | -0.091552 | 0.00021922 | 5.4943e-05
29 | 0.98728 | -0.090193 | 0.0018681 | 0.00046819
30 | 0.98694 | -0.092664 | 0.00053081 | 0.00013303
31 | 0.99922 | -0.005474 | 0.00047675 | 0.00011949
32 | 0.99682 | -0.022439 | 0 | 0
33 | 0.9994 | -0.0042204 | 0 | 0
34 | 0.99642 | -0.025255 | 0 | 0
35 | 0.98927 | -0.076024 | 0 | 0
36 | 0.99962 | -0.0026939 | 0 | 0
37 | 0.98713 | -0.091379 | 0 | 0
38 | 0.9928 | -0.050858 | 0.00028504 | 7.1438e-05
39 | 0.98585 | -0.10055 | 0.0017734 | 0.00044445
40 | 0.99633 | -0.025912 | 0.0019114 | 0.00047905
41 | 0.98904 | -0.077674 | 0.00076153 | 0.00019086
42 | 1 | 0 | -0.056761 | -0.014001
43 | 0.99787 | -0.015004 | 0 | 0
44 | 0.99356 | -0.045423 | 0 | 0
45 | 0.99391 | -0.042991 | 0.0009379 | 0.00023506
46 | 0.99334 | -0.047001 | 0.00024957 | 6.2548e-05
47 | 0.9906 | -0.066415 | 0 | 0
48 | 0.97703 | -0.16366 | 0.00078083 | 0.0001957
49 | 0.97885 | -0.15062 | 0.00027976 | 7.0115e-05
50 | 0.97902 | -0.14937 | 0.00068627 | 0.000172
51 | 0.98695 | -0.092607 | 0 | 0
52 | 0.98708 | -0.091618 | 0.00049697 | 0.00012455
53 | 0.98777 | -0.0867 | 0.00184 | 0.00046114
54 | 0.98767 | -0.087448 | 0.00021899 | 5.4884e-05
55 | 0.98803 | -0.084839 | 0.00018406 | 4.6129e-05
56 | 0.98714 | -0.091233 | 0.0003763 | 9.4309e-05
57 | 0.98712 | -0.091322 | 0.0011769 | 0.00029497
58 | 0.97959 | -0.14531 | 0.00013058 | 3.2726e-05
59 | 0.97951 | -0.14585 | 0.00015018 | 3.764e-05
60 | 0.97946 | -0.14631 | 0 | 0
61 | 0.9794 | -0.14669 | 0.00074903 | 0.00018773
62 | 0.97944 | -0.14643 | 0.00064129 | 0.00016072
63 | 0.97931 | -0.14735 | 0.00098793 | 0.0002476
64 | 0.97924 | -0.14789 | 0 | 0
65 | 0.97881 | -0.15098 | 0 | 0
66 | 0.97873 | -0.15154 | 0.00037537 | 9.4077e-05
67 | 0.97852 | -0.15303 | 0.0013236 | 0.00033172
68 | 0.97872 | -0.15162 | 0 | 0
69 | 0.97871 | -0.15167 | 0.00088166 | 0.00022096
70 | 0.98226 | -0.12623 | 0.00034295 | 8.5951e-05
71 | 0.98238 | -0.12535 | 0 | 0
72 | 0.98209 | -0.12741 | 0 | 0
73 | 0.98255 | -0.12412 | 0.00147 | 0.00036841
74 | 0.98199 | -0.12813 | 0.0021203 | 0.0005314
75 | 0.98277 | -0.1226 | 0 | 0
76 | 0.98199 | -0.12814 | 0.00047559 | 0.00011919
77 | 0.98298 | -0.12107 | 0.00014043 | 3.5194e-05
78 | 0.98299 | -0.12104 | 0 | 0
79 | 0.98299 | -0.12103 | 0 | 0
80 | 0.98277 | -0.12261 | 7.3679e-05 | 1.8466e-05
81 | 0.9855 | -0.10308 | 0.0008951 | 0.00022433
82 | 0.98554 | -0.10277 | 0 | 0
83 | 0.9841 | -0.11308 | 7.205e-05 | 1.8057e-05
84 | 0.98537 | -0.10399 | 0.00069886 | 0.00017515
85 | 0.98388 | -0.11462 | 0.00028109 | 7.0448e-05
86 | 0.98505 | -0.10634 | 0.00028984 | 7.2641e-05
87 | 0.98376 | -0.11551 | 0 | 0
88 | 0.98289 | -0.1222 | 0.00060259 | 0.00015102
89 | 0.9828 | -0.12287 | 0.00033342 | 8.3564e-05
90 | 0.98124 | -0.13428 | 0.0012655 | 0.00031716
91 | 0.98946 | -0.074505 | 0 | 0
92 | 0.97965 | -0.14585 | 0.00061153 | 0.00015326
93 | 0.97966 | -0.14578 | 0.00026832 | 6.7248e-05
94 | 0.98892 | -0.078379 | 0.0005901 | 0.00014789
95 | 0.9889 | -0.078459 | 0.0014306 | 0.00035853
96 | 0.989 | -0.077757 | 0 | 0
97 | 0.98888 | -0.078659 | 0.00074454 | 0.0001866
98 | 0.98896 | -0.078062 | 0.0005025 | 0.00012594
99 | 0.98918 | -0.076483 | 0.00072003 | 0.00018046
100 | 0.98894 | -0.078212 | 0.00067955 | 0.00017031
101 | 0.98908 | -0.077207 | 0.0019908 | 0.00049895
102 | 0.98908 | -0.077248 | 0.00027031 | 6.7747e-05
103 | 0.98314 | -0.11991 | 0.00014935 | 3.7431e-05
104 | 0.98317 | -0.11969 | 0.00034809 | 8.724e-05
105 | 0.98367 | -0.11617 | 8.4676e-05 | 2.1222e-05
106 | 0.98347 | -0.11754 | 0 | 0
107 | 0.9834 | -0.11811 | 0.00059488 | 0.00014909
108 | 0.98082 | -0.13732 | 0.00060456 | 0.00015152
109 | 0.98091 | -0.13667 | 0.00020706 | 5.1895e-05
110 | 0.98058 | -0.13915 | 0 | 0
111 | 0.98097 | -0.13622 | 0 | 0
112 | 0.98114 | -0.13498 | 0 | 0
113 | 0.99332 | -0.047157 | 0.00028633 | 7.1761e-05
114 | 0.99327 | -0.047503 | 0.0018837 | 0.0004721
115 | 0.98053 | -0.13948 | 0.00015298 | 3.834e-05
116 | 0.97972 | -0.1454 | 0.00028582 | 7.1633e-05
117 | 0.97969 | -0.14559 | 0.00030691 | 7.6919e-05
118 | 0.97968 | -0.14567 | 0 | 0
119 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0045458 | 0.0011382 | -0.0045432 | -0.0011383 | 2.6293e-06 | -6.8599e-08 | 0.0069555 | 0.0069558 | 0.0069558 | 0.97245 | -0.19659 | 0.97187 | -0.20077 | 2.5762
1 | -0.0065553 | -0.0016418 | 0.0065558 | 0.0016419 | 5.1065e-07 | 9.548e-08 | 0.01003 | 0.01003 | 0.01003 | 0.97245 | -0.19659 | 0.97253 | -0.19602 | 3.7149
2 | 0.0026546 | 0.00066494 | -0.0026546 | -0.00066495 | 1.5101e-08 | -1.2347e-08 | 0.0040643 | 0.0040643 | 0.0040643 | 0.97187 | -0.20077 | 0.97187 | -0.20081 | 1.5053
3 | -0.0065558 | -0.0016419 | 0.0065566 | 0.0016421 | 7.4241e-07 | 1.3878e-07 | 0.01003 | 0.01003 | 0.01003 | 0.97253 | -0.19602 | 0.97265 | -0.1952 | 3.7149
4 | 0.00066228 | 0.00016563 | -0.00066226 | -0.00016586 | 1.1865e-08 | -2.2463e-07 | 0.0010139 | 0.001014 | 0.001014 | 0.97187 | -0.20081 | 0.97185 | -0.20094 | 0.37554
5 | 0.00028487 | 7.1317e-05 | -0.00028487 | -7.1394e-05 | 7.3847e-10 | -7.7055e-08 | 0.00043578 | 0.00043581 | 0.00043581 | 0.97265 | -0.1952 | 0.97264 | -0.19522 | 0.16141
6 | -0.0068414 | -0.0017134 | 0.006869 | 0.0017189 | 2.7544e-05 | 5.5706e-06 | 0.010466 | 0.010464 | 0.010466 | 0.97265 | -0.1952 | 0.97669 | -0.16612 | 3.8763
7 | -0.0070149 | -0.0017555 | 0.0070163 | 0.0017558 | 1.3743e-06 | 2.8719e-07 | 0.010687 | 0.010686 | 0.010687 | 0.97669 | -0.16612 | 0.97688 | -0.1647 | 3.958
8 | -0.0070163 | -0.0017558 | 0.0070173 | 0.001756 | 1.0075e-06 | 2.1048e-07 | 0.010686 | 0.010686 | 0.010686 | 0.97688 | -0.1647 | 0.97703 | -0.16366 | 3.958
9 | 0.00034428 | 8.6164e-05 | -0.00034428 | -8.6285e-05 | 1.7047e-09 | -1.2118e-07 | 0.00052709 | 0.00052714 | 0.00052714 | 0.97185 | -0.20094 | 0.97185 | -0.20098 | 0.19524
10 | -0.0097466 | -0.0024402 | 0.0097519 | 0.0024418 | 5.3585e-06 | 1.5715e-06 | 0.014835 | 0.014835 | 0.014835 | 0.97756 | -0.15982 | 0.97812 | -0.15584 | 5.4945
11 | 0.0097466 | 0.0024402 | -0.0097423 | -0.002439 | 4.2401e-06 | 1.2439e-06 | 0.014835 | 0.014835 | 0.014835 | 0.97756 | -0.15982 | 0.97712 | -0.16297 | 5.4945
12 | -0.0097519 | -0.0024418 | 0.009759 | 0.0024439 | 7.0437e-06 | 2.0648e-06 | 0.014835 | 0.014835 | 0.014835 | 0.97812 | -0.15584 | 0.97885 | -0.15062 | 5.4944
13 | 0.0077989 | 0.0019519 | -0.0077981 | -0.0019517 | 7.4109e-07 | 1.7956e-07 | 0.011876 | 0.011876 | 0.011876 | 0.97712 | -0.16297 | 0.97703 | -0.16366 | 4.3984
14 | 0.01748 | 0.0043595 | -0.017459 | -0.0043569 | 2.1738e-05 | 2.6168e-06 | 0.02637 | 0.026372 | 0.026372 | 0.9861 | -0.098667 | 0.98483 | -0.10774 | 3.2558
15 | -0.017853 | -0.0044529 | 0.017854 | 0.004453 | 1.3338e-06 | 1.7464e-07 | 0.026932 | 0.026932 | 0.026932 | 0.9861 | -0.098667 | 0.98618 | -0.098122 | 3.325
16 | 0.01718 | 0.0042869 | -0.017173 | -0.0042862 | 6.7311e-06 | 7.5529e-07 | 0.02595 | 0.025951 | 0.025951 | 0.98483 | -0.10774 | 0.98444 | -0.11059 | 3.2038
17 | -0.017854 | -0.004453 | 0.017868 | 0.0044549 | 1.3963e-05 | 1.8248e-06 | 0.026932 | 0.026931 | 0.026932 | 0.98618 | -0.098122 | 0.98697 | -0.092419 | 3.325
18 | 0.016714 | 0.0041716 | -0.016703 | -0.0041705 | 1.0995e-05 | 1.0706e-06 | 0.025257 | 0.025259 | 0.025259 | 0.98444 | -0.11059 | 0.98377 | -0.11538 | 3.1183
19 | 0.00045909 | 0.00011458 | -0.00045908 | -0.00011506 | 1.1253e-08 | -4.7191e-07 | 0.00069376 | 0.00069393 | 0.00069393 | 0.98444 | -0.11059 | 0.98441 | -0.11077 | 0.25701
20 | -0.019833 | -0.0049473 | 0.019838 | 0.0049481 | 4.4254e-06 | 7.8905e-07 | 0.029893 | 0.029893 | 0.029893 | 0.98697 | -0.092419 | 0.9872 | -0.090792 | 3.6905
21 | 0.00017938 | 4.3736e-05 | -0.00017938 | -4.4956e-05 | 4.4124e-09 | -1.2198e-06 | 0.0002709 | 0.00027133 | 0.00027133 | 0.98377 | -0.11538 | 0.98374 | -0.11557 | 0.10049
22 | 0.016523 | 0.0041268 | -0.016509 | -0.0041255 | 1.4125e-05 | 1.2938e-06 | 0.024988 | 0.024989 | 0.024989 | 0.98377 | -0.11538 | 0.9829 | -0.1216 | 3.0851
23 | 0.0015533 | 0.00038845 | -0.0015533 | -0.00038868 | 6.8774e-08 | -2.3064e-07 | 0.0023411 | 0.0023412 | 0.0023412 | 0.9872 | -0.090792 | 0.98715 | -0.091113 | 0.8671
24 | 0.0015916 | 0.00039624 | -0.0015915 | -0.00039676 | 1.6542e-07 | -5.256e-07 | 0.0023982 | 0.0023984 | 0.0023984 | 0.9872 | -0.090792 | 0.98709 | -0.091552 | 0.88829
25 | -0.022983 | -0.0057328 | 0.022984 | 0.0057332 | 1.8874e-06 | 4.3571e-07 | 0.034632 | 0.034632 | 0.034632 | 0.9872 | -0.090792 | 0.98728 | -0.090193 | 4.2756
26 | -0.00034434 | -8.63e-05 | 0.00034434 | 8.6035e-05 | 3.5102e-09 | -2.6538e-07 | 0.00051918 | 0.00051908 | 0.00051918 | 0.98692 | -0.092827 | 0.98693 | -0.092753 | 0.19229
27 | -0.00034434 | -8.6035e-05 | 0.00034435 | 8.5716e-05 | 4.2112e-09 | -3.1851e-07 | 0.00051908 | 0.00051897 | 0.00051908 | 0.98693 | -0.092753 | 0.98694 | -0.092664 | 0.19225
28 | 0.00048148 | 0.00011566 | -0.00048135 | -0.00012064 | 1.3118e-07 | -4.9751e-06 | 0.00072716 | 0.00072892 | 0.00072892 | 0.9829 | -0.1216 | 0.98262 | -0.12365 | 0.26997
29 | 0.016028 | 0.0040098 | -0.01599 | -0.0040004 | 3.8084e-05 | 9.4045e-06 | 0.024262 | 0.024264 | 0.024264 | 0.9829 | -0.1216 | 0.98049 | -0.13884 | 4.4933
30 | 0.0049663 | 0.0012387 | -0.0049612 | -0.0012385 | 5.087e-06 | 1.4756e-07 | 0.0075348 | 0.0075355 | 0.0075355 | 0.98049 | -0.13884 | 0.97946 | -0.14631 | 2.7909
31 | 0.011023 | 0.0027618 | -0.011014 | -0.0027587 | 9.8518e-06 | 3.0783e-06 | 0.016729 | 0.016729 | 0.016729 | 0.98049 | -0.13884 | 0.97959 | -0.14531 | 6.196
32 | 0.0003763 | 9.3915e-05 | -0.0003763 | -9.4309e-05 | 6.2266e-09 | -3.9418e-07 | 0.00056709 | 0.00056723 | 0.00056723 | 0.98715 | -0.091113 | 0.98714 | -0.091233 | 0.21009
33 | 0.001177 | 0.00029476 | -0.0011769 | -0.00029497 | 3.4025e-08 | -2.0839e-07 | 0.0017741 | 0.0017742 | 0.0017742 | 0.98715 | -0.091113 | 0.98712 | -0.091322 | 0.65709
34 | 0.0013723 | 0.00034182 | -0.0013722 | -0.00034187 | 1.2332e-08 | -5.4334e-08 | 0.0020679 | 0.0020679 | 0.0020679 | 0.98709 | -0.091552 | 0.98708 | -0.091618 | 0.7659
35 | -0.024853 | -0.0062014 | 0.024862 | 0.0062038 | 9.3652e-06 | 2.3698e-06 | 0.037448 | 0.037447 | 0.037448 | 0.98728 | -0.090193 | 0.98767 | -0.087448 | 4.6232
36 | -0.00087516 | -0.00021875 | 0.00087516 | 0.00021867 | 6.8202e-09 | -7.7627e-08 | 0.0013193 | 0.0013192 | 0.0013193 | 0.98694 | -0.092664 | 0.98695 | -0.092607 | 0.48862
37 | 0.030098 | 0.0075234 | -0.030028 | -0.007503 | 7.0212e-05 | 2.0416e-05 | 0.044814 | 0.044817 | 0.044817 | 0.99922 | -0.005474 | 0.99682 | -0.022439 | 5.5329
38 | -0.030575 | -0.0076429 | 0.03058 | 0.0076445 | 5.2797e-06 | 1.5493e-06 | 0.045524 | 0.045524 | 0.045524 | 0.99922 | -0.005474 | 0.9994 | -0.0042204 | 5.6203
39 | 0.0019123 | 0.00047706 | -0.0019116 | -0.00047867 | 7.4133e-07 | -1.6151e-06 | 0.0028539 | 0.0028546 | 0.0028546 | 0.99682 | -0.022439 | 0.99642 | -0.025255 | 1.0572
40 | 0.028115 | 0.0070259 | -0.027909 | -0.0069684 | 0.00020644 | 5.7527e-05 | 0.041963 | 0.04197 | 0.04197 | 0.99682 | -0.022439 | 0.98927 | -0.076024 | 5.1815
41 | -0.03058 | -0.0076445 | 0.030586 | 0.0076463 | 6.4306e-06 | 1.8868e-06 | 0.045524 | 0.045524 | 0.045524 | 0.9994 | -0.0042204 | 0.99962 | -0.0026939 | 5.6202
42 | 0.0019116 | 0.00047867 | -0.0019114 | -0.00047905 | 1.7364e-07 | -3.7796e-07 | 0.0028546 | 0.0028547 | 0.0028547 | 0.99642 | -0.025255 | 0.99633 | -0.025912 | 1.0573
43 | 0.027909 | 0.0069684 | -0.027903 | -0.0069667 | 6.3262e-06 | 1.7683e-06 | 0.04197 | 0.041971 | 0.041971 | 0.98927 | -0.076024 | 0.98904 | -0.077674 | 5.1815
44 | -0.05594 | -0.013993 | 0.055961 | 0.014001 | 2.079e-05 | 7.429e-06 | 0.083262 | 0.083262 | 0.083262 | 0.99962 | -0.0026939 | 1 | 0 | 10.2793
45 | 0.025353 | 0.0063469 | -0.02531 | -0.006331 | 4.3037e-05 | 1.5919e-05 | 0.037738 | 0.037738 | 0.037738 | 0.99962 | -0.0026939 | 0.99787 | -0.015004 | 13.9772
46 | -0.01451 | -0.0036145 | 0.014591 | 0.003642 | 8.0806e-05 | 2.7597e-05 | 0.021865 | 0.021864 | 0.021865 | 0.98713 | -0.091379 | 0.9928 | -0.050858 | 8.0983
47 | 0.01451 | 0.0036145 | -0.014492 | -0.0036082 | 1.8189e-05 | 6.2175e-06 | 0.021865 | 0.021866 | 0.021866 | 0.98713 | -0.091379 | 0.98585 | -0.10055 | 8.0984
48 | -0.014876 | -0.0037135 | 0.014892 | 0.003719 | 1.609e-05 | 5.5166e-06 | 0.022291 | 0.022291 | 0.022291 | 0.9928 | -0.050858 | 0.99391 | -0.042991 | 8.2561
49 | 0.012719 | 0.0031638 | -0.012715 | -0.0031625 | 3.8458e-06 | 1.2658e-06 | 0.019189 | 0.019189 | 0.019189 | 0.98585 | -0.10055 | 0.98554 | -0.10277 | 7.1071
50 | 0.027141 | 0.0067758 | -0.027114 | -0.0067685 | 2.6698e-05 | 7.3065e-06 | 0.040825 | 0.040826 | 0.040826 | 0.98904 | -0.077674 | 0.98803 | -0.084839 | 5.0402
51 | 0.0094191 | 0.0023556 | -0.0093797 | -0.0023447 | 3.9398e-05 | 1.099e-05 | 0.014044 | 0.014045 | 0.014045 | 0.99787 | -0.015004 | 0.99356 | -0.045423 | 5.202
52 | 0.015891 | 0.0039753 | -0.01583 | -0.0039541 | 6.1134e-05 | 2.1243e-05 | 0.023695 | 0.023695 | 0.023695 | 0.99787 | -0.015004 | 0.99391 | -0.042991 | 8.7761
53 | 0.0024203 | 0.0006055 | -0.0024197 | -0.00060613 | 5.2752e-07 | -6.3032e-07 | 0.0036244 | 0.0036246 | 0.0036246 | 0.99356 | -0.045423 | 0.99334 | -0.047001 | 1.3425
54 | 0.0069594 | 0.0017392 | -0.0069393 | -0.0017353 | 2.0093e-05 | 3.9e-06 | 0.010421 | 0.010422 | 0.010422 | 0.99356 | -0.045423 | 0.9906 | -0.066415 | 3.8601
55 | 0.0021702 | 0.00054359 | -0.0021701 | -0.00054366 | 4.6691e-08 | -7.3697e-08 | 0.0032508 | 0.0032508 | 0.0032508 | 0.99334 | -0.047001 | 0.99332 | -0.047157 | 1.204
56 | 0.0069393 | 0.0017353 | -0.0069316 | -0.0017337 | 7.7341e-06 | 1.5075e-06 | 0.010422 | 0.010423 | 0.010423 | 0.9906 | -0.066415 | 0.98946 | -0.074505 | 3.8603
57 | -0.010039 | -0.002514 | 0.01004 | 0.0025145 | 1.7327e-06 | 5.1651e-07 | 0.01526 | 0.01526 | 0.01526 | 0.97885 | -0.15062 | 0.97902 | -0.14937 | 5.6518
58 | -0.010727 | -0.0026865 | 0.010732 | 0.0026881 | 5.2106e-06 | 1.6088e-06 | 0.016303 | 0.016303 | 0.016303 | 0.97902 | -0.14937 | 0.97951 | -0.14585 | 6.0381
59 | -0.00087516 | -0.00021867 | 0.00087528 | 0.00021732 | 1.1842e-07 | -1.3486e-06 | 0.0013192 | 0.0013188 | 0.0013192 | 0.98695 | -0.092607 | 0.98708 | -0.091618 | 0.48861
60 | 0.025084 | 0.0062593 | -0.025081 | -0.0062587 | 2.5753e-06 | 6.5737e-07 | 0.037777 | 0.037777 | 0.037777 | 0.98777 | -0.0867 | 0.98767 | -0.087448 | 4.6639
61 | -0.026923 | -0.0067205 | 0.02693 | 0.0067224 | 6.8852e-06 | 1.8748e-06 | 0.040549 | 0.040549 | 0.040549 | 0.98777 | -0.0867 | 0.98803 | -0.084839 | 5.006
62 | 0.010883 | 0.002726 | -0.010882 | -0.0027257 | 8.2178e-07 | 2.5541e-07 | 0.016531 | 0.016531 | 0.016531 | 0.97959 | -0.14531 | 0.97951 | -0.14585 | 6.1226
63 | 0.00074907 | 0.00018713 | -0.00074903 | -0.00018773 | 3.9113e-08 | -5.9419e-07 | 0.0011378 | 0.001138 | 0.001138 | 0.97946 | -0.14631 | 0.9794 | -0.14669 | 0.42149
64 | 0.0042121 | 0.0010514 | -0.0042121 | -0.0010514 | 7.0676e-08 | -7.644e-09 | 0.0063977 | 0.0063977 | 0.0063977 | 0.97946 | -0.14631 | 0.97944 | -0.14643 | 2.3695
65 | 0.0035708 | 0.00089066 | -0.0035703 | -0.0008908 | 4.4997e-07 | -1.3544e-07 | 0.0054234 | 0.0054235 | 0.0054235 | 0.97944 | -0.14643 | 0.97931 | -0.14735 | 2.0087
66 | 0.0025824 | 0.0006432 | -0.0025822 | -0.00064337 | 1.9131e-07 | -1.7712e-07 | 0.0039224 | 0.0039225 | 0.0039225 | 0.97931 | -0.14735 | 0.97924 | -0.14789 | 1.4528
67 | 0.0025822 | 0.00064337 | -0.0025811 | -0.00064439 | 1.0932e-06 | -1.0112e-06 | 0.0039225 | 0.003923 | 0.003923 | 0.97924 | -0.14789 | 0.97881 | -0.15098 | 1.453
68 | 0.0012571 | 0.00031438 | -0.001257 | -0.00031487 | 9.6015e-08 | -4.9262e-07 | 0.0019109 | 0.0019111 | 0.0019111 | 0.97881 | -0.15098 | 0.97873 | -0.15154 | 0.70781
69 | 0.001324 | 0.00033001 | -0.0013236 | -0.00033172 | 3.74e-07 | -1.7158e-06 | 0.0020121 | 0.0020128 | 0.0020128 | 0.97881 | -0.15098 | 0.97852 | -0.15303 | 0.74547
70 | 0.00088167 | 0.00022079 | -0.00088166 | -0.00022091 | 1.0662e-08 | -1.1541e-07 | 0.0013404 | 0.0013404 | 0.0013404 | 0.97873 | -0.15154 | 0.97872 | -0.15162 | 0.49646
71 | 0.00088166 | 0.00022091 | -0.00088166 | -0.00022096 | 5.2156e-09 | -5.6452e-08 | 0.0013404 | 0.0013405 | 0.0013405 | 0.97872 | -0.15162 | 0.97871 | -0.15167 | 0.49647
72 | -0.0029395 | -0.0007359 | 0.0029399 | 0.00073567 | 3.596e-07 | -2.2966e-07 | 0.0044527 | 0.0044526 | 0.0044527 | 0.98226 | -0.12623 | 0.98238 | -0.12535 | 1.6492
73 | 0.0025966 | 0.00064994 | -0.0025961 | -0.00065034 | 4.2328e-07 | -3.921e-07 | 0.0039332 | 0.0039334 | 0.0039334 | 0.98226 | -0.12623 | 0.98209 | -0.12741 | 1.4568
74 | -0.0029399 | -0.00073567 | 0.0029404 | 0.00073535 | 4.9639e-07 | -3.1721e-07 | 0.0044526 | 0.0044524 | 0.0044526 | 0.98238 | -0.12535 | 0.98255 | -0.12412 | 1.6491
75 | 0.0025961 | 0.00065034 | -0.0025959 | -0.00065058 | 2.5881e-07 | -2.3963e-07 | 0.0039334 | 0.0039335 | 0.0039335 | 0.98209 | -0.12741 | 0.98199 | -0.12813 | 1.4569
76 | -0.0044103 | -0.0011038 | 0.0044113 | 0.0011037 | 9.2356e-07 | -6.5157e-08 | 0.0066786 | 0.0066785 | 0.0066786 | 0.98255 | -0.12412 | 0.98277 | -0.1226 | 2.4736
77 | 0.00047559 | 0.00011918 | -0.00047559 | -0.00011919 | 3.5074e-10 | -1.3558e-08 | 0.00072065 | 0.00072066 | 0.00072066 | 0.98199 | -0.12813 | 0.98199 | -0.12814 | 0.26691
78 | -0.0044849 | -0.0011221 | 0.0044859 | 0.001122 | 9.724e-07 | -5.439e-08 | 0.00679 | 0.0067898 | 0.00679 | 0.98277 | -0.1226 | 0.98299 | -0.12103 | 2.5148
79 | 7.3679e-05 | 1.8384e-05 | -7.3679e-05 | -1.8466e-05 | 5.0198e-11 | -8.1916e-08 | 0.00011153 | 0.00011156 | 0.00011156 | 0.98277 | -0.1226 | 0.98277 | -0.12261 | 0.041318
80 | -0.00014043 | -3.5194e-05 | 0.00014043 | 3.4935e-05 | 5.768e-10 | -2.592e-07 | 0.00021258 | 0.00021248 | 0.00021258 | 0.98298 | -0.12107 | 0.98299 | -0.12104 | 0.078732
81 | -0.00014043 | -3.4935e-05 | 0.00014043 | 3.4864e-05 | 1.5766e-10 | -7.0891e-08 | 0.00021248 | 0.00021246 | 0.00021248 | 0.98299 | -0.12104 | 0.98299 | -0.12103 | 0.078698
82 | -0.0046263 | -0.0011569 | 0.0046271 | 0.0011569 | 7.1771e-07 | -2.1373e-08 | 0.0070023 | 0.0070022 | 0.0070023 | 0.98299 | -0.12103 | 0.98314 | -0.11991 | 2.5934
83 | -0.0008951 | -0.00022433 | 0.00089514 | 0.00022392 | 3.79e-08 | -4.0916e-07 | 0.0013515 | 0.0013514 | 0.0013515 | 0.9855 | -0.10308 | 0.98554 | -0.10277 | 0.50057
84 | 0.0061713 | 0.0015422 | -0.0061625 | -0.0015409 | 8.7538e-06 | 1.3103e-06 | 0.0093161 | 0.0093168 | 0.0093168 | 0.98554 | -0.10277 | 0.9841 | -0.11308 | 3.4507
85 | 0.0056485 | 0.0013964 | -0.0056476 | -0.0013963 | 9.2891e-07 | 9.6101e-08 | 0.0085216 | 0.0085217 | 0.0085217 | 0.98554 | -0.10277 | 0.98537 | -0.10399 | 3.1562
86 | 0.0060905 | 0.0015229 | -0.0060892 | -0.0015227 | 1.2952e-06 | 1.8719e-07 | 0.0092079 | 0.009208 | 0.009208 | 0.9841 | -0.11308 | 0.98388 | -0.11462 | 3.4104
87 | 0.0049488 | 0.0012211 | -0.0049472 | -0.0012211 | 1.5644e-06 | 2.9022e-08 | 0.0074664 | 0.0074666 | 0.0074666 | 0.98537 | -0.10399 | 0.98505 | -0.10634 | 2.7654
88 | 0.0058081 | 0.0014522 | -0.0058074 | -0.0014521 | 7.1249e-07 | 8.6078e-08 | 0.0087829 | 0.008783 | 0.008783 | 0.98388 | -0.11462 | 0.98376 | -0.11551 | 3.2529
89 | 0.0046574 | 0.0011484 | -0.0046474 | -0.0011487 | 9.9169e-06 | -2.7111e-07 | 0.0070287 | 0.0070302 | 0.0070302 | 0.98505 | -0.10634 | 0.98289 | -0.1222 | 2.6038
90 | 0.0058074 | 0.0014521 | -0.0058069 | -0.0014521 | 5.2847e-07 | 6.3878e-08 | 0.008783 | 0.008783 | 0.008783 | 0.98376 | -0.11551 | 0.98367 | -0.11617 | 3.253
91 | 0.0037114 | 0.00091652 | -0.0037053 | -0.00091809 | 6.0467e-06 | -1.5637e-06 | 0.0056139 | 0.0056153 | 0.0056153 | 0.98289 | -0.1222 | 0.98124 | -0.13428 | 2.0797
92 | 0.00033345 | 8.1174e-05 | -0.00033342 | -8.3564e-05 | 3.0089e-08 | -2.3903e-06 | 0.00050398 | 0.00050483 | 0.00050483 | 0.98289 | -0.1222 | 0.9828 | -0.12287 | 0.18697
93 | 0.0024399 | 0.00060093 | -0.0024396 | -0.00060118 | 2.2812e-07 | -2.5021e-07 | 0.0036962 | 0.0036964 | 0.0036964 | 0.98124 | -0.13428 | 0.98114 | -0.13498 | 1.369
94 | 0.0046696 | 0.0011684 | -0.0046683 | -0.0011685 | 1.2752e-06 | -4.1741e-08 | 0.0070218 | 0.0070219 | 0.0070219 | 0.98946 | -0.074505 | 0.98918 | -0.076483 | 2.6007
95 | 0.002262 | 0.00056533 | -0.0022611 | -0.0005665 | 8.4333e-07 | -1.1754e-06 | 0.0034012 | 0.0034017 | 0.0034017 | 0.98946 | -0.074505 | 0.98908 | -0.077207 | 1.2599
96 | -0.00061153 | -0.00015326 | 0.00061153 | 0.00015313 | 5.6602e-09 | -1.302e-07 | 0.00092886 | 0.00092881 | 0.00092886 | 0.97965 | -0.14585 | 0.97966 | -0.14578 | 0.34402
97 | -0.00087985 | -0.00022038 | 0.00087987 | 0.00022024 | 1.2903e-08 | -1.4083e-07 | 0.0013364 | 0.0013363 | 0.0013364 | 0.97966 | -0.14578 | 0.97968 | -0.14567 | 0.49495
98 | 0.0021751 | 0.00054477 | -0.0021751 | -0.0005448 | 2.399e-08 | -3.6823e-08 | 0.0032728 | 0.0032728 | 0.0032728 | 0.98892 | -0.078379 | 0.9889 | -0.078459 | 1.2122
99 | -0.0027652 | -0.00069266 | 0.0027655 | 0.00069247 | 2.3813e-07 | -1.9127e-07 | 0.0041607 | 0.0041606 | 0.0041607 | 0.98892 | -0.078379 | 0.989 | -0.077757 | 1.541
100 | 0.00074456 | 0.00018627 | -0.00074454 | -0.0001866 | 2.0529e-08 | -3.2841e-07 | 0.0011202 | 0.0011203 | 0.0011203 | 0.9889 | -0.078459 | 0.98888 | -0.078659 | 0.41494
101 | 0.0011821 | 0.00029567 | -0.0011821 | -0.00029598 | 4.9799e-08 | -3.0463e-07 | 0.0017783 | 0.0017785 | 0.0017785 | 0.989 | -0.077757 | 0.98896 | -0.078062 | 0.65869
102 | -0.0039476 | -0.00098814 | 0.0039483 | 0.000988 | 6.9399e-07 | -1.3779e-07 | 0.0059389 | 0.0059388 | 0.0059389 | 0.989 | -0.077757 | 0.98918 | -0.076483 | 2.1996
103 | 0.00067956 | 0.00017004 | -0.00067955 | -0.00017031 | 1.4129e-08 | -2.7248e-07 | 0.0010224 | 0.0010225 | 0.0010225 | 0.98896 | -0.078062 | 0.98894 | -0.078212 | 0.3787
104 | 0.00027031 | 6.7557e-05 | -0.00027031 | -6.7747e-05 | 1.534e-09 | -1.9021e-07 | 0.00040661 | 0.00040667 | 0.00040667 | 0.98908 | -0.077207 | 0.98908 | -0.077248 | 0.15062
105 | -0.0047764 | -0.0011943 | 0.0047766 | 0.0011943 | 1.4308e-07 | -6.2211e-10 | 0.0072282 | 0.0072282 | 0.0072282 | 0.98314 | -0.11991 | 0.98317 | -0.11969 | 2.6771
106 | -0.0051247 | -0.0012815 | 0.0051258 | 0.0012816 | 1.1165e-06 | 5.2043e-08 | 0.0077551 | 0.0077549 | 0.0077551 | 0.98317 | -0.11969 | 0.9834 | -0.11811 | 2.8722
107 | 0.0057222 | 0.0014309 | -0.0057211 | -0.0014307 | 1.0813e-06 | 1.2228e-07 | 0.0086549 | 0.008655 | 0.008655 | 0.98367 | -0.11617 | 0.98347 | -0.11754 | 3.2056
108 | 0.0057211 | 0.0014307 | -0.0057206 | -0.0014307 | 4.4731e-07 | 5.0623e-08 | 0.008655 | 0.0086551 | 0.0086551 | 0.98347 | -0.11754 | 0.9834 | -0.11811 | 3.2056
109 | -0.0022318 | -0.00055016 | 0.002232 | 0.00054989 | 1.9453e-07 | -2.6908e-07 | 0.0033827 | 0.0033825 | 0.0033827 | 0.98082 | -0.13732 | 0.98091 | -0.13667 | 1.2528
110 | 0.0016273 | 0.00039864 | -0.0016269 | -0.0003998 | 3.9456e-07 | -1.1605e-06 | 0.0024655 | 0.002466 | 0.002466 | 0.98082 | -0.13732 | 0.98058 | -0.13915 | 0.91332
111 | -0.0024391 | -0.00060178 | 0.0024392 | 0.00060162 | 1.4985e-07 | -1.6421e-07 | 0.0036966 | 0.0036966 | 0.0036966 | 0.98091 | -0.13667 | 0.98097 | -0.13622 | 1.3691
112 | 0.00015298 | 3.5887e-05 | -0.00015298 | -3.834e-05 | 6.5222e-09 | -2.453e-06 | 0.0002313 | 0.00023215 | 0.00023215 | 0.98058 | -0.13915 | 0.98053 | -0.13948 | 0.085982
113 | 0.0014739 | 0.00036392 | -0.0014726 | -0.0003685 | 1.2539e-06 | -4.5854e-06 | 0.0022347 | 0.0022365 | 0.0022365 | 0.98058 | -0.13915 | 0.97972 | -0.1454 | 0.82832
114 | -0.0024392 | -0.00060162 | 0.0024396 | 0.00060118 | 4.0406e-07 | -4.4298e-07 | 0.0036966 | 0.0036964 | 0.0036966 | 0.98097 | -0.13622 | 0.98114 | -0.13498 | 1.3691
115 | 0.0018838 | 0.0004719 | -0.0018837 | -0.0004721 | 9.0242e-08 | -2.0036e-07 | 0.0028219 | 0.002822 | 0.002822 | 0.99332 | -0.047157 | 0.99327 | -0.047503 | 1.0452
116 | 0.0011868 | 0.00029687 | -0.0011868 | -0.00029706 | 3.2135e-08 | -1.8726e-07 | 0.0018024 | 0.0018024 | 0.0018024 | 0.97972 | -0.1454 | 0.97969 | -0.14559 | 0.66757
117 | 0.00087988 | 0.00022014 | -0.00087987 | -0.00022024 | 9.4679e-09 | -1.0335e-07 | 0.0013363 | 0.0013363 | 0.0013363 | 0.97969 | -0.14559 | 0.97968 | -0.14567 | 0.49493

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.057062 | 0.014076

## res_load
| p_mw | q_mvar
0 | 0.0020095 | 0.00050363
1 | 0.0018886 | 0.00047333
2 | 0.0019923 | 0.00049932
3 | 0.00014596 | 3.6581e-05
4 | 0.00031798 | 7.9694e-05
5 | 0.0019435 | 0.00048708
6 | 0.00028487 | 7.1394e-05
7 | 0.00034428 | 8.6285e-05
8 | 0.00037254 | 9.3368e-05
9 | 0.00027905 | 6.9935e-05
10 | 0.001965 | 0.00049247
11 | 0.00045908 | 0.00011506
12 | 0.00034434 | 8.63e-05
13 | 0.00017938 | 4.4956e-05
14 | 0.00048135 | 0.00012064
15 | 0.00021922 | 5.4943e-05
16 | 0.0018681 | 0.00046819
17 | 0.00053081 | 0.00013303
18 | 0.00047675 | 0.00011949
19 | 0.00028504 | 7.1438e-05
20 | 0.0017734 | 0.00044445
21 | 0.0019114 | 0.00047905
22 | 0.00076153 | 0.00019086
23 | 0.00030166 | 7.5602e-05
24 | 0.0009379 | 0.00023506
25 | 0.00024957 | 6.2548e-05
26 | 0.00078083 | 0.0001957
27 | 0.00027976 | 7.0115e-05
28 | 0.00068627 | 0.000172
29 | 0.00049697 | 0.00012455
30 | 0.00184 | 0.00046114
31 | 0.00021899 | 5.4884e-05
32 | 0.00018406 | 4.6129e-05
33 | 0.0003763 | 9.4309e-05
34 | 0.0011769 | 0.00029497
35 | 0.00013058 | 3.2726e-05
36 | 0.00015018 | 3.764e-05
37 | 0.00074903 | 0.00018773
38 | 0.00064129 | 0.00016072
39 | 0.00098793 | 0.0002476
40 | 0.00037537 | 9.4077e-05
41 | 0.0013236 | 0.00033172
42 | 0.00088166 | 0.00022096
43 | 0.00034295 | 8.5951e-05
44 | 0.00147 | 0.00036841
45 | 0.0021203 | 0.0005314
46 | 0.00047559 | 0.00011919
47 | 0.00014043 | 3.5194e-05
48 | 7.3679e-05 | 1.8466e-05
49 | 0.0008951 | 0.00022433
50 | 7.205e-05 | 1.8057e-05
51 | 0.00069886 | 0.00017515
52 | 0.00028109 | 7.0448e-05
53 | 0.00028984 | 7.2641e-05
54 | 0.00060259 | 0.00015102
55 | 0.00033342 | 8.3564e-05
56 | 0.0012655 | 0.00031716
57 | 0.00061153 | 0.00015326
58 | 0.00026832 | 6.7248e-05
59 | 0.0005901 | 0.00014789
60 | 0.0014306 | 0.00035853
61 | 0.00074454 | 0.0001866
62 | 0.0005025 | 0.00012594
63 | 0.00072003 | 0.00018046
64 | 0.00067955 | 0.00017031
65 | 0.0019908 | 0.00049895
66 | 0.00027031 | 6.7747e-05
67 | 0.00014935 | 3.7431e-05
68 | 0.00034809 | 8.724e-05
69 | 8.4676e-05 | 2.1222e-05
70 | 0.00059488 | 0.00014909
71 | 0.00060456 | 0.00015152
72 | 0.00020706 | 5.1895e-05
73 | 0.00028633 | 7.1761e-05
74 | 0.0018837 | 0.0004721
75 | 0.00015298 | 3.834e-05
76 | 0.00028582 | 7.1633e-05
77 | 0.00030691 | 7.6919e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1