## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2306-4_1_3_node_4 | 0.4 | n |  | TRUE
1 | bus_LV_2306-4_1_3_node_5 | 0.4 | n |  | TRUE
2 | bus_LV_2306-4_1_3_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_2306-4_1_3_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_2306-4_1_3_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_2306-4_1_3_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_2306-4_1_3_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_2306-4_1_3_node_202 | 0.4 | n |  | TRUE
8 | bus_LV_2306-4_1_3_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_2306-4_1_3_node_38 | 0.4 | n |  | TRUE
10 | bus_LV_2306-4_1_3_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_2306-4_1_3_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_2306-4_1_3_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_2306-4_1_3_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_2306-4_1_3_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_2306-4_1_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_2306-4_1_3_node_87 | 0.4 | n |  | TRUE
17 | bus_LV_2306-4_1_3_node_90 | 0.4 | n |  | TRUE
18 | bus_LV_2306-4_1_3_node_85 | 0.4 | n |  | TRUE
19 | bus_LV_2306-4_1_3_node_201 | 0.4 | n |  | TRUE
20 | bus_LV_2306-4_1_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2306-4_1_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2306-4_1_3_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_2306-4_1_3_node_60 | 0.4 | n |  | TRUE
24 | bus_LV_2306-4_1_3_node_59 | 0.4 | n |  | TRUE
25 | bus_LV_2306-4_1_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_2306-4_1_3_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_2306-4_1_3_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_2306-4_1_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_2306-4_1_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2306-4_1_3_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_2306-4_1_3_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_2306-4_1_3_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_2306-4_1_3_node_41 | 0.4 | n |  | TRUE
34 | bus_LV_2306-4_1_3_node_40 | 0.4 | n |  | TRUE
35 | bus_LV_2306-4_1_3_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_2306-4_1_3_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_2306-4_1_3_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_2306-4_1_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2306-4_1_3_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_2306-4_1_3_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_2306-4_1_3_node_198 | 0.4 | n |  | TRUE
42 | bus_LV_2306-4_1_3_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_2306-4_1_3_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_2306-4_1_3_node_199 | 0.4 | n |  | TRUE
45 | bus_LV_2306-4_1_3_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_2306-4_1_3_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_2306-4_1_3_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_2306-4_1_3_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_2306-4_1_3_node_205 | 0.4 | n |  | TRUE
50 | bus_LV_2306-4_1_3_node_203 | 0.4 | n |  | TRUE
51 | bus_LV_2306-4_1_3_node_163 | 0.4 | n |  | TRUE
52 | bus_LV_2306-4_1_3_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_2306-4_1_3_node_204 | 0.4 | n |  | TRUE
54 | bus_LV_2306-4_1_3_node_68 | 0.4 | n |  | TRUE
55 | bus_LV_2306-4_1_3_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_2306-4_1_3_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_2306-4_1_3_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_2306-4_1_3_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_2306-4_1_3_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_2306-4_1_3_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_2306-4_1_3_node_58 | 0.4 | n |  | TRUE
62 | bus_LV_2306-4_1_3_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_2306-4_1_3_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_2306-4_1_3_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_2306-4_1_3_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_2306-4_1_3_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_2306-4_1_3_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_2306-4_1_3_node_81 | 0.4 | n |  | TRUE
69 | bus_LV_2306-4_1_3_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_2306-4_1_3_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_2306-4_1_3_node_78 | 0.4 | n |  | TRUE
72 | bus_LV_2306-4_1_3_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_2306-4_1_3_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_2306-4_1_3_node_152 | 0.4 | n |  | TRUE
75 | bus_LV_2306-4_1_3_node_151 | 0.4 | n |  | TRUE
76 | bus_LV_2306-4_1_3_node_164 | 0.4 | n |  | TRUE
77 | bus_LV_2306-4_1_3_node_149 | 0.4 | n |  | TRUE
78 | bus_LV_2306-4_1_3_node_150 | 0.4 | n |  | TRUE
79 | bus_LV_2306-4_1_3_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_2306-4_1_3_node_69 | 0.4 | n |  | TRUE
81 | bus_LV_2306-4_1_3_node_208 | 0.4 | n |  | TRUE
82 | bus_LV_2306-4_1_3_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_2306-4_1_3_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_2306-4_1_3_node_70 | 0.4 | n |  | TRUE
85 | bus_LV_2306-4_1_3_node_79 | 0.4 | n |  | TRUE
86 | bus_LV_2306-4_1_3_node_171 | 0.4 | n |  | TRUE
87 | bus_LV_2306-4_1_3_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_2306-4_1_3_node_72 | 0.4 | n |  | TRUE
89 | bus_LV_2306-4_1_3_node_168 | 0.4 | n |  | TRUE
90 | bus_LV_2306-4_1_3_node_71 | 0.4 | n |  | TRUE
91 | bus_LV_2306-4_1_3_node_166 | 0.4 | n |  | TRUE
92 | bus_LV_2306-4_1_3_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_2306-4_1_3_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_2306-4_1_3_node_80 | 0.4 | n |  | TRUE
95 | bus_LV_2306-4_1_3_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_2306-4_1_3_node_170 | 0.4 | n |  | TRUE
97 | bus_LV_2306-4_1_3_node_82 | 0.4 | n |  | TRUE
98 | bus_LV_2306-4_1_3_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_2306-4_1_3_node_88 | 0.4 | n |  | TRUE
100 | bus_LV_2306-4_1_3_node_161 | 0.4 | n |  | TRUE
101 | bus_LV_2306-4_1_3_node_156 | 0.4 | n |  | TRUE
102 | bus_LV_2306-4_1_3_node_89 | 0.4 | n |  | TRUE
103 | bus_LV_2306-4_1_3_node_148 | 0.4 | n |  | TRUE
104 | bus_LV_2306-4_1_3_node_159 | 0.4 | n |  | TRUE
105 | bus_LV_2306-4_1_3_node_155 | 0.4 | n |  | TRUE
106 | bus_LV_2306-4_1_3_node_153 | 0.4 | n |  | TRUE
107 | bus_LV_2306-4_1_3_node_144 | 0.4 | n |  | TRUE
108 | bus_LV_2306-4_1_3_node_145 | 0.4 | n |  | TRUE
109 | bus_LV_2306-4_1_3_node_146 | 0.4 | n |  | TRUE
110 | bus_LV_2306-4_1_3_node_154 | 0.4 | n |  | TRUE
111 | bus_LV_2306-4_1_3_node_157 | 0.4 | n |  | TRUE
112 | bus_LV_2306-4_1_3_node_162 | 0.4 | n |  | TRUE
113 | bus_LV_2306-4_1_3_node_165 | 0.4 | n |  | TRUE
114 | bus_LV_2306-4_1_3_node_160 | 0.4 | n |  | TRUE
115 | bus_LV_2306-4_1_3_node_158 | 0.4 | n |  | TRUE
116 | bus_LV_2306-4_1_3_node_167 | 0.4 | n |  | TRUE
117 | bus_LV_2306-4_1_3_node_169 | 0.4 | n |  | TRUE
118 | bus_LV_2306-4_1_3_node_179 | 0.4 | n |  | TRUE
119 | bus_LV_2306-4_1_3_node_181 | 0.4 | n |  | TRUE
120 | bus_LV_2306-4_1_3_node_177 | 0.4 | n |  | TRUE
121 | bus_LV_2306-4_1_3_node_172 | 0.4 | n |  | TRUE
122 | bus_LV_2306-4_1_3_node_173 | 0.4 | n |  | TRUE
123 | bus_LV_2306-4_1_3_node_174 | 0.4 | n |  | TRUE
124 | bus_LV_2306-4_1_3_node_175 | 0.4 | n |  | TRUE
125 | bus_LV_2306-4_1_3_node_176 | 0.4 | n |  | TRUE
126 | bus_LV_2306-4_1_3_node_180 | 0.4 | n |  | TRUE
127 | bus_LV_2306-4_1_3_node_196 | 0.4 | n |  | TRUE
128 | bus_LV_2306-4_1_3_node_193 | 0.4 | n |  | TRUE
129 | bus_LV_2306-4_1_3_node_178 | 0.4 | n |  | TRUE
130 | bus_LV_2306-4_1_3_node_191 | 0.4 | n |  | TRUE
131 | bus_LV_2306-4_1_3_node_190 | 0.4 | n |  | TRUE
132 | bus_LV_2306-4_1_3_node_188 | 0.4 | n |  | TRUE
133 | bus_LV_2306-4_1_3_node_182 | 0.4 | n |  | TRUE
134 | bus_LV_2306-4_1_3_node_183 | 0.4 | n |  | TRUE
135 | bus_LV_2306-4_1_3_node_184 | 0.4 | n |  | TRUE
136 | bus_LV_2306-4_1_3_node_185 | 0.4 | n |  | TRUE
137 | bus_LV_2306-4_1_3_node_197 | 0.4 | n |  | TRUE
138 | bus_LV_2306-4_1_3_node_189 | 0.4 | n |  | TRUE
139 | bus_LV_2306-4_1_3_node_186 | 0.4 | n |  | TRUE
140 | bus_LV_2306-4_1_3_node_187 | 0.4 | n |  | TRUE
141 | bus_LV_2306-4_1_3_node_192 | 0.4 | n |  | TRUE
142 | bus_LV_2306-4_1_3_node_194 | 0.4 | n |  | TRUE
143 | bus_LV_2306-4_1_3_node_195 | 0.4 | n |  | TRUE
144 | bus_LV_2306-4_1_3_node_200 | 0.4 | n |  | TRUE
145 | bus_MV_119_1_node_182 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2306-4_1_3_load_4 | 0 | 0.00056216 | 0.00014089 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2306-4_1_3_load_5 | 1 | 0.00019319 | 4.8418e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2306-4_1_3_load_6 | 2 | 0.00046356 | 0.00011618 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2306-4_1_3_load_13 | 5 | 0.00036453 | 9.136e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2306-4_1_3_load_202 | 7 | 0.00030959 | 7.759e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2306-4_1_3_load_9 | 8 | 0.00068236 | 0.00017102 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2306-4_1_3_load_38 | 9 | 0.00022792 | 5.7122e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2306-4_1_3_load_42 | 10 | 0.00037513 | 9.4016e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2306-4_1_3_load_33 | 11 | 0.00027617 | 6.9216e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2306-4_1_3_load_14 | 15 | 0.00034523 | 8.6523e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2306-4_1_3_load_90 | 17 | 0.00027735 | 6.951e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2306-4_1_3_load_85 | 18 | 0.00054368 | 0.00013626 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2306-4_1_3_load_15 | 20 | 0.0027091 | 0.00067896 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2306-4_1_3_load_17 | 21 | 0.00044104 | 0.00011054 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2306-4_1_3_load_24 | 22 | 0.00016651 | 4.1731e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2306-4_1_3_load_60 | 23 | 0.00062371 | 0.00015632 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2306-4_1_3_load_19 | 25 | 0.0011114 | 0.00027854 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2306-4_1_3_load_20 | 26 | 0.0001683 | 4.218e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2306-4_1_3_load_21 | 27 | 0.00014406 | 3.6105e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2306-4_1_3_load_39 | 31 | 0.00052694 | 0.00013206 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2306-4_1_3_load_41 | 33 | 9.2152e-05 | 2.3095e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2306-4_1_3_load_40 | 34 | 0.00095754 | 0.00023998 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2306-4_1_3_load_28 | 35 | 0.00013811 | 3.4613e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2306-4_1_3_load_27 | 36 | 0.00085977 | 0.00021548 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2306-4_1_3_load_34 | 40 | 8.731e-05 | 2.1882e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2306-4_1_3_load_198 | 41 | 0.00064043 | 0.00016051 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2306-4_1_3_load_35 | 42 | 0.0011482 | 0.00028776 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2306-4_1_3_load_36 | 43 | 0.0011586 | 0.00029037 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2306-4_1_3_load_199 | 44 | 0.00011751 | 2.9452e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2306-4_1_3_load_43 | 45 | 0.0051168 | 0.0012824 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2306-4_1_3_load_205 | 49 | 0.0064864 | 0.0016256 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2306-4_1_3_load_203 | 50 | 0.00031613 | 7.923e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2306-4_1_3_load_163 | 51 | 0.001287 | 0.00032255 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2306-4_1_3_load_62 | 52 | 0.0014853 | 0.00037224 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2306-4_1_3_load_204 | 53 | 0.0017059 | 0.00042755 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2306-4_1_3_load_47 | 56 | 0.0043541 | 0.0010912 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2306-4_1_3_load_48 | 57 | 0.0026823 | 0.00067225 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2306-4_1_3_load_56 | 60 | 0.00037875 | 9.4925e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2306-4_1_3_load_57 | 62 | 0.0024748 | 0.00062024 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2306-4_1_3_load_50 | 63 | 0.00060077 | 0.00015057 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2306-4_1_3_load_51 | 64 | 0.0014867 | 0.0003726 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2306-4_1_3_load_52 | 65 | 0.001124 | 0.00028169 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2306-4_1_3_load_81 | 68 | 0.00052722 | 0.00013213 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2306-4_1_3_load_65 | 69 | 0.0015696 | 0.00039338 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2306-4_1_3_load_63 | 70 | 0.00070112 | 0.00017572 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2306-4_1_3_load_64 | 73 | 0.0010369 | 0.00025988 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2306-4_1_3_load_151 | 75 | 0.00083799 | 0.00021002 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2306-4_1_3_load_164 | 76 | 0.0023368 | 0.00058566 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2306-4_1_3_load_150 | 78 | 0.0049114 | 0.0012309 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2306-4_1_3_load_208 | 81 | 0.0010626 | 0.00026632 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2306-4_1_3_load_73 | 83 | 0.0020113 | 0.00050407 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2306-4_1_3_load_70 | 84 | 0.00035236 | 8.8311e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2306-4_1_3_load_77 | 87 | 0.00073649 | 0.00018458 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2306-4_1_3_load_72 | 88 | 0.00072461 | 0.00018161 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2306-4_1_3_load_71 | 90 | 0.0011065 | 0.00027731 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2306-4_1_3_load_166 | 91 | 0.0002141 | 5.3658e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2306-4_1_3_load_75 | 92 | 0.00077116 | 0.00019327 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2306-4_1_3_load_76 | 93 | 0.00099125 | 0.00024843 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2306-4_1_3_load_80 | 94 | 0.0051004 | 0.0012783 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2306-4_1_3_load_83 | 95 | 0.0011864 | 0.00029733 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2306-4_1_3_load_170 | 96 | 0.001749 | 0.00043834 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2306-4_1_3_load_82 | 97 | 0.00033345 | 8.3571e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2306-4_1_3_load_161 | 100 | 0.0018511 | 0.00046393 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2306-4_1_3_load_156 | 101 | 0.00083637 | 0.00020961 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2306-4_1_3_load_148 | 103 | 0.00082077 | 0.0002057 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2306-4_1_3_load_159 | 104 | 0.0006659 | 0.00016689 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2306-4_1_3_load_153 | 106 | 0.0014139 | 0.00035437 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2306-4_1_3_load_144 | 107 | 0.0021784 | 0.00054595 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2306-4_1_3_load_145 | 108 | 0.00025441 | 6.3761e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2306-4_1_3_load_146 | 109 | 0.00030652 | 7.6821e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2306-4_1_3_load_154 | 110 | 0.0011962 | 0.00029979 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2306-4_1_3_load_157 | 111 | 0.00059866 | 0.00015004 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2306-4_1_3_load_162 | 112 | 0.00046654 | 0.00011693 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2306-4_1_3_load_165 | 113 | 0.00083899 | 0.00021027 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2306-4_1_3_load_160 | 114 | 0.00065965 | 0.00016532 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2306-4_1_3_load_158 | 115 | 0.00059877 | 0.00015007 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2306-4_1_3_load_167 | 116 | 0.00025965 | 6.5075e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2306-4_1_3_load_169 | 117 | 0.00027013 | 6.7702e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2306-4_1_3_load_181 | 119 | 0.0018202 | 0.0004562 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2306-4_1_3_load_177 | 120 | 0.0010965 | 0.0002748 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2306-4_1_3_load_172 | 121 | 0.0015292 | 0.00038325 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2306-4_1_3_load_173 | 122 | 0.00045991 | 0.00011526 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2306-4_1_3_load_174 | 123 | 0.00051951 | 0.0001302 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2306-4_1_3_load_175 | 124 | 0.00017302 | 4.3362e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2306-4_1_3_load_180 | 126 | 0.00015785 | 3.9561e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2306-4_1_3_load_196 | 127 | 0.00038463 | 9.6397e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2306-4_1_3_load_193 | 128 | 0.0010859 | 0.00027215 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2306-4_1_3_load_178 | 129 | 0.00030568 | 7.661e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2306-4_1_3_load_191 | 130 | 0.00027646 | 6.9288e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2306-4_1_3_load_190 | 131 | 0.00021163 | 5.3039e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2306-4_1_3_load_188 | 132 | 0.00049246 | 0.00012342 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2306-4_1_3_load_182 | 133 | 0.0012096 | 0.00030315 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2306-4_1_3_load_183 | 134 | 0.0034657 | 0.00086858 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2306-4_1_3_load_197 | 137 | 0.00034202 | 8.5717e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2306-4_1_3_load_189 | 138 | 0.00033484 | 8.3918e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2306-4_1_3_load_186 | 139 | 0.0013949 | 0.0003496 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2306-4_1_3_load_187 | 140 | 0.00013734 | 3.442e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2306-4_1_3_load_192 | 141 | 0.00029463 | 7.3841e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2306-4_1_3_load_194 | 142 | 0.0004433 | 0.0001111 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2306-4_1_3_load_195 | 143 | 0.0012032 | 0.00030154 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 88 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2306-4_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.014793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2306-4_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.045291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2306-4_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.032458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2306-4_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.17756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2306-4_1_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.011934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2306-4_1_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.027488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2306-4_1_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.04763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2306-4_1_3_line_7 | NAYY 4x150 SE | 7 | 19 | 0.065678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2306-4_1_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.29145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2306-4_1_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.41174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2306-4_1_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.0047764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2306-4_1_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.16105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2306-4_1_3_line_12 | NAYY 4x150 SE | 11 | 22 | 0.0028118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2306-4_1_3_line_13 | NAYY 4x150 SE | 12 | 30 | 0.015117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2306-4_1_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.014169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2306-4_1_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.097068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2306-4_1_3_line_16 | NAYY 4x150 SE | 14 | 23 | 0.05831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2306-4_1_3_line_17 | NAYY 4x150 SE | 15 | 20 | 0.006646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2306-4_1_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.010362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2306-4_1_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.016782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2306-4_1_3_line_20 | NAYY 4x150 SE | 18 | 98 | 0.12592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2306-4_1_3_line_21 | NAYY 4x150 SE | 19 | 144 | 0.024101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2306-4_1_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.024004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2306-4_1_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.0059972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2306-4_1_3_line_24 | NAYY 4x150 SE | 23 | 24 | 0.23824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_2306-4_1_3_line_25 | NAYY 4x150 SE | 24 | 53 | 0.24216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_2306-4_1_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.011491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2306-4_1_3_line_27 | NAYY 4x150 SE | 25 | 27 | 0.0011027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2306-4_1_3_line_28 | NAYY 4x150 SE | 26 | 28 | 0.010119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2306-4_1_3_line_29 | NAYY 4x150 SE | 27 | 29 | 0.028687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2306-4_1_3_line_30 | NAYY 4x150 SE | 28 | 30 | 0.017194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2306-4_1_3_line_31 | NAYY 4x150 SE | 29 | 31 | 0.016136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2306-4_1_3_line_32 | NAYY 4x150 SE | 29 | 32 | 0.033508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2306-4_1_3_line_33 | NAYY 4x150 SE | 30 | 33 | 0.012309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2306-4_1_3_line_34 | NAYY 4x150 SE | 31 | 34 | 0.0050397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2306-4_1_3_line_35 | NAYY 4x150 SE | 32 | 35 | 0.0084689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2306-4_1_3_line_36 | NAYY 4x150 SE | 35 | 36 | 0.011278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2306-4_1_3_line_37 | NAYY 4x150 SE | 36 | 37 | 0.053731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2306-4_1_3_line_38 | NAYY 4x150 SE | 37 | 38 | 0.041576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2306-4_1_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.18075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2306-4_1_3_line_40 | NAYY 4x150 SE | 38 | 40 | 0.012913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2306-4_1_3_line_41 | NAYY 4x150 SE | 39 | 41 | 0.092125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2306-4_1_3_line_42 | NAYY 4x150 SE | 40 | 42 | 0.00092756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2306-4_1_3_line_43 | NAYY 4x150 SE | 41 | 44 | 0.049913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2306-4_1_3_line_44 | NAYY 4x150 SE | 42 | 43 | 0.02545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2306-4_1_3_line_45 | NAYY 4x150 SE | 44 | 144 | 0.23269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2306-4_1_3_line_46 | NAYY 4x150 SE | 45 | 46 | 0.010231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2306-4_1_3_line_47 | NAYY 4x150 SE | 46 | 47 | 0.067707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_2306-4_1_3_line_48 | NAYY 4x150 SE | 46 | 48 | 0.11417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_2306-4_1_3_line_49 | NAYY 4x150 SE | 47 | 49 | 0.021814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2306-4_1_3_line_50 | NAYY 4x150 SE | 47 | 50 | 0.018294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_2306-4_1_3_line_51 | NAYY 4x150 SE | 48 | 51 | 0.020671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_2306-4_1_3_line_52 | NAYY 4x150 SE | 48 | 52 | 0.015015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2306-4_1_3_line_53 | NAYY 4x150 SE | 50 | 53 | 0.043773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_2306-4_1_3_line_54 | NAYY 4x150 SE | 51 | 54 | 0.0094923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_2306-4_1_3_line_55 | NAYY 4x150 SE | 52 | 55 | 0.036014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2306-4_1_3_line_56 | NAYY 4x150 SE | 54 | 82 | 0.01247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_2306-4_1_3_line_57 | NAYY 4x150 SE | 55 | 60 | 0.016928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2306-4_1_3_line_58 | NAYY 4x150 SE | 56 | 57 | 0.0095446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2306-4_1_3_line_59 | NAYY 4x150 SE | 57 | 58 | 0.023491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2306-4_1_3_line_60 | NAYY 4x150 SE | 58 | 59 | 0.026441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2306-4_1_3_line_61 | NAYY 4x150 SE | 58 | 60 | 0.033145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2306-4_1_3_line_62 | NAYY 4x150 SE | 59 | 61 | 0.041637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2306-4_1_3_line_63 | NAYY 4x150 SE | 59 | 62 | 0.028529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2306-4_1_3_line_64 | NAYY 4x150 SE | 61 | 74 | 0.010401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2306-4_1_3_line_65 | NAYY 4x150 SE | 61 | 75 | 0.010246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2306-4_1_3_line_66 | NAYY 4x150 SE | 63 | 64 | 0.033749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2306-4_1_3_line_67 | NAYY 4x150 SE | 63 | 65 | 0.0023109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2306-4_1_3_line_68 | NAYY 4x150 SE | 64 | 66 | 0.13619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2306-4_1_3_line_69 | NAYY 4x150 SE | 65 | 67 | 0.021563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2306-4_1_3_line_70 | NAYY 4x150 SE | 66 | 68 | 0.048281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2306-4_1_3_line_71 | NAYY 4x150 SE | 67 | 69 | 0.051644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2306-4_1_3_line_72 | NAYY 4x150 SE | 67 | 70 | 0.019188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2306-4_1_3_line_73 | NAYY 4x150 SE | 68 | 71 | 0.020205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2306-4_1_3_line_74 | NAYY 4x150 SE | 69 | 72 | 0.02141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2306-4_1_3_line_75 | NAYY 4x150 SE | 70 | 73 | 0.012882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2306-4_1_3_line_76 | NAYY 4x150 SE | 71 | 94 | 0.004026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2306-4_1_3_line_77 | NAYY 4x150 SE | 71 | 93 | 0.038422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2306-4_1_3_line_78 | NAYY 4x150 SE | 72 | 79 | 0.01876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2306-4_1_3_line_79 | NAYY 4x150 SE | 72 | 80 | 0.092216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2306-4_1_3_line_80 | NAYY 4x150 SE | 74 | 76 | 0.016539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2306-4_1_3_line_81 | NAYY 4x150 SE | 74 | 77 | 0.029863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2306-4_1_3_line_82 | NAYY 4x150 SE | 75 | 78 | 0.019864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2306-4_1_3_line_83 | NAYY 4x150 SE | 76 | 113 | 0.017584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2306-4_1_3_line_84 | NAYY 4x150 SE | 77 | 106 | 0.012807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2306-4_1_3_line_85 | NAYY 4x150 SE | 77 | 102 | 0.009239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2306-4_1_3_line_86 | NAYY 4x150 SE | 79 | 81 | 0.047949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2306-4_1_3_line_87 | NAYY 4x150 SE | 80 | 83 | 0.2092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2306-4_1_3_line_88 | NAYY 4x150 SE | 80 | 84 | 0.011819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2306-4_1_3_line_89 | NAYY 4x150 SE | 82 | 88 | 0.022924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_2306-4_1_3_line_90 | NAYY 4x150 SE | 83 | 89 | 0.0095605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2306-4_1_3_line_91 | NAYY 4x150 SE | 84 | 90 | 0.020573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2306-4_1_3_line_92 | NAYY 4x150 SE | 85 | 86 | 0.21342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2306-4_1_3_line_93 | NAYY 4x150 SE | 85 | 87 | 0.13099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2306-4_1_3_line_94 | NAYY 4x150 SE | 86 | 96 | 0.070099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2306-4_1_3_line_95 | NAYY 4x150 SE | 87 | 92 | 0.0078906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2306-4_1_3_line_96 | NAYY 4x150 SE | 88 | 90 | 0.05968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2306-4_1_3_line_97 | NAYY 4x150 SE | 89 | 91 | 0.03479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2306-4_1_3_line_98 | NAYY 4x150 SE | 91 | 116 | 0.1553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2306-4_1_3_line_99 | NAYY 4x150 SE | 92 | 93 | 0.0051674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2306-4_1_3_line_100 | NAYY 4x150 SE | 94 | 95 | 0.022958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2306-4_1_3_line_101 | NAYY 4x150 SE | 95 | 97 | 0.031994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2306-4_1_3_line_102 | NAYY 4x150 SE | 98 | 99 | 0.055913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2306-4_1_3_line_103 | NAYY 4x150 SE | 99 | 100 | 0.025474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2306-4_1_3_line_104 | NAYY 4x150 SE | 99 | 101 | 0.019663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2306-4_1_3_line_105 | NAYY 4x150 SE | 100 | 104 | 0.028362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2306-4_1_3_line_106 | NAYY 4x150 SE | 101 | 105 | 0.029336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2306-4_1_3_line_107 | NAYY 4x150 SE | 102 | 103 | 0.027017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2306-4_1_3_line_108 | NAYY 4x150 SE | 104 | 115 | 0.026316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2306-4_1_3_line_109 | NAYY 4x150 SE | 105 | 110 | 0.057246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2306-4_1_3_line_110 | NAYY 4x150 SE | 105 | 111 | 0.014731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2306-4_1_3_line_111 | NAYY 4x150 SE | 106 | 112 | 0.0053001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2306-4_1_3_line_112 | NAYY 4x150 SE | 107 | 108 | 0.022363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2306-4_1_3_line_113 | NAYY 4x150 SE | 108 | 109 | 0.0059518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2306-4_1_3_line_114 | NAYY 4x150 SE | 109 | 110 | 0.023871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2306-4_1_3_line_115 | NAYY 4x150 SE | 112 | 114 | 0.0094016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2306-4_1_3_line_116 | NAYY 4x150 SE | 114 | 115 | 0.013805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2306-4_1_3_line_117 | NAYY 4x150 SE | 116 | 117 | 0.14323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2306-4_1_3_line_118 | NAYY 4x150 SE | 117 | 118 | 0.045928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2306-4_1_3_line_119 | NAYY 4x150 SE | 118 | 119 | 0.020604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2306-4_1_3_line_120 | NAYY 4x150 SE | 118 | 120 | 0.081007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2306-4_1_3_line_121 | NAYY 4x150 SE | 119 | 131 | 0.052434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2306-4_1_3_line_122 | NAYY 4x150 SE | 120 | 129 | 0.0038867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2306-4_1_3_line_123 | NAYY 4x150 SE | 121 | 122 | 0.0038911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2306-4_1_3_line_124 | NAYY 4x150 SE | 121 | 123 | 0.0073244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_2306-4_1_3_line_125 | NAYY 4x150 SE | 122 | 124 | 0.02505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_2306-4_1_3_line_126 | NAYY 4x150 SE | 123 | 125 | 0.010737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_2306-4_1_3_line_127 | NAYY 4x150 SE | 124 | 126 | 0.0023158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_2306-4_1_3_line_128 | NAYY 4x150 SE | 125 | 127 | 0.039178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_2306-4_1_3_line_129 | NAYY 4x150 SE | 125 | 128 | 0.011338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_2306-4_1_3_line_130 | NAYY 4x150 SE | 126 | 129 | 0.019051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_2306-4_1_3_line_131 | NAYY 4x150 SE | 128 | 130 | 0.14951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_2306-4_1_3_line_132 | NAYY 4x150 SE | 130 | 141 | 0.012314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_2306-4_1_3_line_133 | NAYY 4x150 SE | 131 | 132 | 0.0058056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_2306-4_1_3_line_134 | NAYY 4x150 SE | 132 | 139 | 0.0050951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_2306-4_1_3_line_135 | NAYY 4x150 SE | 133 | 134 | 0.036169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_2306-4_1_3_line_136 | NAYY 4x150 SE | 133 | 135 | 0.012054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_2306-4_1_3_line_137 | NAYY 4x150 SE | 135 | 136 | 0.034625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_2306-4_1_3_line_138 | NAYY 4x150 SE | 136 | 137 | 0.010192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_2306-4_1_3_line_139 | NAYY 4x150 SE | 137 | 138 | 0.031884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_2306-4_1_3_line_140 | NAYY 4x150 SE | 138 | 140 | 0.16926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_2306-4_1_3_line_141 | NAYY 4x150 SE | 139 | 140 | 0.0027701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_2306-4_1_3_line_142 | NAYY 4x150 SE | 141 | 142 | 0.018526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_2306-4_1_3_line_143 | NAYY 4x150 SE | 142 | 143 | 0.045742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2306-4_1_3_trafo_72 | 0.25 MVA 20/0.4 kV | 145 | 88 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2584285.3753 | 1182131.545 | 2584281.3142 | 1182128.7712 | 2584276.4352 | 1182125.8937 | 2584272.9244 | 1182123.5684
1 | 2584285.3753 | 1182131.545 | 2584286.1944 | 1182132.1045 | 2584297.6019 | 1182140.8345 | 2584309.1595 | 1182148.6303 | 2584317.9664 | 1182152.7537 | 2584323.9409 | 1182154.6506
2 | 2584269.2449 | 1182092.0397 | 2584268.8269 | 1182098.5664 | 2584268.6777 | 1182111.4734 | 2584270.6401 | 1182120.1727 | 2584272.9244 | 1182123.5684
3 | 2584496.1446 | 1182193.1419 | 2584478.6004 | 1182190.9308 | 2584461.3556 | 1182189.3416 | 2584455.6653 | 1182188.5783 | 2584449.508 | 1182187.3492 | 2584441.6914 | 1182185.2019 | 2584434.0255 | 1182182.2982 | 2584423.2254 | 1182177.9797 | 2584412.122 | 1182174.4402 | 2584405.7885 | 1182173.0338 | 2584398.3713 | 1182171.797 | 2584386.931 | 1182170.8265 | 2584373.406 | 1182169.7836 | 2584366.0045 | 1182168.7136 | 2584357.3547 | 1182166.2461 | 2584341.3032 | 1182159.696 | 2584328.5579 | 1182156.1165 | 2584323.9409 | 1182154.6506
4 | 2584269.2449 | 1182092.0397 | 2584264.7732 | 1182084.4142 | 2584262.6745 | 1182082.1409
5 | 2584496.1446 | 1182193.1419 | 2584504.1722 | 1182197.1786 | 2584508.7971 | 1182202.2137 | 2584512.056 | 1182213.4443
6 | 2584512.056 | 1182213.4443 | 2584501.0965 | 1182227.0465 | 2584492.2002 | 1182235.4073 | 2584483.0254 | 1182242.3681 | 2584477.1247 | 1182244.9405
7 | 2584425.1009 | 1182282.0729 | 2584428.1038 | 1182277.0736 | 2584432.5258 | 1182271.6704 | 2584437.4662 | 1182265.999 | 2584443.7204 | 1182260.4687 | 2584451.2738 | 1182255.4464 | 2584460.2196 | 1182251.4766 | 2584470.0449 | 1182248.027 | 2584477.1247 | 1182244.9405
8 | 2583588.0315 | 1183098.8069 | 2583312.8507 | 1183002.8013
9 | 2583886.0112 | 1182814.6627 | 2583588.0315 | 1183098.8069
10 | 2583588.0315 | 1183098.8069 | 2583587.0295 | 1183103.477
11 | 2583993.0191 | 1182749.9256 | 2583984.7575 | 1182738.2306 | 2583977.8607 | 1182734.3916 | 2583965.4145 | 1182730.9121 | 2583951.4736 | 1182730.9497 | 2583937.3712 | 1182736.1792 | 2583922.4515 | 1182746.9361 | 2583912.7329 | 1182758.346 | 2583907.3948 | 1182771.9341 | 2583905.0723 | 1182782.657 | 2583899.2204 | 1182792.5557 | 2583890.8405 | 1182802.1166 | 2583886.1603 | 1182810.5114 | 2583886.0112 | 1182814.6627
12 | 2583587.0295 | 1183103.477 | 2583586.4396 | 1183106.2263 | 2583586.4396 | 1183106.2263
13 | 2584008.0932 | 1182748.3065 | 2583993.0191 | 1182749.9256
14 | 2583532.0459 | 1183225.0155 | 2583534.7257 | 1183238.9264
15 | 2583532.0459 | 1183225.0155 | 2583536.7114 | 1183214.3638 | 2583568.7927 | 1183154.4999 | 2583580.7506 | 1183141.6936 | 2583580.7506 | 1183141.6936
16 | 2583534.7257 | 1183238.9264 | 2583543.4026 | 1183268.251 | 2583549.655 | 1183276.5936 | 2583560.4516 | 1183280.1434 | 2583566.3888 | 1183280.2528
17 | 2583580.7506 | 1183141.6936 | 2583583.54 | 1183135.6613
18 | 2583707.1197 | 1183647.3419 | 2583703.6121 | 1183637.5909
19 | 2583703.6121 | 1183637.5909 | 2583720.2556 | 1183635.4407
20 | 2583845.1339 | 1183619.3074 | 2583720.2556 | 1183635.4407
21 | 2584411.2488 | 1182301.8193 | 2584425.1009 | 1182282.0729
22 | 2583586.4561 | 1183112.2234 | 2583586.4657 | 1183115.7089 | 2583586.0932 | 1183130.1396 | 2583583.54 | 1183135.6613
23 | 2583586.4561 | 1183112.2234 | 2583586.4396 | 1183106.2263
24 | 2583774.8223 | 1183344.923 | 2583766.4417 | 1183342.6558 | 2583754.8122 | 1183344.3439 | 2583745.2348 | 1183345.4817 | 2583735.2457 | 1183344.0304 | 2583720.9104 | 1183336.0765 | 2583652.6978 | 1183276.31 | 2583639.0094 | 1183267.7431 | 2583617.6832 | 1183266.1342 | 2583589.6655 | 1183274.0931 | 2583571.4757 | 1183280.3465 | 2583566.3888 | 1183280.2528
25 | 2584014.461 | 1183379.7981 | 2583774.8223 | 1183344.923
26 | 2584023.7186 | 1182776.8192 | 2584019.9683 | 1182775.1441 | 2584013.8636 | 1182770.9913
27 | 2584024.7254 | 1182777.2689 | 2584023.7186 | 1182776.8192
28 | 2584005.4972 | 1182765.3 | 2584013.8636 | 1182770.9913
29 | 2584050.9179 | 1182788.9683 | 2584024.7254 | 1182777.2689
30 | 2584008.0932 | 1182748.3065 | 2584005.4972 | 1182765.3
31 | 2584050.9179 | 1182788.9683 | 2584066.5279 | 1182793.0552
32 | 2584060.2377 | 1182756.7823 | 2584050.9179 | 1182788.9683
33 | 2584008.0932 | 1182748.3065 | 2584016.9264 | 1182739.7339
34 | 2584066.5279 | 1182793.0552 | 2584071.4032 | 1182794.3317
35 | 2584060.2377 | 1182756.7823 | 2584068.4136 | 1182758.9905
36 | 2584068.4136 | 1182758.9905 | 2584079.3015 | 1182761.931
37 | 2584132.1505 | 1182757.5909 | 2584103.9389 | 1182762.6909 | 2584088.4833 | 1182764.4108 | 2584079.3015 | 1182761.931
38 | 2584132.1505 | 1182757.5909 | 2584141.3844 | 1182756.0656 | 2584154.5623 | 1182753.3958 | 2584159.2974 | 1182748.2361 | 2584167.4668 | 1182739.7656
39 | 2584152.6347 | 1182562.5357 | 2584151.5699 | 1182575.5453 | 2584153.7816 | 1182589.013 | 2584173.1456 | 1182687.5013 | 2584175.0125 | 1182717.7453 | 2584172.7545 | 1182727.0895 | 2584167.4668 | 1182739.7656
40 | 2584167.4668 | 1182739.7656 | 2584180.3791 | 1182739.5907
41 | 2584152.6347 | 1182562.5357 | 2584160.7271 | 1182547.9511 | 2584181.648 | 1182531.1758 | 2584197.7665 | 1182511.434 | 2584203.7079 | 1182494.6985 | 2584206.8925 | 1182490.3568
42 | 2584181.3066 | 1182739.5781 | 2584180.3791 | 1182739.5907
43 | 2584206.8925 | 1182490.3568 | 2584218.6262 | 1182474.3596 | 2584236.8459 | 1182450.433
44 | 2584206.3352 | 1182742.7529 | 2584196.9065 | 1182739.9209 | 2584183.7968 | 1182739.5444 | 2584181.3066 | 1182739.5781
45 | 2584411.2488 | 1182301.8193 | 2584401.5062 | 1182313.4508 | 2584388.6982 | 1182326.58 | 2584379.624 | 1182333.9631 | 2584367.4028 | 1182340.832 | 2584341.8278 | 1182353.5168 | 2584315.2199 | 1182368.2833 | 2584294.4433 | 1182382.2229 | 2584270.5551 | 1182406.1649 | 2584236.8459 | 1182450.433
46 | 2584129.4561 | 1183396.9619 | 2584121.8607 | 1183402.7963 | 2584121.2408 | 1183403.0043
47 | 2584129.4561 | 1183396.9619 | 2584116.5061 | 1183392.961 | 2584092.9943 | 1183393.1238 | 2584073.9478 | 1183398.7887 | 2584067.1614 | 1183407.3668
48 | 2584129.4561 | 1183396.9619 | 2584140.4482 | 1183396.7326 | 2584168.8361 | 1183395.8455 | 2584178.3599 | 1183397.5211 | 2584182.0603 | 1183399.6457 | 2584184.5951 | 1183402.6405 | 2584185.2635 | 1183407.13 | 2584183.724 | 1183410.9805 | 2584175.9604 | 1183416.7152 | 2584149.7786 | 1183431.8592 | 2584147.991 | 1183439.9904
49 | 2584076.4746 | 1183421.6493 | 2584072.0169 | 1183421.8058 | 2584065.996 | 1183416.9193 | 2584067.1614 | 1183407.3668
50 | 2584067.1614 | 1183407.3668 | 2584048.9352 | 1183405.7925
51 | 2584147.991 | 1183439.9904 | 2584167.2649 | 1183432.5188
52 | 2584147.991 | 1183439.9904 | 2584134.6383 | 1183446.8567
53 | 2584048.9352 | 1183405.7925 | 2584048.9352 | 1183405.7925 | 2584031.1976 | 1183395.657 | 2584019.9337 | 1183382.7694 | 2584014.461 | 1183379.7981
54 | 2584176.1154 | 1183429.0878 | 2584167.2649 | 1183432.5188
55 | 2584103.7368 | 1183465.2769 | 2584123.2609 | 1183452.7073 | 2584134.6383 | 1183446.8567
56 | 2584185.9375 | 1183436.7324 | 2584182.9175 | 1183434.9839 | 2584176.1154 | 1183429.0878
57 | 2584103.7368 | 1183465.2769 | 2584094.1789 | 1183462.2342 | 2584087.4268 | 1183463.6418
58 | 2584039.4434 | 1183453.0168 | 2584045.011 | 1183460.7693
59 | 2584058.7138 | 1183479.8491 | 2584045.011 | 1183460.7693
60 | 2584039.5716 | 1183498.1431 | 2584058.7138 | 1183479.8491
61 | 2584058.7138 | 1183479.8491 | 2584075.8435 | 1183468.2974 | 2584087.4268 | 1183463.6418
62 | 2584039.5716 | 1183498.1431 | 2584035.6316 | 1183506.2912 | 2584026.9299 | 1183529.3487 | 2584027.7925 | 1183532.1923 | 2584031.3363 | 1183535.6957
63 | 2584039.5716 | 1183498.1431 | 2584017.921 | 1183479.5643
64 | 2584024.0202 | 1183543.1081 | 2584031.3363 | 1183535.6957
65 | 2584031.3363 | 1183535.6957 | 2584038.2556 | 1183543.2528
66 | 2584448.6804 | 1183372.0347 | 2584478.5597 | 1183356.3427
67 | 2584446.6345 | 1183373.1092 | 2584448.6804 | 1183372.0347
68 | 2584583.4625 | 1183270.0492 | 2584555.8487 | 1183295.9119 | 2584522.2771 | 1183326.248 | 2584482.7907 | 1183354.1206 | 2584478.5597 | 1183356.3427
69 | 2584427.5438 | 1183383.1352 | 2584446.6345 | 1183373.1092
70 | 2584583.4625 | 1183270.0492 | 2584563.953 | 1183235.8154 | 2584559.0941 | 1183228.3849
71 | 2584427.5438 | 1183383.1352 | 2584380.527 | 1183404.5017
72 | 2584427.5438 | 1183383.1352 | 2584417.0881 | 1183367.0465
73 | 2584546.3043 | 1183212.7492 | 2584558.6262 | 1183227.6694 | 2584559.0941 | 1183228.3849
74 | 2584360.5872 | 1183412.1255 | 2584368.6655 | 1183409.8921 | 2584380.527 | 1183404.5017
75 | 2584410.0683 | 1183356.2448 | 2584417.0881 | 1183367.0465
76 | 2584546.3043 | 1183212.7492 | 2584550.0535 | 1183211.2819
77 | 2584546.3043 | 1183212.7492 | 2584536.1599 | 1183213.2313 | 2584517.2505 | 1183207.4107 | 2584508.9701 | 1183209.2451
78 | 2584351.3912 | 1183395.7634 | 2584360.5872 | 1183412.1255
79 | 2584296.7385 | 1183455.7715 | 2584303.6013 | 1183438.3889 | 2584307.1622 | 1183419.4698 | 2584335.741 | 1183418.6386 | 2584360.5872 | 1183412.1255
80 | 2584024.0202 | 1183543.1081 | 2584009.8522 | 1183534.575
81 | 2584024.0202 | 1183543.1081 | 2584012.2106 | 1183554.3455 | 2584001.5232 | 1183562.7675
82 | 2584037.1688 | 1183560.2264 | 2584042.6365 | 1183553.697 | 2584038.4947 | 1183543.514 | 2584038.2556 | 1183543.2528
83 | 2583996.7921 | 1183546.3495 | 2584009.8522 | 1183534.575
84 | 2584001.5232 | 1183562.7675 | 2583996.7336 | 1183574.6455
85 | 2583993.8654 | 1183567.9685 | 2584001.5232 | 1183562.7675
86 | 2584351.3912 | 1183395.7634 | 2584385.3335 | 1183370.3946 | 2584386.548 | 1183364.8775
87 | 2584296.7385 | 1183455.7715 | 2584310.32 | 1183467.7753 | 2584321.478 | 1183481.2863 | 2584342.4847 | 1183518.5615 | 2584350.7892 | 1183561.8176 | 2584349.0883 | 1183603.01 | 2584351.2048 | 1183635.7436 | 2584355.7815 | 1183647.5826
88 | 2584296.7385 | 1183455.7715 | 2584286.5564 | 1183449.7704
89 | 2584185.9375 | 1183436.7324 | 2584208.8502 | 1183436.001
90 | 2584359.2287 | 1183656.5 | 2584355.7815 | 1183647.5826
91 | 2584286.5564 | 1183449.7704 | 2584283.0681 | 1183447.7145 | 2584267.5892 | 1183441.9323
92 | 2584368.359 | 1183223.2408 | 2584337.7332 | 1183012.0343
93 | 2584368.359 | 1183223.2408 | 2584378.6878 | 1183229.039 | 2584393.5843 | 1183229.9893 | 2584443.7841 | 1183220.5866 | 2584486.0223 | 1183214.3288 | 2584496.2213 | 1183212.0694
94 | 2584337.7332 | 1183012.0343 | 2584362.2787 | 1182986.2899 | 2584385.624 | 1182960.849
95 | 2584503.9251 | 1183210.3627 | 2584496.2213 | 1183212.0694
96 | 2584267.5892 | 1183441.9323 | 2584254.5813 | 1183437.0731 | 2584228.0953 | 1183435.3867 | 2584208.8502 | 1183436.001
97 | 2584359.2287 | 1183656.5 | 2584367.3256 | 1183661.4591 | 2584379.3898 | 1183662.717 | 2584392.5555 | 1183662.6825
98 | 2584523.0611 | 1183669.1344 | 2584523.0611 | 1183669.1344 | 2584518.028 | 1183671.0707 | 2584510.7763 | 1183679.9163 | 2584505.3329 | 1183691.3586 | 2584499.8925 | 1183698.1207 | 2584493.1532 | 1183701.4288 | 2584483.0401 | 1183701.8998 | 2584466.8066 | 1183697.1397 | 2584435.9455 | 1183679.9335 | 2584413.3479 | 1183667.286 | 2584394.13 | 1183662.6784 | 2584392.5555 | 1183662.6825
99 | 2584503.9251 | 1183210.3627 | 2584508.9701 | 1183209.2451
100 | 2584571.4329 | 1183202.9151 | 2584550.0535 | 1183211.2819
101 | 2584600.059 | 1183188.762 | 2584581.477 | 1183198.9843 | 2584571.4329 | 1183202.9151
102 | 2583845.1339 | 1183619.3074 | 2583901.1698 | 1183621.4124
103 | 2583901.1698 | 1183621.4124 | 2583925.7057 | 1183614.5632
104 | 2583901.1698 | 1183621.4124 | 2583883.9791 | 1183630.9578
105 | 2583952.079 | 1183604.6882 | 2583943.6338 | 1183609.5584 | 2583925.7057 | 1183614.5632
106 | 2583861.3742 | 1183648.8787 | 2583869.744 | 1183638.862 | 2583883.9791 | 1183630.9578
107 | 2583993.8654 | 1183567.9685 | 2583975.2515 | 1183548.3864
108 | 2583974.8299 | 1183591.4634 | 2583969.7992 | 1183594.4691 | 2583952.079 | 1183604.6882
109 | 2583861.3742 | 1183648.8787 | 2583849.5979 | 1183666.5864 | 2583839.2709 | 1183686.6804 | 2583833.8635 | 1183698.927
110 | 2583861.3742 | 1183648.8787 | 2583865.5046 | 1183663.0193
111 | 2583996.7336 | 1183574.6455 | 2583994.7515 | 1183579.561 | 2583994.7515 | 1183579.561
112 | 2583817.2779 | 1183746.3116 | 2583822.5432 | 1183741.8877 | 2583825.0699 | 1183736.289 | 2583825.199 | 1183726.9465
113 | 2583825.199 | 1183726.9465 | 2583825.2812 | 1183720.9952
114 | 2583833.8635 | 1183698.927 | 2583825.3187 | 1183718.279 | 2583825.2812 | 1183720.9952
115 | 2583994.7515 | 1183579.561 | 2583986.6807 | 1183584.383
116 | 2583974.8299 | 1183591.4634 | 2583986.6807 | 1183584.383
117 | 2584523.0611 | 1183669.1344 | 2584536.1643 | 1183670.7345 | 2584551.7415 | 1183675.5855 | 2584606.7034 | 1183711.373 | 2584623.9161 | 1183717.0426 | 2584642.7468 | 1183713.7256 | 2584650.9206 | 1183707.1679 | 2584651.1548 | 1183706.842
118 | 2584672.6168 | 1183666.4243 | 2584668.8942 | 1183673.3374 | 2584658.2377 | 1183696.9882 | 2584651.1548 | 1183706.842
119 | 2584672.6168 | 1183666.4243 | 2584690.2193 | 1183677.1328
120 | 2584672.6168 | 1183666.4243 | 2584655.4901 | 1183652.6946 | 2584636.8183 | 1183637.8128 | 2584626.9464 | 1183622.3302 | 2584626.9043 | 1183605.9996 | 2584627.2248 | 1183605.6326
121 | 2584722.4422 | 1183714.688 | 2584721.4329 | 1183705.1078 | 2584717.8571 | 1183697.8466 | 2584705.3163 | 1183686.3172 | 2584690.2193 | 1183677.1328
122 | 2584627.2248 | 1183605.6326 | 2584629.7812 | 1183602.7049
123 | 2584670.5976 | 1183574.4595 | 2584667.0272 | 1183576.0062
124 | 2584670.5976 | 1183574.4595 | 2584677.3184 | 1183571.5481
125 | 2584667.0272 | 1183576.0062 | 2584657.7152 | 1183580.0402 | 2584645.3008 | 1183588.2833
126 | 2584687.1709 | 1183567.28 | 2584677.3184 | 1183571.5481
127 | 2584645.3008 | 1183588.2833 | 2584643.3716 | 1183589.5643
128 | 2584687.1709 | 1183567.28 | 2584694.154 | 1183578.5235 | 2584703.2014 | 1183594.0082 | 2584709.2508 | 1183599.2555
129 | 2584687.1709 | 1183567.28 | 2584697.8875 | 1183563.577
130 | 2584629.7812 | 1183602.7049 | 2584638.3361 | 1183592.9078 | 2584643.3716 | 1183589.5643
131 | 2584829.8545 | 1183496.8981 | 2584816.6023 | 1183502.7822 | 2584802.0946 | 1183513.3246 | 2584778.2361 | 1183532.9512 | 2584760.5118 | 1183542.3236 | 2584728.4322 | 1183553.0223 | 2584697.8875 | 1183563.577
132 | 2584829.8545 | 1183496.8981 | 2584835.4133 | 1183494.43 | 2584841.4549 | 1183492.9036
133 | 2584722.4422 | 1183714.688 | 2584722.4422 | 1183714.688 | 2584722.3495 | 1183720.4929
134 | 2584722.2681 | 1183725.5873 | 2584722.3495 | 1183720.4929
135 | 2584765.9526 | 1183942.8158 | 2584758.571 | 1183938.3668 | 2584735.2188 | 1183952.9844
136 | 2584776.2767 | 1183949.0382 | 2584765.9526 | 1183942.8158
137 | 2584789.4965 | 1183921.8459 | 2584789.3303 | 1183937.4766 | 2584787.7491 | 1183943.0169 | 2584781.7463 | 1183947.7346 | 2584776.2767 | 1183949.0382
138 | 2584789.4965 | 1183921.8459 | 2584789.0998 | 1183911.6613
139 | 2584789.0998 | 1183911.6613 | 2584788.1405 | 1183887.0313 | 2584786.8812 | 1183879.9065
140 | 2584722.2239 | 1183728.357 | 2584721.7384 | 1183758.7459 | 2584733.9832 | 1183794.7999 | 2584764.7233 | 1183836.8652 | 2584781.8487 | 1183865.3139 | 2584786.3513 | 1183876.9084 | 2584786.8812 | 1183879.9065
141 | 2584722.2681 | 1183725.5873 | 2584722.2239 | 1183728.357
142 | 2584841.4549 | 1183492.9036 | 2584859.4161 | 1183488.3657
143 | 2584859.4161 | 1183488.3657 | 2584896.3523 | 1183479.0339 | 2584903.5082 | 1183476.3433

## bus_geodata
| x | y | coords
0 | 2584285.3753 | 1182131.545
1 | 2584272.9244 | 1182123.5684
2 | 2584323.9409 | 1182154.6506
3 | 2584269.2449 | 1182092.0397
4 | 2584496.1446 | 1182193.1419
5 | 2584262.6745 | 1182082.1409
6 | 2584512.056 | 1182213.4443
7 | 2584477.1247 | 1182244.9405
8 | 2583312.8507 | 1183002.8013
9 | 2583588.0315 | 1183098.8069
10 | 2583886.0112 | 1182814.6627
11 | 2583587.0295 | 1183103.477
12 | 2583993.0191 | 1182749.9256
13 | 2583532.0459 | 1183225.0155
14 | 2583534.7257 | 1183238.9264
15 | 2583580.7506 | 1183141.6936
16 | 2583703.6121 | 1183637.5909
17 | 2583707.1197 | 1183647.3419
18 | 2583720.2556 | 1183635.4407
19 | 2584425.1009 | 1182282.0729
20 | 2583583.54 | 1183135.6613
21 | 2583586.4561 | 1183112.2234
22 | 2583586.4396 | 1183106.2263
23 | 2583566.3888 | 1183280.2528
24 | 2583774.8223 | 1183344.923
25 | 2584023.7186 | 1182776.8192
26 | 2584013.8636 | 1182770.9913
27 | 2584024.7254 | 1182777.2689
28 | 2584005.4972 | 1182765.3
29 | 2584050.9179 | 1182788.9683
30 | 2584008.0932 | 1182748.3065
31 | 2584066.5279 | 1182793.0552
32 | 2584060.2377 | 1182756.7823
33 | 2584016.9264 | 1182739.7339
34 | 2584071.4033 | 1182794.3317
35 | 2584068.4136 | 1182758.9905
36 | 2584079.3015 | 1182761.931
37 | 2584132.1505 | 1182757.5909
38 | 2584167.4668 | 1182739.7656
39 | 2584152.6347 | 1182562.5357
40 | 2584180.3791 | 1182739.5907
41 | 2584206.8925 | 1182490.3568
42 | 2584181.3066 | 1182739.5781
43 | 2584206.3352 | 1182742.7529
44 | 2584236.8458 | 1182450.433
45 | 2584121.2408 | 1183403.0043
46 | 2584129.4561 | 1183396.9619
47 | 2584067.1614 | 1183407.3668
48 | 2584147.991 | 1183439.9904
49 | 2584076.4746 | 1183421.6493
50 | 2584048.9352 | 1183405.7925
51 | 2584167.2649 | 1183432.5188
52 | 2584134.6383 | 1183446.8567
53 | 2584014.461 | 1183379.7981
54 | 2584176.1154 | 1183429.0878
55 | 2584103.7368 | 1183465.2769
56 | 2584039.4434 | 1183453.0168
57 | 2584045.011 | 1183460.7693
58 | 2584058.7138 | 1183479.8491
59 | 2584039.5716 | 1183498.1431
60 | 2584087.4268 | 1183463.6418
61 | 2584031.3363 | 1183535.6957
62 | 2584017.921 | 1183479.5643
63 | 2584448.6804 | 1183372.0347
64 | 2584478.5597 | 1183356.3427
65 | 2584446.6345 | 1183373.1092
66 | 2584583.4625 | 1183270.0492
67 | 2584427.5438 | 1183383.1352
68 | 2584559.0941 | 1183228.3849
69 | 2584380.527 | 1183404.5017
70 | 2584417.0881 | 1183367.0465
71 | 2584546.3043 | 1183212.7492
72 | 2584360.5872 | 1183412.1255
73 | 2584410.0683 | 1183356.2448
74 | 2584024.0202 | 1183543.1081
75 | 2584038.2556 | 1183543.2528
76 | 2584009.8522 | 1183534.575
77 | 2584001.5232 | 1183562.7675
78 | 2584037.1688 | 1183560.2264
79 | 2584351.3912 | 1183395.7634
80 | 2584296.7385 | 1183455.7715
81 | 2584386.548 | 1183364.8775
82 | 2584185.9375 | 1183436.7324
83 | 2584355.7815 | 1183647.5826
84 | 2584286.5564 | 1183449.7704
85 | 2584368.359 | 1183223.2408
86 | 2584337.7332 | 1183012.0343
87 | 2584496.2213 | 1183212.0694
88 | 2584208.8502 | 1183436.001
89 | 2584359.2287 | 1183656.5
90 | 2584267.5892 | 1183441.9323
91 | 2584392.5555 | 1183662.6825
92 | 2584503.9251 | 1183210.3627
93 | 2584508.9701 | 1183209.2451
94 | 2584550.0535 | 1183211.2819
95 | 2584571.4329 | 1183202.9151
96 | 2584385.624 | 1182960.849
97 | 2584600.059 | 1183188.762
98 | 2583845.1339 | 1183619.3074
99 | 2583901.1698 | 1183621.4124
100 | 2583925.7057 | 1183614.5632
101 | 2583883.9791 | 1183630.9578
102 | 2583993.8654 | 1183567.9685
103 | 2583975.2515 | 1183548.3864
104 | 2583952.079 | 1183604.6882
105 | 2583861.3742 | 1183648.8787
106 | 2583996.7336 | 1183574.6455
107 | 2583817.2779 | 1183746.3116
108 | 2583825.199 | 1183726.9465
109 | 2583825.2812 | 1183720.9952
110 | 2583833.8635 | 1183698.927
111 | 2583865.5046 | 1183663.0193
112 | 2583994.7515 | 1183579.561
113 | 2583996.7921 | 1183546.3494
114 | 2583986.6807 | 1183584.383
115 | 2583974.8299 | 1183591.4634
116 | 2584523.0611 | 1183669.1344
117 | 2584651.1548 | 1183706.842
118 | 2584672.6168 | 1183666.4243
119 | 2584690.2193 | 1183677.1328
120 | 2584627.2248 | 1183605.6326
121 | 2584670.5976 | 1183574.4595
122 | 2584667.0272 | 1183576.0062
123 | 2584677.3184 | 1183571.5481
124 | 2584645.3008 | 1183588.2833
125 | 2584687.1709 | 1183567.28
126 | 2584643.3716 | 1183589.5643
127 | 2584709.2508 | 1183599.2555
128 | 2584697.8875 | 1183563.577
129 | 2584629.7812 | 1183602.7049
130 | 2584829.8545 | 1183496.8981
131 | 2584722.4422 | 1183714.688
132 | 2584722.3495 | 1183720.4929
133 | 2584765.9526 | 1183942.8158
134 | 2584735.2188 | 1183952.9844
135 | 2584776.2767 | 1183949.0382
136 | 2584789.4965 | 1183921.8459
137 | 2584789.0998 | 1183911.6613
138 | 2584786.8812 | 1183879.9065
139 | 2584722.2681 | 1183725.5873
140 | 2584722.2239 | 1183728.357
141 | 2584841.4549 | 1183492.9036
142 | 2584859.4161 | 1183488.3657
143 | 2584903.5082 | 1183476.3433
144 | 2584411.2488 | 1182301.8193
145 | 2584185.9375 | 1183436.7324

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97054 | -0.21113 | 0.00056216 | 0.00014089
1 | 0.97053 | -0.21122 | 0.00019319 | 4.8418e-05
2 | 0.97061 | -0.21059 | 0.00046356 | 0.00011618
3 | 0.97051 | -0.21135 | 0 | 0
4 | 0.97103 | -0.20758 | 0 | 0
5 | 0.9705 | -0.21139 | 0.00036453 | 9.136e-05
6 | 0.97109 | -0.20711 | 0 | 0
7 | 0.9712 | -0.2063 | 0.00030959 | 7.759e-05
8 | 0.98303 | -0.12033 | 0.00068236 | 0.00017102
9 | 0.98332 | -0.11824 | 0.00022792 | 5.7122e-05
10 | 0.97764 | -0.15916 | 0.00037513 | 9.4016e-05
11 | 0.98339 | -0.11772 | 0.00027617 | 6.9216e-05
12 | 0.97551 | -0.17462 | 0 | 0
13 | 0.98607 | -0.098477 | 0 | 0
14 | 0.98637 | -0.096371 | 0 | 0
15 | 0.98405 | -0.11293 | 0.00034523 | 8.6523e-05
16 | 0.98773 | -0.086397 | 0 | 0
17 | 0.98773 | -0.086427 | 0.00027735 | 6.951e-05
18 | 0.98774 | -0.086349 | 0.00054368 | 0.00013626
19 | 0.97138 | -0.20496 | 0 | 0
20 | 0.98392 | -0.1139 | 0.0027091 | 0.00067896
21 | 0.98353 | -0.11673 | 0.00044104 | 0.00011054
22 | 0.98343 | -0.11741 | 0.00016651 | 4.1731e-05
23 | 0.98758 | -0.087717 | 0.00062371 | 0.00015632
24 | 0.99017 | -0.069315 | 0 | 0
25 | 0.9748 | -0.17975 | 0.0011114 | 0.00027854
26 | 0.97495 | -0.17867 | 0.0001683 | 4.218e-05
27 | 0.97479 | -0.17984 | 0.00014406 | 3.6105e-05
28 | 0.97508 | -0.17771 | 0 | 0
29 | 0.97448 | -0.18214 | 0 | 0
30 | 0.97531 | -0.17607 | 0 | 0
31 | 0.97444 | -0.18239 | 0.00052694 | 0.00013206
32 | 0.97418 | -0.18431 | 0 | 0
33 | 0.97531 | -0.17608 | 9.2152e-05 | 2.3095e-05
34 | 0.97443 | -0.18244 | 0.00095754 | 0.00023998
35 | 0.9741 | -0.18485 | 0.00013811 | 3.4613e-05
36 | 0.97401 | -0.18557 | 0.00085977 | 0.00021548
37 | 0.97361 | -0.18848 | 0 | 0
38 | 0.9733 | -0.19073 | 0 | 0
39 | 0.9726 | -0.19594 | 0 | 0
40 | 0.97326 | -0.19106 | 8.731e-05 | 2.1882e-05
41 | 0.97224 | -0.19859 | 0.00064043 | 0.00016051
42 | 0.97325 | -0.19108 | 0.0011482 | 0.00028776
43 | 0.97321 | -0.19139 | 0.0011586 | 0.00029037
44 | 0.97209 | -0.19968 | 0.00011751 | 2.9452e-05
45 | 0.99462 | -0.037725 | 0.0051168 | 0.0012824
46 | 0.9947 | -0.037196 | 0 | 0
47 | 0.99355 | -0.045311 | 0 | 0
48 | 0.99705 | -0.020612 | 0 | 0
49 | 0.99335 | -0.046742 | 0.0064864 | 0.0016256
50 | 0.99332 | -0.046905 | 0.00031613 | 7.923e-05
51 | 0.99797 | -0.014192 | 0.001287 | 0.00032255
52 | 0.99634 | -0.025598 | 0.0014853 | 0.00037224
53 | 0.9928 | -0.050652 | 0.0017059 | 0.00042755
54 | 0.9984 | -0.011186 | 0 | 0
55 | 0.99471 | -0.037045 | 0 | 0
56 | 0.99216 | -0.054992 | 0.0043541 | 0.0010912
57 | 0.99222 | -0.05457 | 0.0026823 | 0.00067225
58 | 0.99245 | -0.052895 | 0 | 0
59 | 0.99154 | -0.059368 | 0 | 0
60 | 0.99394 | -0.042439 | 0.00037875 | 9.4925e-05
61 | 0.99024 | -0.068533 | 0 | 0
62 | 0.99144 | -0.060085 | 0.0024748 | 0.00062024
63 | 0.98985 | -0.071122 | 0.00060077 | 0.00015057
64 | 0.98922 | -0.075578 | 0.0014867 | 0.0003726
65 | 0.98989 | -0.070803 | 0.001124 | 0.00028169
66 | 0.98698 | -0.09153 | 0 | 0
67 | 0.99035 | -0.06758 | 0 | 0
68 | 0.98618 | -0.097198 | 0.00052722 | 0.00013213
69 | 0.99157 | -0.058959 | 0.0015696 | 0.00039338
70 | 0.9903 | -0.06792 | 0.00070112 | 0.00017572
71 | 0.98586 | -0.099462 | 0 | 0
72 | 0.99212 | -0.05505 | 0 | 0
73 | 0.99028 | -0.068056 | 0.0010369 | 0.00025988
74 | 0.99 | -0.070217 | 0 | 0
75 | 0.99016 | -0.069133 | 0.00083799 | 0.00021002
76 | 0.98993 | -0.070753 | 0.0023368 | 0.00058566
77 | 0.98946 | -0.074088 | 0 | 0
78 | 0.99002 | -0.070127 | 0.0049114 | 0.0012309
79 | 0.99209 | -0.055253 | 0 | 0
80 | 0.99465 | -0.037261 | 0 | 0
81 | 0.99202 | -0.055771 | 0.0010626 | 0.00026632
82 | 0.99896 | -0.0072409 | 0 | 0
83 | 0.98852 | -0.080191 | 0.0020113 | 0.00050407
84 | 0.99532 | -0.032578 | 0.00035236 | 8.8311e-05
85 | 0.98524 | -0.10393 | 0 | 0
86 | 0.9847 | -0.10781 | 0 | 0
87 | 0.98558 | -0.10154 | 0.00073649 | 0.00018458
88 | 1 | 0 | -0.10551 | -0.026338
89 | 0.98827 | -0.081968 | 0 | 0
90 | 0.99649 | -0.024368 | 0.0011065 | 0.00027731
91 | 0.98735 | -0.088441 | 0.0002141 | 5.3658e-05
92 | 0.9856 | -0.10133 | 0.00077116 | 0.00019327
93 | 0.98563 | -0.10116 | 0.00099125 | 0.00024843
94 | 0.98583 | -0.099736 | 0.0051004 | 0.0012783
95 | 0.98578 | -0.1001 | 0.0011864 | 0.00029733
96 | 0.98453 | -0.10908 | 0.001749 | 0.00043834
97 | 0.98576 | -0.10021 | 0.00033345 | 8.3571e-05
98 | 0.98789 | -0.085281 | 0 | 0
99 | 0.98795 | -0.084801 | 0 | 0
100 | 0.98818 | -0.083179 | 0.0018511 | 0.00046393
101 | 0.9878 | -0.085885 | 0.00083637 | 0.00020961
102 | 0.98945 | -0.074165 | 0 | 0
103 | 0.98942 | -0.074392 | 0.00082077 | 0.0002057
104 | 0.98851 | -0.080837 | 0.0006659 | 0.00016689
105 | 0.98761 | -0.087249 | 0 | 0
106 | 0.98924 | -0.075641 | 0.0014139 | 0.00035437
107 | 0.9871 | -0.090878 | 0.0021784 | 0.00054595
108 | 0.98717 | -0.090379 | 0.00025441 | 6.3761e-05
109 | 0.98719 | -0.09023 | 0.00030652 | 7.6821e-05
110 | 0.98728 | -0.08956 | 0.0011962 | 0.00029979
111 | 0.98759 | -0.08734 | 0.00059866 | 0.00015004
112 | 0.98916 | -0.076208 | 0.00046654 | 0.00011693
113 | 0.98991 | -0.070903 | 0.00083899 | 0.00021027
114 | 0.98902 | -0.077168 | 0.00065965 | 0.00016532
115 | 0.98884 | -0.078486 | 0.00059877 | 0.00015007
116 | 0.9833 | -0.11713 | 0.00025965 | 6.5075e-05
117 | 0.97962 | -0.14339 | 0.00027013 | 6.7702e-05
118 | 0.97846 | -0.15171 | 0 | 0
119 | 0.97818 | -0.15374 | 0.0018202 | 0.0004562
120 | 0.97753 | -0.15845 | 0.0010965 | 0.0002748
121 | 0.97702 | -0.16205 | 0.0015292 | 0.00038325
122 | 0.97706 | -0.16182 | 0.00045991 | 0.00011526
123 | 0.97698 | -0.16238 | 0.00051951 | 0.0001302
124 | 0.97728 | -0.16019 | 0.00017302 | 4.3362e-05
125 | 0.97692 | -0.16279 | 0 | 0
126 | 0.97731 | -0.16003 | 0.00015785 | 3.9561e-05
127 | 0.9769 | -0.16295 | 0.00038463 | 9.6397e-05
128 | 0.97687 | -0.16319 | 0.0010859 | 0.00027215
129 | 0.97749 | -0.15873 | 0.00030568 | 7.661e-05
130 | 0.97638 | -0.16668 | 0.00027646 | 6.9288e-05
131 | 0.9776 | -0.15791 | 0.00021163 | 5.3039e-05
132 | 0.97754 | -0.15836 | 0.00049246 | 0.00012342
133 | 0.97552 | -0.17287 | 0.0012096 | 0.00030315
134 | 0.97533 | -0.17419 | 0.0034657 | 0.00086858
135 | 0.9756 | -0.17228 | 0 | 0
136 | 0.97584 | -0.17058 | 0 | 0
137 | 0.97591 | -0.17008 | 0.00034202 | 8.5717e-05
138 | 0.97614 | -0.1684 | 0.00033484 | 8.3918e-05
139 | 0.97748 | -0.15873 | 0.0013949 | 0.0003496
140 | 0.97746 | -0.15889 | 0.00013734 | 3.442e-05
141 | 0.97635 | -0.16693 | 0.00029463 | 7.3841e-05
142 | 0.9763 | -0.16725 | 0.0004433 | 0.0001111
143 | 0.97622 | -0.16783 | 0.0012032 | 0.00030154
144 | 0.97145 | -0.20447 | 0 | 0
145 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00055774 | 0.00013905 | -0.00055773 | -0.00013923 | 6.7463e-09 | -1.8021e-07 | 0.00085485 | 0.00085492 | 0.00085492 | 0.97054 | -0.21113 | 0.97053 | -0.21122 | 0.31664
1 | -0.0011199 | -0.00027994 | 0.00112 | 0.00027942 | 8.3282e-08 | -5.277e-07 | 0.0017167 | 0.0017165 | 0.0017167 | 0.97054 | -0.21113 | 0.97061 | -0.21059 | 0.63583
2 | 0.00036454 | 9.0815e-05 | -0.00036453 | -9.1214e-05 | 6.3243e-09 | -3.9866e-07 | 0.00055872 | 0.00055886 | 0.00055886 | 0.97053 | -0.21122 | 0.97051 | -0.21135 | 0.20699
3 | -0.0015835 | -0.00039559 | 0.0015842 | 0.00039365 | 6.5252e-07 | -1.9445e-06 | 0.0024272 | 0.0024264 | 0.0024272 | 0.97061 | -0.21059 | 0.97103 | -0.20758 | 0.89897
4 | 0.00036453 | 9.1214e-05 | -0.00036453 | -9.136e-05 | 2.326e-09 | -1.4657e-07 | 0.00055886 | 0.00055892 | 0.00055892 | 0.97051 | -0.21135 | 0.9705 | -0.21139 | 0.20701
5 | -0.0015842 | -0.00039365 | 0.0015843 | 0.00039335 | 1.0098e-07 | -3.0121e-07 | 0.0024264 | 0.0024263 | 0.0024264 | 0.97103 | -0.20758 | 0.97109 | -0.20711 | 0.89868
6 | -0.0015843 | -0.00039335 | 0.0015845 | 0.00039283 | 1.7495e-07 | -5.2204e-07 | 0.0024263 | 0.0024261 | 0.0024263 | 0.97109 | -0.20711 | 0.9712 | -0.2063 | 0.89863
7 | -0.0018941 | -0.00047042 | 0.0018944 | 0.00046974 | 3.4473e-07 | -6.803e-07 | 0.0029004 | 0.0029001 | 0.0029004 | 0.9712 | -0.2063 | 0.97138 | -0.20496 | 1.0742
8 | -0.00068236 | -0.00017102 | 0.00068255 | 0.00016739 | 1.9378e-07 | -3.6215e-06 | 0.0010329 | 0.0010316 | 0.0010329 | 0.98303 | -0.12033 | 0.98332 | -0.11824 | 0.38255
9 | 0.009512 | 0.0023731 | -0.0094588 | -0.0023578 | 5.3211e-05 | 1.5273e-05 | 0.01439 | 0.014392 | 0.014392 | 0.98332 | -0.11824 | 0.97764 | -0.15916 | 5.3304
10 | -0.010423 | -0.0025976 | 0.010423 | 0.0025978 | 7.4093e-07 | 2.2438e-07 | 0.015767 | 0.015767 | 0.015767 | 0.98332 | -0.11824 | 0.98339 | -0.11772 | 5.8396
11 | 0.0090837 | 0.0022638 | -0.0090645 | -0.0022584 | 1.9198e-05 | 5.3688e-06 | 0.013821 | 0.013822 | 0.013822 | 0.97764 | -0.15916 | 0.97551 | -0.17462 | 5.1192
12 | -0.010699 | -0.002667 | 0.0107 | 0.0026672 | 4.596e-07 | 1.4109e-07 | 0.016185 | 0.016185 | 0.016185 | 0.98339 | -0.11772 | 0.98343 | -0.11741 | 5.9943
13 | 0.0090645 | 0.0022584 | -0.0090627 | -0.0022579 | 1.8021e-06 | 5.0444e-07 | 0.013822 | 0.013822 | 0.013822 | 0.97551 | -0.17462 | 0.97531 | -0.17607 | 5.1193
14 | -0.014398 | -0.003597 | 0.014402 | 0.0035984 | 4.1719e-06 | 1.4238e-06 | 0.021722 | 0.021722 | 0.021722 | 0.98607 | -0.098477 | 0.98637 | -0.096371 | 8.0453
15 | 0.014398 | 0.003597 | -0.014369 | -0.0035872 | 2.8581e-05 | 9.7572e-06 | 0.021722 | 0.021723 | 0.021723 | 0.98607 | -0.098477 | 0.98405 | -0.11293 | 8.0455
16 | -0.014402 | -0.0035984 | 0.014419 | 0.0036043 | 1.7169e-05 | 5.8581e-06 | 0.021722 | 0.021722 | 0.021722 | 0.98637 | -0.096371 | 0.98758 | -0.087717 | 8.0453
17 | 0.014024 | 0.0035007 | -0.014022 | -0.0035001 | 1.864e-06 | 6.3251e-07 | 0.021201 | 0.021201 | 0.021201 | 0.98405 | -0.11293 | 0.98392 | -0.1139 | 7.8521
18 | 0.00027735 | 6.9378e-05 | -0.00027735 | -6.951e-05 | 1.1287e-09 | -1.3219e-07 | 0.00041778 | 0.00041783 | 0.00041783 | 0.98773 | -0.086397 | 0.98773 | -0.086427 | 0.15475
19 | -0.00027735 | -6.9378e-05 | 0.00027735 | 6.9164e-05 | 1.8274e-09 | -2.1409e-07 | 0.00041778 | 0.00041771 | 0.00041778 | 0.98773 | -0.086397 | 0.98774 | -0.086349 | 0.15473
20 | -0.00082104 | -0.00020542 | 0.00082116 | 0.00020386 | 1.2013e-07 | -1.5657e-06 | 0.0012368 | 0.0012362 | 0.0012368 | 0.98774 | -0.086349 | 0.98789 | -0.085281 | 0.45806
21 | -0.0018944 | -0.00046974 | 0.0018945 | 0.00046949 | 1.2648e-07 | -2.4972e-07 | 0.0029001 | 0.0029 | 0.0029001 | 0.97138 | -0.20496 | 0.97145 | -0.20447 | 1.0741
22 | 0.011313 | 0.0028211 | -0.011308 | -0.0028197 | 4.3819e-06 | 1.3806e-06 | 0.017104 | 0.017104 | 0.017104 | 0.98392 | -0.1139 | 0.98353 | -0.11673 | 6.3348
23 | 0.010867 | 0.0027092 | -0.010866 | -0.0027089 | 1.011e-06 | 3.1275e-07 | 0.016437 | 0.016437 | 0.016437 | 0.98353 | -0.11673 | 0.98343 | -0.11741 | 6.0876
24 | -0.015043 | -0.0037606 | 0.015081 | 0.0037692 | 3.817e-05 | 8.5678e-06 | 0.022662 | 0.02266 | 0.022662 | 0.98758 | -0.087717 | 0.99017 | -0.069315 | 4.1966
25 | -0.015081 | -0.0037692 | 0.01512 | 0.0037778 | 3.8791e-05 | 8.6732e-06 | 0.02266 | 0.022657 | 0.02266 | 0.99017 | -0.069315 | 0.9928 | -0.050652 | 4.1962
26 | -0.0087978 | -0.0021915 | 0.0087991 | 0.0021919 | 1.2922e-06 | 3.5375e-07 | 0.013425 | 0.013425 | 0.013425 | 0.9748 | -0.17975 | 0.97495 | -0.17867 | 4.9721
27 | 0.0076864 | 0.001913 | -0.0076863 | -0.001913 | 9.4648e-08 | 2.2656e-08 | 0.011728 | 0.011728 | 0.011728 | 0.9748 | -0.17975 | 0.97479 | -0.17984 | 4.3438
28 | -0.0089674 | -0.0022341 | 0.0089685 | 0.0022344 | 1.1819e-06 | 3.2837e-07 | 0.013682 | 0.013682 | 0.013682 | 0.97495 | -0.17867 | 0.97508 | -0.17771 | 5.0673
29 | 0.0075422 | 0.0018769 | -0.0075398 | -0.0018763 | 2.3708e-06 | 5.5435e-07 | 0.011508 | 0.011508 | 0.011508 | 0.97479 | -0.17984 | 0.97448 | -0.18214 | 4.2624
30 | -0.0089685 | -0.0022344 | 0.0089705 | 0.002235 | 2.0083e-06 | 5.579e-07 | 0.013682 | 0.013681 | 0.013682 | 0.97508 | -0.17771 | 0.97531 | -0.17607 | 5.0672
31 | 0.0014845 | 0.00037181 | -0.0014845 | -0.00037199 | 5.1739e-08 | -1.8112e-07 | 0.0022668 | 0.0022669 | 0.0022669 | 0.97448 | -0.18214 | 0.97444 | -0.18239 | 0.83958
32 | 0.0060553 | 0.0015045 | -0.0060535 | -0.0015042 | 1.7858e-06 | 2.6954e-07 | 0.0092417 | 0.0092418 | 0.0092418 | 0.97448 | -0.18214 | 0.97418 | -0.18431 | 3.4229
33 | 9.2152e-05 | 2.2942e-05 | -9.2152e-05 | -2.3095e-05 | 1.5176e-10 | -1.5355e-07 | 0.00014054 | 0.0001406 | 0.0001406 | 0.97531 | -0.17607 | 0.97531 | -0.17608 | 0.052072
34 | 0.00095755 | 0.00023992 | -0.00095754 | -0.00023998 | 6.7237e-09 | -6.0194e-08 | 0.0014622 | 0.0014622 | 0.0014622 | 0.97444 | -0.18239 | 0.97443 | -0.18244 | 0.54156
35 | 0.0060535 | 0.0015042 | -0.0060531 | -0.0015042 | 4.5136e-07 | 6.8168e-08 | 0.0092418 | 0.0092419 | 0.0092419 | 0.97418 | -0.18431 | 0.9741 | -0.18485 | 3.4229
36 | 0.0059149 | 0.0014695 | -0.0059144 | -0.0014695 | 5.7396e-07 | 8.0372e-08 | 0.0090309 | 0.0090309 | 0.0090309 | 0.9741 | -0.18485 | 0.97401 | -0.18557 | 3.3448
37 | 0.0050546 | 0.001254 | -0.0050526 | -0.0012539 | 1.997e-06 | 9.9592e-08 | 0.0077174 | 0.0077177 | 0.0077177 | 0.97401 | -0.18557 | 0.97361 | -0.18848 | 2.8584
38 | 0.0050526 | 0.0012539 | -0.0050511 | -0.0012538 | 1.5453e-06 | 7.7469e-08 | 0.0077177 | 0.0077179 | 0.0077179 | 0.97361 | -0.18848 | 0.9733 | -0.19073 | 2.8585
39 | 0.0026568 | 0.00065422 | -0.0026549 | -0.00065575 | 1.8573e-06 | -1.5304e-06 | 0.0040576 | 0.0040584 | 0.0040584 | 0.9733 | -0.19073 | 0.9726 | -0.19594 | 1.5031
40 | 0.0023943 | 0.00059959 | -0.0023942 | -0.00059971 | 1.0796e-07 | -1.1896e-07 | 0.0036603 | 0.0036603 | 0.0036603 | 0.9733 | -0.19073 | 0.97326 | -0.19106 | 1.3557
41 | 0.0026549 | 0.00065575 | -0.002654 | -0.00065653 | 9.4693e-07 | -7.7866e-07 | 0.0040584 | 0.0040588 | 0.0040588 | 0.9726 | -0.19594 | 0.97224 | -0.19859 | 1.5033
42 | 0.0023068 | 0.00057783 | -0.0023068 | -0.00057784 | 7.1994e-09 | -8.7577e-09 | 0.0035268 | 0.0035268 | 0.0035268 | 0.97326 | -0.19106 | 0.97325 | -0.19108 | 1.3062
43 | 0.0020136 | 0.00049602 | -0.0020133 | -0.00049652 | 2.9522e-07 | -5.0533e-07 | 0.0030787 | 0.0030789 | 0.0030789 | 0.97224 | -0.19859 | 0.97209 | -0.19968 | 1.1403
44 | 0.0011586 | 0.00029007 | -0.0011586 | -0.00029037 | 4.9833e-08 | -2.9709e-07 | 0.0017714 | 0.0017715 | 0.0017715 | 0.97325 | -0.19108 | 0.97321 | -0.19139 | 0.6561
45 | 0.0018957 | 0.00046707 | -0.0018945 | -0.00046949 | 1.2207e-06 | -2.4133e-06 | 0.002899 | 0.0029 | 0.0029 | 0.97209 | -0.19968 | 0.97145 | -0.20447 | 1.0741
46 | -0.0051168 | -0.0012824 | 0.0051172 | 0.0012824 | 3.7412e-07 | 1.1094e-08 | 0.0076551 | 0.007655 | 0.0076551 | 0.99462 | -0.037725 | 0.9947 | -0.037196 | 2.8352
47 | 0.023668 | 0.0059221 | -0.023642 | -0.0059136 | 2.6478e-05 | 8.428e-06 | 0.035403 | 0.035404 | 0.035404 | 0.9947 | -0.037196 | 0.99355 | -0.045311 | 6.5562
48 | -0.028785 | -0.0072045 | 0.028852 | 0.0072269 | 6.6038e-05 | 2.2428e-05 | 0.043058 | 0.043057 | 0.043058 | 0.9947 | -0.037196 | 0.99705 | -0.020612 | 7.9737
49 | 0.0064877 | 0.0016259 | -0.0064864 | -0.0016256 | 1.2851e-06 | 2.1182e-07 | 0.0097164 | 0.0097165 | 0.0097165 | 0.99355 | -0.045311 | 0.99335 | -0.046742 | 3.5987
50 | 0.017154 | 0.0042878 | -0.01715 | -0.0042868 | 3.7662e-06 | 9.7481e-07 | 0.025687 | 0.025687 | 0.025687 | 0.99355 | -0.045311 | 0.99332 | -0.046905 | 4.7569
51 | -0.062042 | -0.015564 | 0.062097 | 0.015584 | 5.53e-05 | 2.073e-05 | 0.092598 | 0.092598 | 0.092598 | 0.99705 | -0.020612 | 0.99797 | -0.014192 | 17.1477
52 | 0.033191 | 0.0083368 | -0.033168 | -0.0083282 | 2.2995e-05 | 8.6484e-06 | 0.049541 | 0.049541 | 0.049541 | 0.99705 | -0.020612 | 0.99634 | -0.025598 | 18.3484
53 | 0.016834 | 0.0042076 | -0.016826 | -0.0042054 | 8.6825e-06 | 2.2068e-06 | 0.025214 | 0.025214 | 0.025214 | 0.99332 | -0.046905 | 0.9928 | -0.050652 | 4.6693
54 | -0.063384 | -0.015907 | 0.063411 | 0.015917 | 2.6457e-05 | 9.9276e-06 | 0.094516 | 0.094516 | 0.094516 | 0.99797 | -0.014192 | 0.9984 | -0.011186 | 17.5031
55 | 0.031682 | 0.007956 | -0.031632 | -0.0079371 | 5.0326e-05 | 1.8888e-05 | 0.047323 | 0.047323 | 0.047323 | 0.99634 | -0.025598 | 0.99471 | -0.037045 | 17.5269
56 | -0.063411 | -0.015917 | 0.063446 | 0.01593 | 3.4756e-05 | 1.3042e-05 | 0.094516 | 0.094516 | 0.094516 | 0.9984 | -0.011186 | 0.99896 | -0.0072409 | 17.503
57 | 0.031632 | 0.0079371 | -0.031608 | -0.0079282 | 2.3655e-05 | 8.8786e-06 | 0.047323 | 0.047323 | 0.047323 | 0.99471 | -0.037045 | 0.99394 | -0.042439 | 17.5269
58 | -0.0043541 | -0.0010912 | 0.0043544 | 0.0010912 | 2.5397e-07 | -2.5587e-08 | 0.0065302 | 0.0065301 | 0.0065302 | 0.99216 | -0.054992 | 0.99222 | -0.05457 | 2.4186
59 | -0.0070367 | -0.0017635 | 0.0070383 | 0.0017638 | 1.6323e-06 | 3.2434e-07 | 0.010553 | 0.010553 | 0.010553 | 0.99222 | -0.05457 | 0.99245 | -0.052895 | 3.9084
60 | 0.024146 | 0.0060525 | -0.024124 | -0.0060445 | 2.1625e-05 | 7.976e-06 | 0.036203 | 0.036203 | 0.036203 | 0.99245 | -0.052895 | 0.99154 | -0.059368 | 13.4086
61 | -0.031184 | -0.0078163 | 0.03123 | 0.0078333 | 4.5214e-05 | 1.6961e-05 | 0.046756 | 0.046756 | 0.046756 | 0.99245 | -0.052895 | 0.99394 | -0.042439 | 17.317
62 | 0.021649 | 0.0054246 | -0.021622 | -0.0054146 | 2.7425e-05 | 1.0012e-05 | 0.032489 | 0.032489 | 0.032489 | 0.99154 | -0.059368 | 0.99024 | -0.068533 | 12.0331
63 | 0.002475 | 0.00061996 | -0.0024748 | -0.00062024 | 2.456e-07 | -2.7348e-07 | 0.0037142 | 0.0037143 | 0.0037143 | 0.99154 | -0.059368 | 0.99144 | -0.060085 | 1.3757
64 | 0.015871 | 0.0039736 | -0.015868 | -0.0039723 | 3.6913e-06 | 1.2859e-06 | 0.023848 | 0.023848 | 0.023848 | 0.99024 | -0.068533 | 0.99 | -0.070217 | 8.8327
65 | 0.0057505 | 0.001441 | -0.00575 | -0.0014409 | 4.7741e-07 | 5.1816e-08 | 0.0086411 | 0.0086411 | 0.0086411 | 0.99024 | -0.068533 | 0.99016 | -0.069133 | 3.2004
66 | 0.012931 | 0.0032375 | -0.012923 | -0.0032349 | 7.9564e-06 | 2.6266e-06 | 0.019437 | 0.019437 | 0.019437 | 0.98985 | -0.071122 | 0.98922 | -0.075578 | 7.199
67 | -0.013531 | -0.0033881 | 0.013532 | 0.0033883 | 5.966e-07 | 1.9976e-07 | 0.02034 | 0.02034 | 0.02034 | 0.98985 | -0.071122 | 0.98989 | -0.070803 | 7.5334
68 | 0.011436 | 0.0028623 | -0.011411 | -0.0028544 | 2.5146e-05 | 7.9269e-06 | 0.017201 | 0.017202 | 0.017202 | 0.98922 | -0.075578 | 0.98698 | -0.09153 | 6.371
69 | -0.014656 | -0.00367 | 0.014662 | 0.0036722 | 6.5301e-06 | 2.2342e-06 | 0.02203 | 0.02203 | 0.02203 | 0.98989 | -0.070803 | 0.99035 | -0.06758 | 8.1592
70 | 0.011411 | 0.0028544 | -0.011402 | -0.0028515 | 8.9146e-06 | 2.8122e-06 | 0.017202 | 0.017202 | 0.017202 | 0.98698 | -0.09153 | 0.98618 | -0.097198 | 6.371
71 | -0.016401 | -0.0041074 | 0.01642 | 0.0041143 | 1.9567e-05 | 6.8604e-06 | 0.024641 | 0.024641 | 0.024641 | 0.99035 | -0.06758 | 0.99157 | -0.058959 | 9.1264
72 | 0.0017382 | 0.00043523 | -0.0017381 | -0.00043544 | 8.1658e-08 | -2.1548e-07 | 0.0026115 | 0.0026116 | 0.0026116 | 0.99035 | -0.06758 | 0.9903 | -0.06792 | 0.96725
73 | 0.010875 | 0.0027194 | -0.010871 | -0.0027184 | 3.3937e-06 | 1.0476e-06 | 0.016406 | 0.016406 | 0.016406 | 0.98618 | -0.097198 | 0.98586 | -0.099462 | 6.0764
74 | -0.01799 | -0.0045077 | 0.018 | 0.0045111 | 9.7368e-06 | 3.4686e-06 | 0.026996 | 0.026996 | 0.026996 | 0.99157 | -0.058959 | 0.99212 | -0.05505 | 9.9987
75 | 0.001037 | 0.00025973 | -0.0010369 | -0.00025988 | 1.9515e-08 | -1.5824e-07 | 0.0015581 | 0.0015581 | 0.0015581 | 0.9903 | -0.06792 | 0.99028 | -0.068056 | 0.57709
76 | 0.0066205 | 0.0016585 | -0.0066202 | -0.0016585 | 2.5084e-07 | 4.5144e-08 | 0.0099924 | 0.0099924 | 0.0099924 | 0.98586 | -0.099462 | 0.98583 | -0.099736 | 3.7009
77 | 0.0042508 | 0.0010598 | -0.0042498 | -0.0010599 | 9.8636e-07 | -1.1043e-07 | 0.006414 | 0.0064142 | 0.0064142 | 0.98586 | -0.099462 | 0.98563 | -0.10116 | 2.3756
78 | 0.0010628 | 0.0002655 | -0.0010627 | -0.00026573 | 2.9732e-08 | -2.3081e-07 | 0.0015937 | 0.0015937 | 0.0015937 | 0.99212 | -0.05505 | 0.99209 | -0.055253 | 0.59027
79 | -0.019062 | -0.0047766 | 0.019109 | 0.0047935 | 4.7034e-05 | 1.6896e-05 | 0.02859 | 0.02859 | 0.02859 | 0.99212 | -0.05505 | 0.99465 | -0.037261 | 10.5889
80 | 0.003176 | 0.00079559 | -0.0031758 | -0.00079571 | 2.3518e-07 | -1.222e-07 | 0.0047736 | 0.0047736 | 0.0047736 | 0.99 | -0.070217 | 0.98993 | -0.070753 | 1.768
81 | 0.012692 | 0.0031767 | -0.012685 | -0.0031745 | 6.7801e-06 | 2.224e-06 | 0.019075 | 0.019075 | 0.019075 | 0.99 | -0.070217 | 0.98946 | -0.074088 | 7.0648
82 | 0.004912 | 0.0012309 | -0.0049114 | -0.0012309 | 6.7542e-07 | 4.3201e-09 | 0.0073818 | 0.0073819 | 0.0073819 | 0.99016 | -0.069133 | 0.99002 | -0.070127 | 2.734
83 | 0.00083901 | 0.00021005 | -0.00083899 | -0.00021027 | 1.7451e-08 | -2.1935e-07 | 0.0012611 | 0.0012612 | 0.0012612 | 0.98993 | -0.070753 | 0.98991 | -0.070903 | 0.46709
84 | 0.011864 | 0.0029692 | -0.011862 | -0.0029684 | 2.5437e-06 | 8.1388e-07 | 0.017841 | 0.017841 | 0.017841 | 0.98946 | -0.074088 | 0.98924 | -0.075641 | 6.6077
85 | 0.0008208 | 0.00020525 | -0.00082079 | -0.00020537 | 8.7822e-09 | -1.1529e-07 | 0.0012342 | 0.0012343 | 0.0012343 | 0.98946 | -0.074088 | 0.98945 | -0.074165 | 0.45713
86 | 0.0010627 | 0.00026573 | -0.0010626 | -0.00026632 | 7.6007e-08 | -5.8987e-07 | 0.0015937 | 0.001594 | 0.001594 | 0.99209 | -0.055253 | 0.99202 | -0.055771 | 0.59035
87 | 0.020424 | 0.0051451 | -0.020302 | -0.0051009 | 0.00012195 | 4.4204e-05 | 0.030563 | 0.030564 | 0.030564 | 0.99465 | -0.037261 | 0.98852 | -0.080191 | 11.3201
88 | -0.039533 | -0.0099386 | 0.039559 | 0.0099484 | 2.5806e-05 | 9.7718e-06 | 0.059153 | 0.059153 | 0.059153 | 0.99465 | -0.037261 | 0.99532 | -0.032578 | 21.9085
89 | -0.063446 | -0.01593 | 0.063509 | 0.015954 | 6.3895e-05 | 2.3974e-05 | 0.094516 | 0.094516 | 0.094516 | 0.99896 | -0.0072409 | 1 | 0 | 17.503
90 | 0.01829 | 0.0045968 | -0.018286 | -0.0045952 | 4.5237e-06 | 1.6174e-06 | 0.027537 | 0.027537 | 0.027537 | 0.98852 | -0.080191 | 0.98827 | -0.081968 | 10.1989
91 | -0.039911 | -0.010037 | 0.039957 | 0.010054 | 4.5722e-05 | 1.7318e-05 | 0.05968 | 0.05968 | 0.05968 | 0.99532 | -0.032578 | 0.99649 | -0.024368 | 22.1036
92 | 0.0017502 | 0.0004352 | -0.0017493 | -0.00043756 | 9.2999e-07 | -2.3587e-06 | 0.0026421 | 0.0026431 | 0.0026431 | 0.98524 | -0.10393 | 0.9847 | -0.10781 | 0.97893
93 | -0.0017502 | -0.0004352 | 0.0017508 | 0.00043375 | 5.7048e-07 | -1.4493e-06 | 0.0026421 | 0.0026415 | 0.0026421 | 0.98524 | -0.10393 | 0.98558 | -0.10154 | 0.97857
94 | 0.0017493 | 0.00043756 | -0.001749 | -0.00043834 | 3.0562e-07 | -7.7403e-07 | 0.0026431 | 0.0026434 | 0.0026434 | 0.9847 | -0.10781 | 0.98453 | -0.10908 | 0.97904
95 | -0.0024873 | -0.00061834 | 0.0024873 | 0.00061826 | 6.9368e-08 | -7.3877e-08 | 0.0037535 | 0.0037535 | 0.0037535 | 0.98558 | -0.10154 | 0.9856 | -0.10133 | 1.3902
96 | 0.041203 | 0.010384 | -0.041063 | -0.010331 | 0.00014008 | 5.3098e-05 | 0.061332 | 0.061332 | 0.061332 | 1 | 0 | 0.99649 | -0.024368 | 22.7155
97 | 0.018286 | 0.0045952 | -0.018269 | -0.0045893 | 1.6462e-05 | 5.8861e-06 | 0.027537 | 0.027537 | 0.027537 | 0.98827 | -0.081968 | 0.98735 | -0.088441 | 10.1989
98 | 0.018055 | 0.0045356 | -0.017983 | -0.00451 | 7.1772e-05 | 2.5627e-05 | 0.027214 | 0.027215 | 0.027215 | 0.98735 | -0.088441 | 0.9833 | -0.11713 | 10.0797
99 | -0.0032585 | -0.00081153 | 0.0032586 | 0.0008115 | 7.7979e-08 | -3.5864e-08 | 0.0049177 | 0.0049177 | 0.0049177 | 0.9856 | -0.10133 | 0.98563 | -0.10116 | 1.8214
100 | 0.0015199 | 0.00038023 | -0.0015198 | -0.00038049 | 7.5386e-08 | -2.6371e-07 | 0.0022939 | 0.002294 | 0.002294 | 0.98583 | -0.099736 | 0.98578 | -0.1001 | 0.84963
101 | 0.00033346 | 8.3165e-05 | -0.00033345 | -8.3571e-05 | 5.0567e-09 | -4.0593e-07 | 0.0005032 | 0.00050335 | 0.00050335 | 0.98578 | -0.1001 | 0.98576 | -0.10021 | 0.18643
102 | -0.00082116 | -0.00020386 | 0.00082121 | 0.00020316 | 5.3306e-08 | -6.9542e-07 | 0.0012362 | 0.0012359 | 0.0012362 | 0.98789 | -0.085281 | 0.98795 | -0.084801 | 0.45785
103 | -0.0061951 | -0.0015482 | 0.0061965 | 0.0015484 | 1.3835e-06 | 2.0583e-07 | 0.0093292 | 0.0093291 | 0.0093292 | 0.98795 | -0.084801 | 0.98818 | -0.083179 | 3.4553
104 | 0.0053739 | 0.0013451 | -0.0053731 | -0.001345 | 8.037e-07 | 5.7366e-08 | 0.0080933 | 0.0080934 | 0.0080934 | 0.98795 | -0.084801 | 0.9878 | -0.085885 | 2.9976
105 | -0.0080476 | -0.0020124 | 0.0080502 | 0.002013 | 2.5983e-06 | 6.3586e-07 | 0.012117 | 0.012116 | 0.012117 | 0.98818 | -0.083179 | 0.98851 | -0.080837 | 4.4876
106 | 0.0045367 | 0.0011354 | -0.0045359 | -0.0011354 | 8.5482e-07 | -4.6679e-08 | 0.0068335 | 0.0068336 | 0.0068336 | 0.9878 | -0.085885 | 0.98761 | -0.087249 | 2.531
107 | 0.00082079 | 0.00020537 | -0.00082077 | -0.0002057 | 2.5685e-08 | -3.3712e-07 | 0.0012343 | 0.0012344 | 0.0012344 | 0.98945 | -0.074165 | 0.98942 | -0.074392 | 0.45718
108 | -0.0087161 | -0.0021799 | 0.0087189 | 0.0021806 | 2.8261e-06 | 7.4949e-07 | 0.013119 | 0.013119 | 0.013119 | 0.98851 | -0.080837 | 0.98884 | -0.078486 | 4.8588
109 | 0.0039372 | 0.00098558 | -0.0039359 | -0.00098583 | 1.2569e-06 | -2.4886e-07 | 0.0059317 | 0.0059319 | 0.0059319 | 0.98761 | -0.087249 | 0.98728 | -0.08956 | 2.197
110 | 0.00059867 | 0.00014985 | -0.00059866 | -0.00015004 | 7.4786e-09 | -1.8563e-07 | 0.00090194 | 0.00090201 | 0.00090201 | 0.98761 | -0.087249 | 0.98759 | -0.08734 | 0.33408
111 | 0.010448 | 0.0026141 | -0.010447 | -0.0026138 | 8.1665e-07 | 2.4606e-07 | 0.015714 | 0.015714 | 0.015714 | 0.98924 | -0.075641 | 0.98916 | -0.076208 | 5.82
112 | -0.0021784 | -0.00054595 | 0.0021785 | 0.00054572 | 1.5047e-07 | -2.2801e-07 | 0.0032838 | 0.0032837 | 0.0032838 | 0.9871 | -0.090878 | 0.98717 | -0.090379 | 1.2162
113 | -0.0024329 | -0.00060948 | 0.002433 | 0.00060943 | 4.9946e-08 | -5.6884e-08 | 0.0036672 | 0.0036672 | 0.0036672 | 0.98717 | -0.090379 | 0.98719 | -0.09023 | 1.3582
114 | -0.0027395 | -0.00068625 | 0.0027397 | 0.00068604 | 2.5397e-07 | -2.0755e-07 | 0.0041292 | 0.0041291 | 0.0041292 | 0.98719 | -0.09023 | 0.98728 | -0.08956 | 1.5293
115 | 0.0099803 | 0.0024969 | -0.009979 | -0.0024965 | 1.3221e-06 | 3.8784e-07 | 0.015012 | 0.015012 | 0.015012 | 0.98916 | -0.076208 | 0.98902 | -0.077168 | 5.56
116 | 0.0093194 | 0.0023312 | -0.0093177 | -0.0023307 | 1.6931e-06 | 4.7409e-07 | 0.01402 | 0.01402 | 0.01402 | 0.98902 | -0.077168 | 0.98884 | -0.078486 | 5.1925
117 | 0.017724 | 0.0044449 | -0.01766 | -0.004422 | 6.4299e-05 | 2.292e-05 | 0.026822 | 0.026823 | 0.026823 | 0.9833 | -0.11713 | 0.97962 | -0.14339 | 9.9344
118 | 0.017389 | 0.0043543 | -0.017369 | -0.0043472 | 1.9993e-05 | 7.1121e-06 | 0.026412 | 0.026413 | 0.026413 | 0.97962 | -0.14339 | 0.97846 | -0.15171 | 9.7825
119 | 0.0094273 | 0.0023604 | -0.0094246 | -0.0023597 | 2.6423e-06 | 7.5757e-07 | 0.014336 | 0.014336 | 0.014336 | 0.97846 | -0.15171 | 0.97818 | -0.15374 | 5.3096
120 | 0.0079421 | 0.0019868 | -0.0079347 | -0.0019849 | 7.3727e-06 | 1.8191e-06 | 0.012077 | 0.012077 | 0.012077 | 0.97846 | -0.15171 | 0.97753 | -0.15845 | 4.473
121 | 0.0076044 | 0.0019035 | -0.0076 | -0.0019024 | 4.3777e-06 | 1.0259e-06 | 0.011567 | 0.011567 | 0.011567 | 0.97818 | -0.15374 | 0.9776 | -0.15791 | 4.2842
122 | 0.0068383 | 0.0017101 | -0.006838 | -0.0017101 | 2.6273e-07 | 5.2327e-08 | 0.010408 | 0.010408 | 0.010408 | 0.97753 | -0.15845 | 0.97749 | -0.15873 | 3.8548
123 | -0.0057387 | -0.0014348 | 0.0057388 | 0.0014348 | 1.8542e-07 | 2.2584e-08 | 0.0087388 | 0.0087388 | 0.0087388 | 0.97702 | -0.16205 | 0.97706 | -0.16182 | 3.2366
124 | 0.0042095 | 0.0010516 | -0.0042093 | -0.0010516 | 1.8778e-07 | -1.9498e-08 | 0.0064098 | 0.0064099 | 0.0064099 | 0.97702 | -0.16205 | 0.97698 | -0.16238 | 2.374
125 | -0.0061987 | -0.0015501 | 0.0062001 | 0.0015503 | 1.3927e-06 | 2.2185e-07 | 0.0094392 | 0.0094391 | 0.0094392 | 0.97706 | -0.16182 | 0.97728 | -0.16019 | 3.496
126 | 0.0036898 | 0.00092138 | -0.0036896 | -0.00092143 | 2.1151e-07 | -5.3094e-08 | 0.0056186 | 0.0056187 | 0.0056187 | 0.97698 | -0.16238 | 0.97692 | -0.16279 | 2.081
127 | -0.0063732 | -0.0015937 | 0.0063733 | 0.0015937 | 1.3604e-07 | 2.3304e-08 | 0.0097025 | 0.0097025 | 0.0097025 | 0.97728 | -0.16019 | 0.97731 | -0.16003 | 3.5935
128 | 0.00038464 | 9.5909e-05 | -0.00038463 | -9.6397e-05 | 8.3886e-09 | -4.873e-07 | 0.00058569 | 0.00058587 | 0.00058587 | 0.97692 | -0.16279 | 0.9769 | -0.16295 | 0.21699
129 | 0.0033049 | 0.00082552 | -0.0033048 | -0.0008256 | 1.7922e-07 | -7.3025e-08 | 0.005033 | 0.005033 | 0.005033 | 0.97692 | -0.16279 | 0.97687 | -0.16319 | 1.8641
130 | -0.0065311 | -0.0016333 | 0.0065323 | 0.0016335 | 1.1752e-06 | 2.1324e-07 | 0.0099428 | 0.0099427 | 0.0099428 | 0.97731 | -0.16003 | 0.97749 | -0.15873 | 3.6825
131 | 0.0022189 | 0.00055344 | -0.0022178 | -0.0005549 | 1.0654e-06 | -1.4611e-06 | 0.0033789 | 0.0033796 | 0.0033796 | 0.97687 | -0.16319 | 0.97638 | -0.16668 | 1.2517
132 | 0.0019413 | 0.00048562 | -0.0019413 | -0.00048574 | 6.7244e-08 | -1.2814e-07 | 0.0029583 | 0.0029583 | 0.0029583 | 0.97638 | -0.16668 | 0.97635 | -0.16693 | 1.0957
133 | 0.0073884 | 0.0018494 | -0.0073879 | -0.0018493 | 4.5811e-07 | 1.0341e-07 | 0.011245 | 0.011245 | 0.011245 | 0.9776 | -0.15791 | 0.97754 | -0.15836 | 4.1649
134 | 0.0068955 | 0.0017259 | -0.0068951 | -0.0017258 | 3.5022e-07 | 7.0831e-08 | 0.010496 | 0.010496 | 0.010496 | 0.97754 | -0.15836 | 0.97748 | -0.15873 | 3.8872
135 | 0.0034663 | 0.00086837 | -0.0034657 | -0.00086858 | 6.3094e-07 | -2.088e-07 | 0.0052872 | 0.0052874 | 0.0052874 | 0.97552 | -0.17287 | 0.97533 | -0.17419 | 1.9583
136 | -0.0046759 | -0.0011715 | 0.0046762 | 0.0011715 | 3.8262e-07 | -3.3429e-09 | 0.0071323 | 0.0071322 | 0.0071323 | 0.97552 | -0.17287 | 0.9756 | -0.17228 | 2.6416
137 | -0.0046762 | -0.0011715 | 0.0046773 | 0.0011715 | 1.099e-06 | -9.7559e-09 | 0.0071322 | 0.007132 | 0.0071322 | 0.9756 | -0.17228 | 0.97584 | -0.17058 | 2.6416
138 | -0.0046773 | -0.0011715 | 0.0046777 | 0.0011715 | 3.2351e-07 | -2.9152e-09 | 0.007132 | 0.007132 | 0.007132 | 0.97584 | -0.17058 | 0.97591 | -0.17008 | 2.6415
139 | -0.0050197 | -0.0012572 | 0.0050209 | 0.0012573 | 1.1654e-06 | 4.9748e-08 | 0.0076535 | 0.0076533 | 0.0076535 | 0.97591 | -0.17008 | 0.97614 | -0.1684 | 2.8346
140 | -0.0053557 | -0.0013412 | 0.0053627 | 0.0013418 | 7.0384e-06 | 5.8837e-07 | 0.0081638 | 0.008163 | 0.0081638 | 0.97614 | -0.1684 | 0.97746 | -0.15889 | 3.0236
141 | 0.0055002 | 0.0013762 | -0.0055001 | -0.0013762 | 1.2115e-07 | 1.1876e-08 | 0.0083721 | 0.0083721 | 0.0083721 | 0.97748 | -0.15873 | 0.97746 | -0.15889 | 3.1008
142 | 0.0016466 | 0.0004119 | -0.0016466 | -0.00041211 | 7.279e-08 | -2.0367e-07 | 0.0025093 | 0.0025094 | 0.0025094 | 0.97635 | -0.16693 | 0.9763 | -0.16725 | 0.9294
143 | 0.0012033 | 0.00030101 | -0.0012032 | -0.00030154 | 9.5987e-08 | -5.3503e-07 | 0.0018337 | 0.0018339 | 0.0018339 | 0.9763 | -0.16725 | 0.97622 | -0.16783 | 0.67923

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10624 | 0.02652

## res_load
| p_mw | q_mvar
0 | 0.00056216 | 0.00014089
1 | 0.00019319 | 4.8418e-05
2 | 0.00046356 | 0.00011618
3 | 0.00036453 | 9.136e-05
4 | 0.00030959 | 7.759e-05
5 | 0.00068236 | 0.00017102
6 | 0.00022792 | 5.7122e-05
7 | 0.00037513 | 9.4016e-05
8 | 0.00027617 | 6.9216e-05
9 | 0.00034523 | 8.6523e-05
10 | 0.00027735 | 6.951e-05
11 | 0.00054368 | 0.00013626
12 | 0.0027091 | 0.00067896
13 | 0.00044104 | 0.00011054
14 | 0.00016651 | 4.1731e-05
15 | 0.00062371 | 0.00015632
16 | 0.0011114 | 0.00027854
17 | 0.0001683 | 4.218e-05
18 | 0.00014406 | 3.6105e-05
19 | 0.00052694 | 0.00013206
20 | 9.2152e-05 | 2.3095e-05
21 | 0.00095754 | 0.00023998
22 | 0.00013811 | 3.4613e-05
23 | 0.00085977 | 0.00021548
24 | 8.731e-05 | 2.1882e-05
25 | 0.00064043 | 0.00016051
26 | 0.0011482 | 0.00028776
27 | 0.0011586 | 0.00029037
28 | 0.00011751 | 2.9452e-05
29 | 0.0051168 | 0.0012824
30 | 0.0064864 | 0.0016256
31 | 0.00031613 | 7.923e-05
32 | 0.001287 | 0.00032255
33 | 0.0014853 | 0.00037224
34 | 0.0017059 | 0.00042755
35 | 0.0043541 | 0.0010912
36 | 0.0026823 | 0.00067225
37 | 0.00037875 | 9.4925e-05
38 | 0.0024748 | 0.00062024
39 | 0.00060077 | 0.00015057
40 | 0.0014867 | 0.0003726
41 | 0.001124 | 0.00028169
42 | 0.00052722 | 0.00013213
43 | 0.0015696 | 0.00039338
44 | 0.00070112 | 0.00017572
45 | 0.0010369 | 0.00025988
46 | 0.00083799 | 0.00021002
47 | 0.0023368 | 0.00058566
48 | 0.0049114 | 0.0012309
49 | 0.0010626 | 0.00026632
50 | 0.0020113 | 0.00050407
51 | 0.00035236 | 8.8311e-05
52 | 0.00073649 | 0.00018458
53 | 0.00072461 | 0.00018161
54 | 0.0011065 | 0.00027731
55 | 0.0002141 | 5.3658e-05
56 | 0.00077116 | 0.00019327
57 | 0.00099125 | 0.00024843
58 | 0.0051004 | 0.0012783
59 | 0.0011864 | 0.00029733
60 | 0.001749 | 0.00043834
61 | 0.00033345 | 8.3571e-05
62 | 0.0018511 | 0.00046393
63 | 0.00083637 | 0.00020961
64 | 0.00082077 | 0.0002057
65 | 0.0006659 | 0.00016689
66 | 0.0014139 | 0.00035437
67 | 0.0021784 | 0.00054595
68 | 0.00025441 | 6.3761e-05
69 | 0.00030652 | 7.6821e-05
70 | 0.0011962 | 0.00029979
71 | 0.00059866 | 0.00015004
72 | 0.00046654 | 0.00011693
73 | 0.00083899 | 0.00021027
74 | 0.00065965 | 0.00016532
75 | 0.00059877 | 0.00015007
76 | 0.00025965 | 6.5075e-05
77 | 0.00027013 | 6.7702e-05
78 | 0.0018202 | 0.0004562
79 | 0.0010965 | 0.0002748
80 | 0.0015292 | 0.00038325
81 | 0.00045991 | 0.00011526
82 | 0.00051951 | 0.0001302
83 | 0.00017302 | 4.3362e-05
84 | 0.00015785 | 3.9561e-05
85 | 0.00038463 | 9.6397e-05
86 | 0.0010859 | 0.00027215
87 | 0.00030568 | 7.661e-05
88 | 0.00027646 | 6.9288e-05
89 | 0.00021163 | 5.3039e-05
90 | 0.00049246 | 0.00012342
91 | 0.0012096 | 0.00030315
92 | 0.0034657 | 0.00086858
93 | 0.00034202 | 8.5717e-05
94 | 0.00033484 | 8.3918e-05
95 | 0.0013949 | 0.0003496
96 | 0.00013734 | 3.442e-05
97 | 0.00029463 | 7.3841e-05
98 | 0.0004433 | 0.0001111
99 | 0.0012032 | 0.00030154

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1