## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2337-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2337-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2337-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2337-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2337-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2337-3_0_3_node_47 | 0.4 | n |  | TRUE
6 | bus_LV_2337-3_0_3_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_2337-3_0_3_node_46 | 0.4 | n |  | TRUE
8 | bus_LV_2337-3_0_3_node_61 | 0.4 | n |  | TRUE
9 | bus_LV_2337-3_0_3_node_59 | 0.4 | n |  | TRUE
10 | bus_LV_2337-3_0_3_node_44 | 0.4 | n |  | TRUE
11 | bus_LV_2337-3_0_3_node_67 | 0.4 | n |  | TRUE
12 | bus_LV_2337-3_0_3_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_2337-3_0_3_node_58 | 0.4 | n |  | TRUE
14 | bus_LV_2337-3_0_3_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_2337-3_0_3_node_5 | 0.4 | n |  | TRUE
16 | bus_LV_2337-3_0_3_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_2337-3_0_3_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_2337-3_0_3_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_2337-3_0_3_node_50 | 0.4 | n |  | TRUE
20 | bus_LV_2337-3_0_3_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_2337-3_0_3_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_2337-3_0_3_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_2337-3_0_3_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_2337-3_0_3_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_2337-3_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_2337-3_0_3_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_2337-3_0_3_node_53 | 0.4 | n |  | TRUE
28 | bus_LV_2337-3_0_3_node_52 | 0.4 | n |  | TRUE
29 | bus_LV_2337-3_0_3_node_48 | 0.4 | n |  | TRUE
30 | bus_LV_2337-3_0_3_node_66 | 0.4 | n |  | TRUE
31 | bus_LV_2337-3_0_3_node_54 | 0.4 | n |  | TRUE
32 | bus_LV_2337-3_0_3_node_64 | 0.4 | n |  | TRUE
33 | bus_LV_2337-3_0_3_node_65 | 0.4 | n |  | TRUE
34 | bus_LV_2337-3_0_3_node_60 | 0.4 | n |  | TRUE
35 | bus_LV_2337-3_0_3_node_15 | 0.4 | n |  | TRUE
36 | bus_LV_2337-3_0_3_node_9 | 0.4 | n |  | TRUE
37 | bus_LV_2337-3_0_3_node_10 | 0.4 | n |  | TRUE
38 | bus_LV_2337-3_0_3_node_11 | 0.4 | n |  | TRUE
39 | bus_LV_2337-3_0_3_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_2337-3_0_3_node_12 | 0.4 | n |  | TRUE
41 | bus_LV_2337-3_0_3_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_2337-3_0_3_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_2337-3_0_3_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_2337-3_0_3_node_13 | 0.4 | n |  | TRUE
45 | bus_LV_2337-3_0_3_node_14 | 0.4 | n |  | TRUE
46 | bus_LV_2337-3_0_3_node_16 | 0.4 | n |  | TRUE
47 | bus_LV_2337-3_0_3_node_17 | 0.4 | n |  | TRUE
48 | bus_LV_2337-3_0_3_node_19 | 0.4 | n |  | TRUE
49 | bus_LV_2337-3_0_3_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_2337-3_0_3_node_20 | 0.4 | n |  | TRUE
51 | bus_LV_2337-3_0_3_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_2337-3_0_3_node_21 | 0.4 | n |  | TRUE
53 | bus_LV_2337-3_0_3_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_2337-3_0_3_node_30 | 0.4 | n |  | TRUE
55 | bus_LV_2337-3_0_3_node_31 | 0.4 | n |  | TRUE
56 | bus_LV_2337-3_0_3_node_33 | 0.4 | n |  | TRUE
57 | bus_LV_2337-3_0_3_node_34 | 0.4 | n |  | TRUE
58 | bus_LV_2337-3_0_3_node_63 | 0.4 | n |  | TRUE
59 | bus_LV_2337-3_0_3_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_2337-3_0_3_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_2337-3_0_3_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_2337-3_0_3_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_2337-3_0_3_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_2337-3_0_3_node_62 | 0.4 | n |  | TRUE
65 | bus_LV_2337-3_0_3_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_2337-3_0_3_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_2337-3_0_3_node_55 | 0.4 | n |  | TRUE
68 | bus_MV_366_0_node_202 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2337-3_0_3_load_0 | 0 | 0.010763 | 0.0026974 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2337-3_0_3_load_2 | 2 | 0.0068259 | 0.0017107 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2337-3_0_3_load_4 | 4 | 0.0075548 | 0.0018934 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2337-3_0_3_load_43 | 6 | 0.0037203 | 0.0009324 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2337-3_0_3_load_46 | 7 | 0.0093569 | 0.0023451 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2337-3_0_3_load_59 | 9 | 0.0010877 | 0.00027261 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2337-3_0_3_load_44 | 10 | 0.0039197 | 0.00098237 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2337-3_0_3_load_67 | 11 | 0.0046783 | 0.0011725 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2337-3_0_3_load_29 | 12 | 0.0044777 | 0.0011222 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2337-3_0_3_load_58 | 13 | 0.003503 | 0.00087793 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2337-3_0_3_load_5 | 15 | 0.0040777 | 0.001022 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2337-3_0_3_load_6 | 16 | 0.00086585 | 0.000217 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2337-3_0_3_load_7 | 17 | 0.00727 | 0.001822 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2337-3_0_3_load_8 | 18 | 0.0017711 | 0.00044389 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2337-3_0_3_load_50 | 19 | 0.0012757 | 0.00031972 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2337-3_0_3_load_18 | 20 | 0.0015361 | 0.00038498 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2337-3_0_3_load_22 | 21 | 0.0073491 | 0.0018419 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2337-3_0_3_load_23 | 22 | 0.0011418 | 0.00028617 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2337-3_0_3_load_35 | 26 | 0.00076429 | 0.00019155 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2337-3_0_3_load_53 | 27 | 0.00091901 | 0.00023033 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2337-3_0_3_load_52 | 28 | 0.00057553 | 0.00014424 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2337-3_0_3_load_48 | 29 | 0.00089198 | 0.00022355 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2337-3_0_3_load_66 | 30 | 0.00096623 | 0.00024216 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2337-3_0_3_load_64 | 32 | 0.00097356 | 0.000244 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2337-3_0_3_load_65 | 33 | 0.00058164 | 0.00014577 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2337-3_0_3_load_60 | 34 | 0.0053222 | 0.0013339 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2337-3_0_3_load_9 | 36 | 0.0037574 | 0.0009417 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2337-3_0_3_load_10 | 37 | 0.0080368 | 0.0020142 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2337-3_0_3_load_11 | 38 | 0.0014216 | 0.00035629 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2337-3_0_3_load_28 | 39 | 0.0029378 | 0.00073628 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2337-3_0_3_load_12 | 40 | 0.00053085 | 0.00013304 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2337-3_0_3_load_40 | 42 | 0.0015037 | 0.00037687 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2337-3_0_3_load_38 | 43 | 0.0019764 | 0.00049533 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2337-3_0_3_load_13 | 44 | 0.0062081 | 0.0015559 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2337-3_0_3_load_16 | 46 | 0.0036609 | 0.0009175 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2337-3_0_3_load_17 | 47 | 0.0051879 | 0.0013002 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2337-3_0_3_load_19 | 48 | 0.0038176 | 0.00095678 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2337-3_0_3_load_45 | 49 | 0.0066192 | 0.0016589 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2337-3_0_3_load_20 | 50 | 0.004691 | 0.0011757 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2337-3_0_3_load_39 | 51 | 0.0035547 | 0.00089089 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2337-3_0_3_load_21 | 52 | 0.005367 | 0.0013451 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2337-3_0_3_load_37 | 53 | 0.0017389 | 0.0004358 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2337-3_0_3_load_30 | 54 | 0.00084698 | 0.00021227 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2337-3_0_3_load_31 | 55 | 0.0020171 | 0.00050554 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2337-3_0_3_load_33 | 56 | 0.002927 | 0.00073357 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2337-3_0_3_load_34 | 57 | 0.0047587 | 0.0011926 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2337-3_0_3_load_63 | 58 | 0.00051455 | 0.00012896 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2337-3_0_3_load_41 | 59 | 0.0025268 | 0.00063327 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2337-3_0_3_load_42 | 60 | 0.013798 | 0.0034581 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2337-3_0_3_load_36 | 61 | 0.0018469 | 0.00046287 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2337-3_0_3_load_49 | 62 | 0.00068232 | 0.000171 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2337-3_0_3_load_51 | 63 | 0.00076834 | 0.00019256 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2337-3_0_3_load_62 | 64 | 0.00086382 | 0.00021649 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2337-3_0_3_load_55 | 67 | 0.0032351 | 0.00081078 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2337-3_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.031998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_2337-3_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.013716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_2337-3_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.054221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2337-3_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.013669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_2337-3_0_3_line_4 | NAYY 4x150 SE | 3 | 8 | 0.043122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2337-3_0_3_line_5 | NAYY 4x150 SE | 3 | 9 | 0.015873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2337-3_0_3_line_6 | NAYY 4x150 SE | 4 | 10 | 0.0035159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_2337-3_0_3_line_7 | NAYY 4x150 SE | 5 | 6 | 0.068652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_2337-3_0_3_line_8 | NAYY 4x150 SE | 5 | 7 | 0.029406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_2337-3_0_3_line_9 | NAYY 4x150 SE | 6 | 65 | 0.0166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2337-3_0_3_line_10 | NAYY 4x150 SE | 6 | 60 | 0.015458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_2337-3_0_3_line_11 | NAYY 4x150 SE | 7 | 49 | 0.0066868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_2337-3_0_3_line_12 | NAYY 4x150 SE | 8 | 11 | 0.050859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2337-3_0_3_line_13 | NAYY 4x150 SE | 8 | 12 | 0.045208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2337-3_0_3_line_14 | NAYY 4x150 SE | 9 | 13 | 0.035149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2337-3_0_3_line_15 | NAYY 4x150 SE | 10 | 14 | 0.018442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_2337-3_0_3_line_16 | NAYY 4x150 SE | 12 | 41 | 0.0028947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2337-3_0_3_line_17 | NAYY 4x150 SE | 14 | 59 | 0.0032334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_2337-3_0_3_line_18 | NAYY 4x150 SE | 14 | 55 | 0.014234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2337-3_0_3_line_19 | NAYY 4x150 SE | 15 | 16 | 0.026983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2337-3_0_3_line_20 | NAYY 4x150 SE | 15 | 17 | 0.040019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2337-3_0_3_line_21 | NAYY 4x150 SE | 16 | 18 | 0.065593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_2337-3_0_3_line_22 | NAYY 4x150 SE | 17 | 19 | 0.086521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2337-3_0_3_line_23 | NAYY 4x150 SE | 18 | 20 | 0.017952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_2337-3_0_3_line_24 | NAYY 4x150 SE | 19 | 28 | 0.0068646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2337-3_0_3_line_25 | NAYY 4x150 SE | 19 | 29 | 0.024487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2337-3_0_3_line_26 | NAYY 4x150 SE | 20 | 35 | 0.010797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_2337-3_0_3_line_27 | NAYY 4x150 SE | 21 | 22 | 0.022705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2337-3_0_3_line_28 | NAYY 4x150 SE | 21 | 23 | 0.0097429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2337-3_0_3_line_29 | NAYY 4x150 SE | 22 | 24 | 0.019341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2337-3_0_3_line_30 | NAYY 4x150 SE | 23 | 25 | 0.018759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2337-3_0_3_line_31 | NAYY 4x150 SE | 24 | 26 | 0.017729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2337-3_0_3_line_32 | NAYY 4x150 SE | 25 | 34 | 0.040441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2337-3_0_3_line_33 | NAYY 4x150 SE | 26 | 27 | 0.028742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2337-3_0_3_line_34 | NAYY 4x150 SE | 27 | 31 | 0.015094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2337-3_0_3_line_35 | NAYY 4x150 SE | 28 | 30 | 0.0099028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2337-3_0_3_line_36 | NAYY 4x150 SE | 29 | 62 | 0.024753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2337-3_0_3_line_37 | NAYY 4x150 SE | 30 | 33 | 0.0098007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2337-3_0_3_line_38 | NAYY 4x150 SE | 31 | 32 | 0.01659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2337-3_0_3_line_39 | NAYY 4x150 SE | 31 | 33 | 0.025502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2337-3_0_3_line_40 | NAYY 4x150 SE | 35 | 47 | 0.015475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2337-3_0_3_line_41 | NAYY 4x150 SE | 35 | 48 | 0.02269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2337-3_0_3_line_42 | NAYY 4x150 SE | 35 | 44 | 0.023157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_2337-3_0_3_line_43 | NAYY 4x150 SE | 36 | 37 | 0.00072472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2337-3_0_3_line_44 | NAYY 4x150 SE | 36 | 38 | 0.021902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2337-3_0_3_line_45 | NAYY 4x150 SE | 37 | 39 | 0.07295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2337-3_0_3_line_46 | NAYY 4x150 SE | 38 | 40 | 0.033852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2337-3_0_3_line_47 | NAYY 4x150 SE | 39 | 41 | 0.044176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2337-3_0_3_line_48 | NAYY 4x150 SE | 42 | 43 | 0.026263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2337-3_0_3_line_49 | NAYY 4x150 SE | 43 | 61 | 0.027375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2337-3_0_3_line_50 | NAYY 4x150 SE | 44 | 45 | 0.023391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_2337-3_0_3_line_51 | NAYY 4x150 SE | 45 | 46 | 0.045466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_2337-3_0_3_line_52 | NAYY 4x150 SE | 46 | 49 | 0.029884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_2337-3_0_3_line_53 | NAYY 4x150 SE | 47 | 50 | 0.017633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2337-3_0_3_line_54 | NAYY 4x150 SE | 48 | 51 | 0.010035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2337-3_0_3_line_55 | NAYY 4x150 SE | 50 | 52 | 0.016324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2337-3_0_3_line_56 | NAYY 4x150 SE | 51 | 53 | 0.0023052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2337-3_0_3_line_57 | NAYY 4x150 SE | 53 | 61 | 0.038599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2337-3_0_3_line_58 | NAYY 4x150 SE | 54 | 55 | 0.01827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2337-3_0_3_line_59 | NAYY 4x150 SE | 54 | 56 | 0.29775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2337-3_0_3_line_60 | NAYY 4x150 SE | 56 | 57 | 0.045306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2337-3_0_3_line_61 | NAYY 4x150 SE | 57 | 58 | 0.016152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2337-3_0_3_line_62 | NAYY 4x150 SE | 59 | 60 | 0.024663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_2337-3_0_3_line_63 | NAYY 4x150 SE | 62 | 63 | 0.0053763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2337-3_0_3_line_64 | NAYY 4x150 SE | 63 | 64 | 0.0077016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2337-3_0_3_line_65 | NAYY 4x150 SE | 65 | 66 | 0.004553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2337-3_0_3_line_66 | NAYY 4x150 SE | 66 | 67 | 0.019648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2337-3_0_3_trafo_2 | 0.25 MVA 20/0.4 kV | 68 | 2 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2556261.4085 | 1161249.7676 | 2556246.89 | 1161271.0178 | 2556247.5025 | 1161277.2499
1 | 2556258.9364 | 1161284.826 | 2556247.5025 | 1161277.2499
2 | 2556309.3998 | 1161275.2201 | 2556304.5455 | 1161272.5651 | 2556280.9823 | 1161260.8195 | 2556261.4085 | 1161249.7676
3 | 2556261.4085 | 1161249.7676 | 2556250.2618 | 1161242.7118 | 2556249.8646 | 1161242.448
4 | 2556309.3998 | 1161275.2201 | 2556335.5717 | 1161289.5592 | 2556346.7433 | 1161296.904
5 | 2556309.3998 | 1161275.2201 | 2556317.1896 | 1161261.3895
6 | 2556246.9357 | 1161240.5028 | 2556249.8646 | 1161242.448
7 | 2556157.2995 | 1161255.0634 | 2556199.5887 | 1161200.9829
8 | 2556157.2995 | 1161255.0634 | 2556156.729 | 1161258.7806 | 2556155.8622 | 1161262.8446 | 2556154.9388 | 1161266.4977 | 2556153.3061 | 1161271.6679 | 2556151.4682 | 1161276.0058 | 2556147.8775 | 1161282.6911
9 | 2556187.6917 | 1161189.4073 | 2556197.532 | 1161199.0627 | 2556199.5887 | 1161200.9829
10 | 2556210.8875 | 1161211.5317 | 2556199.5887 | 1161200.9829
11 | 2556144.3918 | 1161288.3954 | 2556144.7358 | 1161287.9168 | 2556147.8775 | 1161282.6911 | 2556147.8775 | 1161282.6911
12 | 2556346.7433 | 1161296.904 | 2556357.1417 | 1161281.1868 | 2556363.3256 | 1161274.9275 | 2556367.2101 | 1161273.8209 | 2556370.6451 | 1161275.1855 | 2556383.0278 | 1161284.4746
13 | 2556346.7433 | 1161296.904 | 2556360.8945 | 1161306.217 | 2556382.7455 | 1161324.1492
14 | 2556342.6313 | 1161254.263 | 2556330.8068 | 1161247.6165 | 2556328.8722 | 1161247.1192 | 2556327.1171 | 1161247.0542 | 2556325.695 | 1161247.487 | 2556323.6969 | 1161249.8361 | 2556317.1896 | 1161261.3895
15 | 2556231.9081 | 1161229.8167 | 2556243.6555 | 1161238.3244 | 2556246.9357 | 1161240.5028
16 | 2556384.9831 | 1161325.9855 | 2556382.7455 | 1161324.1492
17 | 2556231.9081 | 1161229.8167 | 2556229.2786 | 1161227.9351
18 | 2556231.9081 | 1161229.8167 | 2556239.3117 | 1161217.6591
19 | 2556108.8137 | 1161450.4413 | 2556104.6226 | 1161446.9484 | 2556095.9457 | 1161441.2756 | 2556085.4336 | 1161437.5271
20 | 2556142.6132 | 1161471.2611 | 2556122.4076 | 1161461.7705 | 2556108.8137 | 1161450.4413
21 | 2556112.5316 | 1161389.5233 | 2556110.5772 | 1161390.5644 | 2556101.1721 | 1161396.3696 | 2556091.5916 | 1161407.5121 | 2556082.2434 | 1161422.1215 | 2556079.0525 | 1161435.2517 | 2556085.4336 | 1161437.5271
22 | 2556142.6132 | 1161471.2611 | 2556196.3375 | 1161539.0817
23 | 2556112.5316 | 1161389.5233 | 2556122.6594 | 1161384.1283 | 2556127.3699 | 1161379.6828
24 | 2556196.3375 | 1161539.0817 | 2556191.8381 | 1161541.9827 | 2556190.8958 | 1161543.164
25 | 2556217.4143 | 1161548.6491 | 2556206.411 | 1161539.8308 | 2556201.0588 | 1161538.2246 | 2556196.3375 | 1161539.0817 | 2556196.3375 | 1161539.0817
26 | 2556133.7967 | 1161371.0511 | 2556128.7853 | 1161378.3471 | 2556127.3699 | 1161379.6828
27 | 2556226.6999 | 1161658.7807 | 2556218.9678 | 1161653.0092 | 2556212.6729 | 1161647.1409 | 2556210.0635 | 1161643.5356
28 | 2556235.8751 | 1161657.8995 | 2556230.1272 | 1161659.798 | 2556228.6102 | 1161659.809 | 2556226.9028 | 1161658.9321 | 2556226.6999 | 1161658.7807
29 | 2556201.3649 | 1161626.3015 | 2556205.7106 | 1161635.9304 | 2556208.9112 | 1161641.9435 | 2556210.0635 | 1161643.5356
30 | 2556235.8751 | 1161657.8995 | 2556249.774 | 1161670.538
31 | 2556201.3649 | 1161626.3015 | 2556194.9944 | 1161619.5445 | 2556189.7209 | 1161612.9517
32 | 2556249.774 | 1161670.538 | 2556223.2068 | 1161701.0289
33 | 2556189.7209 | 1161612.9517 | 2556189.2569 | 1161612.3716 | 2556172.6401 | 1161589.8364
34 | 2556162.7058 | 1161578.5034 | 2556169.9334 | 1161586.1657 | 2556172.6401 | 1161589.8364
35 | 2556190.8958 | 1161543.164 | 2556184.7205 | 1161550.9054
36 | 2556217.4143 | 1161548.6491 | 2556236.73 | 1161564.1291
37 | 2556184.7205 | 1161550.9054 | 2556178.6088 | 1161558.5671
38 | 2556162.7058 | 1161578.5034 | 2556150.0717 | 1161567.7507
39 | 2556162.7058 | 1161578.5034 | 2556178.6088 | 1161558.5671
40 | 2556133.7967 | 1161371.0511 | 2556142.8737 | 1161358.5174
41 | 2556133.7967 | 1161371.0511 | 2556152.6923 | 1161383.6132
42 | 2556133.7967 | 1161371.0511 | 2556114.5136 | 1161358.2286
43 | 2556448.7372 | 1161376.869 | 2556449.3725 | 1161377.2177
44 | 2556468.5732 | 1161387.755 | 2556449.3725 | 1161377.2177
45 | 2556418.072 | 1161310.6776 | 2556448.7372 | 1161376.869
46 | 2556468.5732 | 1161387.755 | 2556498.25 | 1161404.0415
47 | 2556384.9831 | 1161325.9855 | 2556403.4504 | 1161306.1076 | 2556406.5186 | 1161304.4511 | 2556409.1926 | 1161304.4317 | 2556411.1539 | 1161305.4402 | 2556418.072 | 1161310.6776
48 | 2556233.8988 | 1161448.694 | 2556215.3264 | 1161430.125
49 | 2556195.1124 | 1161411.8146 | 2556200.7837 | 1161415.585 | 2556215.3264 | 1161430.125
50 | 2556095.0361 | 1161345.2767 | 2556114.5136 | 1161358.2286
51 | 2556095.0361 | 1161345.2767 | 2556097.5894 | 1161342.3788 | 2556125.3715 | 1161311.4106
52 | 2556144.3918 | 1161288.3954 | 2556141.3376 | 1161292.6441 | 2556134.9147 | 1161300.773 | 2556125.3715 | 1161311.4106
53 | 2556155.5922 | 1161348.5468 | 2556152.3015 | 1161348.0595 | 2556149.0211 | 1161350.0289 | 2556142.8737 | 1161358.5174
54 | 2556152.6923 | 1161383.6132 | 2556161.0492 | 1161389.1689
55 | 2556168.9169 | 1161357.9766 | 2556155.5922 | 1161348.5468 | 2556155.5922 | 1161348.5468
56 | 2556162.9689 | 1161390.4452 | 2556161.0492 | 1161389.1689
57 | 2556195.1124 | 1161411.8146 | 2556162.9689 | 1161390.4452
58 | 2556239.3117 | 1161217.6591 | 2556242.8493 | 1161211.8498 | 2556246.3092 | 1161207.1666 | 2556249.7019 | 1161202.7173 | 2556249.7374 | 1161202.6809
59 | 2556249.7374 | 1161202.6809 | 2556416.5197 | 1160956.026
60 | 2556416.5197 | 1160956.026 | 2556417.2735 | 1160948.688 | 2556430.316 | 1160913.0715
61 | 2556435.8701 | 1160897.9043 | 2556430.316 | 1160913.0715
62 | 2556229.2786 | 1161227.9351 | 2556227.4483 | 1161226.6254 | 2556223.5009 | 1161223.308 | 2556210.8875 | 1161211.5317
63 | 2556240.9252 | 1161567.4912 | 2556236.73 | 1161564.1291
64 | 2556246.935 | 1161572.3076 | 2556240.9252 | 1161567.4912
65 | 2556184.6327 | 1161186.0278 | 2556187.6917 | 1161189.4073
66 | 2556184.6327 | 1161186.0278 | 2556196.4894 | 1161170.3611

## bus_geodata
| x | y | coords
0 | 2556247.5025 | 1161277.2499
1 | 2556261.4085 | 1161249.7676
2 | 2556258.9364 | 1161284.826
3 | 2556309.3998 | 1161275.2201
4 | 2556249.8646 | 1161242.448
5 | 2556157.2995 | 1161255.0634
6 | 2556199.5887 | 1161200.9829
7 | 2556147.8775 | 1161282.6911
8 | 2556346.7433 | 1161296.904
9 | 2556317.1896 | 1161261.3895
10 | 2556246.9357 | 1161240.5028
11 | 2556383.0278 | 1161284.4746
12 | 2556382.7455 | 1161324.1492
13 | 2556342.6313 | 1161254.263
14 | 2556231.9081 | 1161229.8167
15 | 2556108.8137 | 1161450.4413
16 | 2556085.4336 | 1161437.5271
17 | 2556142.6132 | 1161471.2611
18 | 2556112.5316 | 1161389.5233
19 | 2556196.3375 | 1161539.0817
20 | 2556127.3699 | 1161379.6828
21 | 2556226.6999 | 1161658.7807
22 | 2556210.0635 | 1161643.5356
23 | 2556235.8751 | 1161657.8995
24 | 2556201.3649 | 1161626.3015
25 | 2556249.774 | 1161670.538
26 | 2556189.7209 | 1161612.9517
27 | 2556172.6401 | 1161589.8364
28 | 2556190.8958 | 1161543.164
29 | 2556217.4143 | 1161548.6491
30 | 2556184.7205 | 1161550.9054
31 | 2556162.7058 | 1161578.5034
32 | 2556150.0717 | 1161567.7507
33 | 2556178.6088 | 1161558.5671
34 | 2556223.2068 | 1161701.0289
35 | 2556133.7967 | 1161371.0511
36 | 2556449.3725 | 1161377.2177
37 | 2556448.7372 | 1161376.869
38 | 2556468.5732 | 1161387.755
39 | 2556418.072 | 1161310.6776
40 | 2556498.25 | 1161404.0415
41 | 2556384.9831 | 1161325.9855
42 | 2556233.8988 | 1161448.694
43 | 2556215.3264 | 1161430.125
44 | 2556114.5136 | 1161358.2286
45 | 2556095.0361 | 1161345.2768
46 | 2556125.3715 | 1161311.4107
47 | 2556142.8737 | 1161358.5174
48 | 2556152.6923 | 1161383.6132
49 | 2556144.3918 | 1161288.3954
50 | 2556155.5922 | 1161348.5468
51 | 2556161.0492 | 1161389.1689
52 | 2556168.9169 | 1161357.9766
53 | 2556162.9689 | 1161390.4452
54 | 2556249.7374 | 1161202.6809
55 | 2556239.3117 | 1161217.6591
56 | 2556416.5197 | 1160956.026
57 | 2556430.316 | 1160913.0715
58 | 2556435.8701 | 1160897.9043
59 | 2556229.2786 | 1161227.9351
60 | 2556210.8875 | 1161211.5317
61 | 2556195.1124 | 1161411.8146
62 | 2556236.73 | 1161564.1291
63 | 2556240.9252 | 1161567.4912
64 | 2556246.935 | 1161572.3076
65 | 2556187.6917 | 1161189.4073
66 | 2556184.6327 | 1161186.0278
67 | 2556196.4894 | 1161170.3611
68 | 2556261.4085 | 1161249.7676

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9988 | -0.0082873 | 0.010763 | 0.0026974
1 | 0.99617 | -0.026543 | 0 | 0
2 | 1 | 0 | -0.18445 | -0.046328
3 | 0.9938 | -0.043198 | 0 | 0
4 | 0.99525 | -0.032971 | 0.0075548 | 0.0018934
5 | 0.98843 | -0.080628 | 0 | 0
6 | 0.99157 | -0.058663 | 0.0037203 | 0.0009324
7 | 0.98709 | -0.090077 | 0.0093569 | 0.0023451
8 | 0.99219 | -0.054488 | 0 | 0
9 | 0.99369 | -0.043935 | 0.0010877 | 0.00027261
10 | 0.99502 | -0.034537 | 0.0039197 | 0.00098237
11 | 0.99185 | -0.056903 | 0.0046783 | 0.0011725
12 | 0.99081 | -0.06421 | 0.0044777 | 0.0011222
13 | 0.99352 | -0.04518 | 0.003503 | 0.00087793
14 | 0.99388 | -0.04252 | 0 | 0
15 | 0.97884 | -0.14853 | 0.0040777 | 0.001022
16 | 0.9802 | -0.13885 | 0.00086585 | 0.000217
17 | 0.97706 | -0.16121 | 0.00727 | 0.001822
18 | 0.9819 | -0.12683 | 0.0017711 | 0.00044389
19 | 0.97413 | -0.18218 | 0.0012757 | 0.00031972
20 | 0.98222 | -0.12454 | 0.0015361 | 0.00038498
21 | 0.97069 | -0.20696 | 0.0073491 | 0.0018419
22 | 0.97111 | -0.20391 | 0.0011418 | 0.00028617
23 | 0.97061 | -0.20751 | 0 | 0
24 | 0.97151 | -0.20109 | 0 | 0
25 | 0.97047 | -0.20857 | 0 | 0
26 | 0.97186 | -0.19849 | 0.00076429 | 0.00019155
27 | 0.97248 | -0.19407 | 0.00091901 | 0.00023033
28 | 0.97395 | -0.18352 | 0.00057553 | 0.00014424
29 | 0.97402 | -0.18301 | 0.00089198 | 0.00022355
30 | 0.97369 | -0.1854 | 0.00096623 | 0.00024216
31 | 0.97282 | -0.1916 | 0 | 0
32 | 0.9728 | -0.19177 | 0.00097356 | 0.000244
33 | 0.97344 | -0.18716 | 0.00058164 | 0.00014577
34 | 0.97015 | -0.21085 | 0.0053222 | 0.0013339
35 | 0.98242 | -0.1231 | 0 | 0
36 | 0.98823 | -0.082492 | 0.0037574 | 0.0009417
37 | 0.98823 | -0.08245 | 0.0080368 | 0.0020142
38 | 0.98817 | -0.08293 | 0.0014216 | 0.00035629
39 | 0.98968 | -0.07221 | 0.0029378 | 0.00073628
40 | 0.98814 | -0.083114 | 0.00053085 | 0.00013304
41 | 0.99074 | -0.064701 | 0 | 0
42 | 0.98128 | -0.13129 | 0.0015037 | 0.00037687
43 | 0.98133 | -0.13088 | 0.0019764 | 0.00049533
44 | 0.98319 | -0.11764 | 0.0062081 | 0.0015559
45 | 0.98404 | -0.11165 | 0 | 0
46 | 0.98568 | -0.10001 | 0.0036609 | 0.0009175
47 | 0.98208 | -0.12554 | 0.0051879 | 0.0013002
48 | 0.98195 | -0.12649 | 0.0038176 | 0.00095678
49 | 0.98682 | -0.092016 | 0.0066192 | 0.0016589
50 | 0.98182 | -0.12737 | 0.004691 | 0.0011757
51 | 0.98179 | -0.12759 | 0.0035547 | 0.00089089
52 | 0.9817 | -0.12828 | 0.005367 | 0.0013451
53 | 0.98177 | -0.12776 | 0.0017389 | 0.0004358
54 | 0.99341 | -0.045795 | 0.00084698 | 0.00021227
55 | 0.99365 | -0.044117 | 0.0020171 | 0.00050554
56 | 0.9899 | -0.070635 | 0.002927 | 0.00073357
57 | 0.98955 | -0.073071 | 0.0047587 | 0.0011926
58 | 0.98954 | -0.073156 | 0.00051455 | 0.00012896
59 | 0.9937 | -0.0438 | 0.0025268 | 0.00063327
60 | 0.99232 | -0.053372 | 0.013798 | 0.0034581
61 | 0.98147 | -0.12989 | 0.0018469 | 0.00046287
62 | 0.97394 | -0.18361 | 0.00068232 | 0.000171
63 | 0.97392 | -0.1837 | 0.00076834 | 0.00019256
64 | 0.97391 | -0.18377 | 0.00086382 | 0.00021649
65 | 0.99149 | -0.059208 | 0 | 0
66 | 0.99147 | -0.059358 | 0 | 0
67 | 0.99138 | -0.060004 | 0.0032351 | 0.00081078
68 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.17267 | 0.043549 | -0.17223 | -0.04338 | 0.00044078 | 0.00016828 | 0.25734 | 0.25734 | 0.25734 | 0.9988 | -0.0082873 | 0.99617 | -0.026543 | 31.7708
1 | -0.18343 | -0.046246 | 0.18365 | 0.046328 | 0.00021322 | 8.1467e-05 | 0.27338 | 0.27338 | 0.27338 | 0.9988 | -0.0082873 | 1 | 0 | 33.7503
2 | 0.030612 | 0.0076909 | -0.030541 | -0.0076644 | 7.0764e-05 | 2.6513e-05 | 0.045733 | 0.045733 | 0.045733 | 0.99617 | -0.026543 | 0.9938 | -0.043198 | 16.9382
3 | 0.14162 | 0.03569 | -0.14149 | -0.035641 | 0.00012731 | 4.8433e-05 | 0.21161 | 0.21161 | 0.21161 | 0.99617 | -0.026543 | 0.99525 | -0.032971 | 26.1248
4 | 0.02595 | 0.0065141 | -0.025909 | -0.006499 | 4.063e-05 | 1.5069e-05 | 0.038858 | 0.038858 | 0.038858 | 0.9938 | -0.043198 | 0.99219 | -0.054488 | 14.392
5 | 0.0045918 | 0.0011503 | -0.0045913 | -0.0011503 | 4.6819e-07 | -2.5579e-08 | 0.0068751 | 0.0068752 | 0.0068752 | 0.9938 | -0.043198 | 0.99369 | -0.043935 | 2.5464
6 | 0.13394 | 0.033748 | -0.13391 | -0.033737 | 2.9345e-05 | 1.115e-05 | 0.20032 | 0.20032 | 0.20032 | 0.99525 | -0.032971 | 0.99502 | -0.034537 | 24.7303
7 | -0.094919 | -0.023879 | 0.095211 | 0.023988 | 0.0002917 | 0.00010954 | 0.14293 | 0.14293 | 0.14293 | 0.98843 | -0.080628 | 0.99157 | -0.058663 | 17.6452
8 | 0.094919 | 0.023879 | -0.094794 | -0.023832 | 0.00012495 | 4.6927e-05 | 0.14293 | 0.14293 | 0.14293 | 0.98843 | -0.080628 | 0.98709 | -0.090077 | 17.6452
9 | 0.0032357 | 0.00081049 | -0.0032354 | -0.00081061 | 2.4421e-07 | -1.2018e-07 | 0.0048555 | 0.0048556 | 0.0048556 | 0.99157 | -0.058663 | 0.99149 | -0.059208 | 1.7984
10 | -0.10217 | -0.025731 | 0.10224 | 0.02576 | 7.5623e-05 | 2.8487e-05 | 0.15336 | 0.15336 | 0.15336 | 0.99157 | -0.058663 | 0.99232 | -0.053372 | 18.9338
11 | 0.085437 | 0.021487 | -0.085414 | -0.021478 | 2.3081e-05 | 8.621e-06 | 0.12882 | 0.12882 | 0.12882 | 0.98709 | -0.090077 | 0.98682 | -0.092016 | 15.9038
12 | 0.0046799 | 0.0011724 | -0.0046783 | -0.0011725 | 1.5633e-06 | -5.5363e-08 | 0.0070184 | 0.0070186 | 0.0070186 | 0.99219 | -0.054488 | 0.99185 | -0.056903 | 2.5995
13 | 0.021229 | 0.0053266 | -0.0212 | -0.0053162 | 2.8599e-05 | 1.0416e-05 | 0.03184 | 0.03184 | 0.03184 | 0.99219 | -0.054488 | 0.99081 | -0.06421 | 11.7926
14 | 0.0035036 | 0.00087771 | -0.003503 | -0.00087793 | 6.037e-07 | -2.2305e-07 | 0.0052464 | 0.0052465 | 0.0052465 | 0.99369 | -0.043935 | 0.99352 | -0.04518 | 1.9432
15 | 0.12999 | 0.032754 | -0.12984 | -0.032699 | 0.00014505 | 5.507e-05 | 0.19445 | 0.19445 | 0.19445 | 0.99502 | -0.034537 | 0.99388 | -0.04252 | 24.0067
16 | 0.016723 | 0.004194 | -0.016722 | -0.0041936 | 1.1394e-06 | 4.0094e-07 | 0.025115 | 0.025115 | 0.025115 | 0.99081 | -0.06421 | 0.99074 | -0.064701 | 9.302
17 | 0.11874 | 0.029918 | -0.11872 | -0.02991 | 2.127e-05 | 8.0552e-06 | 0.17784 | 0.17784 | 0.17784 | 0.99388 | -0.04252 | 0.9937 | -0.0438 | 21.9552
18 | 0.011099 | 0.0027812 | -0.011096 | -0.0027805 | 2.4526e-06 | 7.5888e-07 | 0.016617 | 0.016617 | 0.016617 | 0.99388 | -0.04252 | 0.99365 | -0.044117 | 6.1544
19 | -0.0346 | -0.0086901 | 0.034647 | 0.0087077 | 4.6595e-05 | 1.7581e-05 | 0.052605 | 0.052605 | 0.052605 | 0.97884 | -0.14853 | 0.9802 | -0.13885 | 19.4835
20 | 0.030523 | 0.0076681 | -0.030469 | -0.0076479 | 5.378e-05 | 2.0182e-05 | 0.046407 | 0.046407 | 0.046407 | 0.97884 | -0.14853 | 0.97706 | -0.16121 | 17.1877
21 | -0.035513 | -0.0089247 | 0.035572 | 0.0089459 | 5.9498e-05 | 2.1227e-05 | 0.05392 | 0.053919 | 0.05392 | 0.9802 | -0.13885 | 0.9819 | -0.12683 | 9.9851
22 | 0.023199 | 0.0058259 | -0.023132 | -0.005801 | 6.741e-05 | 2.4846e-05 | 0.035335 | 0.035335 | 0.035335 | 0.97706 | -0.16121 | 0.97413 | -0.18218 | 13.0872
23 | -0.037343 | -0.0093898 | 0.037355 | 0.0093937 | 1.1964e-05 | 3.9199e-06 | 0.056603 | 0.056603 | 0.056603 | 0.9819 | -0.12683 | 0.98222 | -0.12454 | 6.9881
24 | 0.018649 | 0.0046783 | -0.018645 | -0.004677 | 3.4764e-06 | 1.2516e-06 | 0.028488 | 0.028488 | 0.028488 | 0.97413 | -0.18218 | 0.97395 | -0.18352 | 10.5512
25 | 0.003207 | 0.00080306 | -0.0032067 | -0.00080323 | 3.6667e-07 | -1.6379e-07 | 0.0048986 | 0.0048987 | 0.0048987 | 0.97413 | -0.18218 | 0.97402 | -0.18301 | 1.8143
26 | -0.038892 | -0.0097787 | 0.038899 | 0.0097813 | 7.7993e-06 | 2.5897e-06 | 0.05893 | 0.05893 | 0.05893 | 0.98222 | -0.12454 | 0.98242 | -0.1231 | 7.2753
27 | -0.012674 | -0.003176 | 0.01268 | 0.0031778 | 5.348e-06 | 1.7761e-06 | 0.019429 | 0.019429 | 0.019429 | 0.97069 | -0.20696 | 0.97111 | -0.20391 | 7.1958
28 | 0.0053251 | 0.0013341 | -0.0053247 | -0.0013341 | 4.051e-07 | 3.538e-08 | 0.0081629 | 0.0081629 | 0.0081629 | 0.97069 | -0.20696 | 0.97061 | -0.20751 | 3.0233
29 | -0.013821 | -0.0034639 | 0.013827 | 0.0034658 | 5.4131e-06 | 1.8426e-06 | 0.021178 | 0.021178 | 0.021178 | 0.97111 | -0.20391 | 0.97151 | -0.20109 | 7.8438
30 | 0.0053247 | 0.0013341 | -0.0053239 | -0.001334 | 7.7999e-07 | 6.8179e-08 | 0.0081629 | 0.008163 | 0.008163 | 0.97061 | -0.20751 | 0.97047 | -0.20857 | 3.0233
31 | -0.013827 | -0.0034658 | 0.013832 | 0.0034675 | 4.9619e-06 | 1.6888e-06 | 0.021178 | 0.021178 | 0.021178 | 0.97151 | -0.20109 | 0.97186 | -0.19849 | 7.8437
32 | 0.0053239 | 0.001334 | -0.0053222 | -0.0013339 | 1.6816e-06 | 1.4724e-07 | 0.008163 | 0.0081632 | 0.0081632 | 0.97047 | -0.20857 | 0.97015 | -0.21085 | 3.0234
33 | -0.014596 | -0.003659 | 0.014605 | 0.0036621 | 8.9575e-06 | 3.0888e-06 | 0.022348 | 0.022348 | 0.022348 | 0.97186 | -0.19849 | 0.97248 | -0.19407 | 8.2771
34 | -0.015524 | -0.0038924 | 0.015529 | 0.0038943 | 5.3146e-06 | 1.8567e-06 | 0.023754 | 0.023754 | 0.023754 | 0.97248 | -0.19407 | 0.97282 | -0.1916 | 8.7979
35 | 0.01807 | 0.0045328 | -0.018065 | -0.0045311 | 4.7102e-06 | 1.6884e-06 | 0.027609 | 0.027609 | 0.027609 | 0.97395 | -0.18352 | 0.97369 | -0.1854 | 10.2255
36 | 0.0023147 | 0.00057968 | -0.0023145 | -0.00057991 | 1.9313e-07 | -2.3378e-07 | 0.003536 | 0.0035361 | 0.0035361 | 0.97402 | -0.18301 | 0.97394 | -0.18361 | 1.3097
37 | 0.017099 | 0.0042889 | -0.017095 | -0.0042874 | 4.1764e-06 | 1.4844e-06 | 0.026132 | 0.026132 | 0.026132 | 0.97369 | -0.1854 | 0.97344 | -0.18716 | 9.6786
38 | 0.00097359 | 0.0002438 | -0.00097356 | -0.000244 | 2.2957e-08 | -1.9715e-07 | 0.0014891 | 0.0014892 | 0.0014892 | 0.97282 | -0.1916 | 0.9728 | -0.19177 | 0.55155
39 | -0.016503 | -0.0041381 | 0.016513 | 0.0041417 | 1.014e-05 | 3.5833e-06 | 0.025243 | 0.025243 | 0.025243 | 0.97282 | -0.1916 | 0.97344 | -0.18716 | 9.3494
40 | 0.015254 | 0.0038236 | -0.015249 | -0.0038218 | 5.1551e-06 | 1.7868e-06 | 0.023105 | 0.023105 | 0.023105 | 0.98242 | -0.1231 | 0.98208 | -0.12554 | 8.5574
41 | 0.014449 | 0.003621 | -0.014442 | -0.0036187 | 6.7812e-06 | 2.321e-06 | 0.021885 | 0.021885 | 0.021885 | 0.98242 | -0.1231 | 0.98195 | -0.12649 | 8.1055
42 | -0.068602 | -0.017226 | 0.068654 | 0.017245 | 5.2017e-05 | 1.9126e-05 | 0.10392 | 0.10392 | 0.10392 | 0.98242 | -0.1231 | 0.98319 | -0.11764 | 12.8296
43 | -0.00571 | -0.0014304 | 0.00571 | 0.0014304 | 3.3427e-08 | 3.5714e-09 | 0.0085975 | 0.0085975 | 0.0085975 | 0.98823 | -0.082492 | 0.98823 | -0.08245 | 3.1843
44 | 0.0019526 | 0.00048867 | -0.0019525 | -0.0004889 | 1.1812e-07 | -2.3517e-07 | 0.0029398 | 0.0029399 | 0.0029399 | 0.98823 | -0.082492 | 0.98817 | -0.08293 | 1.0889
45 | -0.013747 | -0.0034446 | 0.013766 | 0.0034512 | 1.9503e-05 | 6.565e-06 | 0.020699 | 0.020699 | 0.020699 | 0.98823 | -0.08245 | 0.98968 | -0.07221 | 7.6662
46 | 0.00053087 | 0.00013262 | -0.00053085 | -0.00013304 | 1.3496e-08 | -4.2847e-07 | 0.00079924 | 0.0007994 | 0.0007994 | 0.98817 | -0.08293 | 0.98814 | -0.083114 | 0.29607
47 | -0.016704 | -0.0041874 | 0.016722 | 0.0041936 | 1.7388e-05 | 6.1195e-06 | 0.025116 | 0.025115 | 0.025116 | 0.98968 | -0.07221 | 0.99074 | -0.064701 | 9.3021
48 | -0.0015037 | -0.00037687 | 0.0015038 | 0.00037657 | 8.5205e-08 | -2.9902e-07 | 0.0022802 | 0.0022801 | 0.0022802 | 0.98128 | -0.13129 | 0.98133 | -0.13088 | 0.84453
49 | -0.0034802 | -0.0008719 | 0.0034807 | 0.00087174 | 4.7566e-07 | -1.6296e-07 | 0.005277 | 0.0052769 | 0.005277 | 0.98133 | -0.13088 | 0.98147 | -0.12989 | 1.9544
50 | -0.074863 | -0.018801 | 0.074925 | 0.018824 | 6.2471e-05 | 2.3137e-05 | 0.11331 | 0.11331 | 0.11331 | 0.98319 | -0.11764 | 0.98404 | -0.11165 | 13.9895
51 | -0.074925 | -0.018824 | 0.075046 | 0.018869 | 0.00012143 | 4.4968e-05 | 0.11331 | 0.11331 | 0.11331 | 0.98404 | -0.11165 | 0.98568 | -0.10001 | 13.9895
52 | -0.078707 | -0.019787 | 0.078795 | 0.019819 | 8.7786e-05 | 3.262e-05 | 0.11884 | 0.11884 | 0.11884 | 0.98568 | -0.10001 | 0.98682 | -0.092016 | 14.6717
53 | 0.010061 | 0.0025216 | -0.010059 | -0.0025208 | 2.5571e-06 | 7.6044e-07 | 0.015244 | 0.015245 | 0.015245 | 0.98208 | -0.12554 | 0.98182 | -0.12737 | 5.6461
54 | 0.010624 | 0.0026619 | -0.010623 | -0.0026614 | 1.6231e-06 | 4.9735e-07 | 0.0161 | 0.0161 | 0.0161 | 0.98195 | -0.12649 | 0.98179 | -0.12759 | 5.9629
55 | 0.0053677 | 0.0013451 | -0.005367 | -0.0013451 | 6.741e-07 | 5.2853e-08 | 0.008135 | 0.0081351 | 0.0081351 | 0.98182 | -0.12737 | 0.9817 | -0.12828 | 3.013
56 | 0.0070681 | 0.0017706 | -0.007068 | -0.0017705 | 1.6507e-07 | 3.4336e-08 | 0.010712 | 0.010712 | 0.010712 | 0.98179 | -0.12759 | 0.98177 | -0.12776 | 3.9675
57 | 0.0053291 | 0.0013347 | -0.0053275 | -0.0013346 | 1.5712e-06 | 1.1637e-07 | 0.0080767 | 0.0080769 | 0.0080769 | 0.98177 | -0.12776 | 0.98147 | -0.12989 | 2.9914
58 | -0.0090772 | -0.0022744 | 0.0090793 | 0.0022749 | 2.1075e-06 | 5.7399e-07 | 0.013596 | 0.013596 | 0.013596 | 0.99341 | -0.045795 | 0.99365 | -0.044117 | 5.0357
59 | 0.0082302 | 0.0020621 | -0.008202 | -0.0020551 | 2.8239e-05 | 7.0197e-06 | 0.012328 | 0.012329 | 0.012329 | 0.99341 | -0.045795 | 0.9899 | -0.070635 | 4.5663
60 | 0.005275 | 0.0013215 | -0.0052732 | -0.0013214 | 1.7775e-06 | 1.0142e-07 | 0.0079292 | 0.0079294 | 0.0079294 | 0.9899 | -0.070635 | 0.98955 | -0.073071 | 2.9368
61 | 0.00051456 | 0.00012875 | -0.00051455 | -0.00012896 | 6.0337e-09 | -2.0518e-07 | 0.00077368 | 0.00077376 | 0.00077376 | 0.98955 | -0.073071 | 0.98954 | -0.073156 | 0.28658
62 | 0.1162 | 0.029277 | -0.11604 | -0.029218 | 0.00015541 | 5.8816e-05 | 0.17405 | 0.17405 | 0.17405 | 0.9937 | -0.0438 | 0.99232 | -0.053372 | 21.4881
63 | 0.0016322 | 0.00040891 | -0.0016322 | -0.00040897 | 2.0862e-08 | -5.888e-08 | 0.0024937 | 0.0024937 | 0.0024937 | 0.97394 | -0.18361 | 0.97392 | -0.1837 | 0.92359
64 | 0.00086383 | 0.0002164 | -0.00086382 | -0.00021649 | 8.371e-09 | -9.2618e-08 | 0.0013198 | 0.0013198 | 0.0013198 | 0.97392 | -0.1837 | 0.97391 | -0.18377 | 0.48882
65 | 0.0032354 | 0.00081061 | -0.0032353 | -0.00081064 | 6.6983e-08 | -3.2956e-08 | 0.0048556 | 0.0048556 | 0.0048556 | 0.99149 | -0.059208 | 0.99147 | -0.059358 | 1.7984
66 | 0.0032353 | 0.00081064 | -0.0032351 | -0.00081078 | 2.8906e-07 | -1.4218e-07 | 0.0048556 | 0.0048557 | 0.0048557 | 0.99147 | -0.059358 | 0.99138 | -0.060004 | 1.7984

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19127 | 0.048038

## res_load
| p_mw | q_mvar
0 | 0.010763 | 0.0026974
1 | 0.0068259 | 0.0017107
2 | 0.0075548 | 0.0018934
3 | 0.0037203 | 0.0009324
4 | 0.0093569 | 0.0023451
5 | 0.0010877 | 0.00027261
6 | 0.0039197 | 0.00098237
7 | 0.0046783 | 0.0011725
8 | 0.0044777 | 0.0011222
9 | 0.003503 | 0.00087793
10 | 0.0040777 | 0.001022
11 | 0.00086585 | 0.000217
12 | 0.00727 | 0.001822
13 | 0.0017711 | 0.00044389
14 | 0.0012757 | 0.00031972
15 | 0.0015361 | 0.00038498
16 | 0.0073491 | 0.0018419
17 | 0.0011418 | 0.00028617
18 | 0.00076429 | 0.00019155
19 | 0.00091901 | 0.00023033
20 | 0.00057553 | 0.00014424
21 | 0.00089198 | 0.00022355
22 | 0.00096623 | 0.00024216
23 | 0.00097356 | 0.000244
24 | 0.00058164 | 0.00014577
25 | 0.0053222 | 0.0013339
26 | 0.0037574 | 0.0009417
27 | 0.0080368 | 0.0020142
28 | 0.0014216 | 0.00035629
29 | 0.0029378 | 0.00073628
30 | 0.00053085 | 0.00013304
31 | 0.0015037 | 0.00037687
32 | 0.0019764 | 0.00049533
33 | 0.0062081 | 0.0015559
34 | 0.0036609 | 0.0009175
35 | 0.0051879 | 0.0013002
36 | 0.0038176 | 0.00095678
37 | 0.0066192 | 0.0016589
38 | 0.004691 | 0.0011757
39 | 0.0035547 | 0.00089089
40 | 0.005367 | 0.0013451
41 | 0.0017389 | 0.0004358
42 | 0.00084698 | 0.00021227
43 | 0.0020171 | 0.00050554
44 | 0.002927 | 0.00073357
45 | 0.0047587 | 0.0011926
46 | 0.00051455 | 0.00012896
47 | 0.0025268 | 0.00063327
48 | 0.013798 | 0.0034581
49 | 0.0018469 | 0.00046287
50 | 0.00068232 | 0.000171
51 | 0.00076834 | 0.00019256
52 | 0.00086382 | 0.00021649
53 | 0.0032351 | 0.00081078

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1