## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2401-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2401-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2401-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2401-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2401-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2401-1_0_4_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_2401-1_0_4_node_77 | 0.4 | n |  | TRUE
7 | bus_LV_2401-1_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2401-1_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2401-1_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2401-1_0_4_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_2401-1_0_4_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_2401-1_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2401-1_0_4_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_2401-1_0_4_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_2401-1_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2401-1_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2401-1_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2401-1_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2401-1_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2401-1_0_4_node_47 | 0.4 | n |  | TRUE
21 | bus_LV_2401-1_0_4_node_44 | 0.4 | n |  | TRUE
22 | bus_LV_2401-1_0_4_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_2401-1_0_4_node_112 | 0.4 | n |  | TRUE
24 | bus_LV_2401-1_0_4_node_45 | 0.4 | n |  | TRUE
25 | bus_LV_2401-1_0_4_node_83 | 0.4 | n |  | TRUE
26 | bus_LV_2401-1_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_2401-1_0_4_node_96 | 0.4 | n |  | TRUE
28 | bus_LV_2401-1_0_4_node_97 | 0.4 | n |  | TRUE
29 | bus_LV_2401-1_0_4_node_78 | 0.4 | n |  | TRUE
30 | bus_LV_2401-1_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_2401-1_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_2401-1_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_2401-1_0_4_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2401-1_0_4_node_64 | 0.4 | n |  | TRUE
35 | bus_LV_2401-1_0_4_node_62 | 0.4 | n |  | TRUE
36 | bus_LV_2401-1_0_4_node_98 | 0.4 | n |  | TRUE
37 | bus_LV_2401-1_0_4_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_2401-1_0_4_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_2401-1_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_2401-1_0_4_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_2401-1_0_4_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_2401-1_0_4_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_2401-1_0_4_node_51 | 0.4 | n |  | TRUE
44 | bus_LV_2401-1_0_4_node_52 | 0.4 | n |  | TRUE
45 | bus_LV_2401-1_0_4_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_2401-1_0_4_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_2401-1_0_4_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_2401-1_0_4_node_49 | 0.4 | n |  | TRUE
49 | bus_LV_2401-1_0_4_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_2401-1_0_4_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_2401-1_0_4_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_2401-1_0_4_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_2401-1_0_4_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_2401-1_0_4_node_122 | 0.4 | n |  | TRUE
55 | bus_LV_2401-1_0_4_node_59 | 0.4 | n |  | TRUE
56 | bus_LV_2401-1_0_4_node_92 | 0.4 | n |  | TRUE
57 | bus_LV_2401-1_0_4_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_2401-1_0_4_node_37 | 0.4 | n |  | TRUE
59 | bus_LV_2401-1_0_4_node_38 | 0.4 | n |  | TRUE
60 | bus_LV_2401-1_0_4_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_2401-1_0_4_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_2401-1_0_4_node_41 | 0.4 | n |  | TRUE
63 | bus_LV_2401-1_0_4_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_2401-1_0_4_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_2401-1_0_4_node_123 | 0.4 | n |  | TRUE
66 | bus_LV_2401-1_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_2401-1_0_4_node_82 | 0.4 | n |  | TRUE
68 | bus_LV_2401-1_0_4_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_2401-1_0_4_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_2401-1_0_4_node_88 | 0.4 | n |  | TRUE
71 | bus_LV_2401-1_0_4_node_89 | 0.4 | n |  | TRUE
72 | bus_LV_2401-1_0_4_node_86 | 0.4 | n |  | TRUE
73 | bus_LV_2401-1_0_4_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_2401-1_0_4_node_46 | 0.4 | n |  | TRUE
75 | bus_LV_2401-1_0_4_node_75 | 0.4 | n |  | TRUE
76 | bus_LV_2401-1_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_2401-1_0_4_node_95 | 0.4 | n |  | TRUE
78 | bus_LV_2401-1_0_4_node_110 | 0.4 | n |  | TRUE
79 | bus_LV_2401-1_0_4_node_80 | 0.4 | n |  | TRUE
80 | bus_LV_2401-1_0_4_node_55 | 0.4 | n |  | TRUE
81 | bus_LV_2401-1_0_4_node_84 | 0.4 | n |  | TRUE
82 | bus_LV_2401-1_0_4_node_121 | 0.4 | n |  | TRUE
83 | bus_LV_2401-1_0_4_node_111 | 0.4 | n |  | TRUE
84 | bus_LV_2401-1_0_4_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_2401-1_0_4_node_69 | 0.4 | n |  | TRUE
86 | bus_LV_2401-1_0_4_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_2401-1_0_4_node_81 | 0.4 | n |  | TRUE
88 | bus_LV_2401-1_0_4_node_65 | 0.4 | n |  | TRUE
89 | bus_LV_2401-1_0_4_node_66 | 0.4 | n |  | TRUE
90 | bus_LV_2401-1_0_4_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_2401-1_0_4_node_109 | 0.4 | n |  | TRUE
92 | bus_LV_2401-1_0_4_node_107 | 0.4 | n |  | TRUE
93 | bus_LV_2401-1_0_4_node_71 | 0.4 | n |  | TRUE
94 | bus_LV_2401-1_0_4_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_2401-1_0_4_node_99 | 0.4 | n |  | TRUE
96 | bus_LV_2401-1_0_4_node_105 | 0.4 | n |  | TRUE
97 | bus_LV_2401-1_0_4_node_72 | 0.4 | n |  | TRUE
98 | bus_LV_2401-1_0_4_node_74 | 0.4 | n |  | TRUE
99 | bus_LV_2401-1_0_4_node_76 | 0.4 | n |  | TRUE
100 | bus_LV_2401-1_0_4_node_79 | 0.4 | n |  | TRUE
101 | bus_LV_2401-1_0_4_node_108 | 0.4 | n |  | TRUE
102 | bus_LV_2401-1_0_4_node_113 | 0.4 | n |  | TRUE
103 | bus_LV_2401-1_0_4_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_2401-1_0_4_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_2401-1_0_4_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_2401-1_0_4_node_91 | 0.4 | n |  | TRUE
107 | bus_LV_2401-1_0_4_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_2401-1_0_4_node_119 | 0.4 | n |  | TRUE
109 | bus_LV_2401-1_0_4_node_118 | 0.4 | n |  | TRUE
110 | bus_LV_2401-1_0_4_node_100 | 0.4 | n |  | TRUE
111 | bus_LV_2401-1_0_4_node_101 | 0.4 | n |  | TRUE
112 | bus_LV_2401-1_0_4_node_102 | 0.4 | n |  | TRUE
113 | bus_LV_2401-1_0_4_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_2401-1_0_4_node_117 | 0.4 | n |  | TRUE
115 | bus_LV_2401-1_0_4_node_124 | 0.4 | n |  | TRUE
116 | bus_LV_2401-1_0_4_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_2401-1_0_4_node_106 | 0.4 | n |  | TRUE
118 | bus_LV_2401-1_0_4_node_114 | 0.4 | n |  | TRUE
119 | bus_LV_2401-1_0_4_node_115 | 0.4 | n |  | TRUE
120 | bus_LV_2401-1_0_4_node_120 | 0.4 | n |  | TRUE
121 | bus_MV_334_0_node_267 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2401-1_0_4_load_0 | 0 | 0.00083452 | 0.00020915 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2401-1_0_4_load_1 | 1 | 0.0018128 | 0.00045432 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2401-1_0_4_load_2 | 2 | 0.0008337 | 0.00020895 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2401-1_0_4_load_3 | 3 | 0.0013178 | 0.00033027 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2401-1_0_4_load_4 | 4 | 0.00083098 | 0.00020826 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2401-1_0_4_load_18 | 5 | 0.0013175 | 0.00033019 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2401-1_0_4_load_5 | 7 | 0.0017984 | 0.00045072 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2401-1_0_4_load_6 | 8 | 0.0033835 | 0.00084798 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2401-1_0_4_load_7 | 9 | 0.00434 | 0.0010877 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2401-1_0_4_load_15 | 10 | 0.0034293 | 0.00085945 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2401-1_0_4_load_9 | 12 | 0.0014409 | 0.00036111 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2401-1_0_4_load_29 | 13 | 0.0020289 | 0.00050849 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2401-1_0_4_load_28 | 14 | 0.0021583 | 0.00054093 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2401-1_0_4_load_10 | 15 | 0.0016632 | 0.00041683 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2401-1_0_4_load_11 | 16 | 0.00091827 | 0.00023014 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2401-1_0_4_load_12 | 17 | 0.0016996 | 0.00042597 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2401-1_0_4_load_14 | 19 | 0.0020586 | 0.00051594 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2401-1_0_4_load_47 | 20 | 0.0027627 | 0.00069241 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2401-1_0_4_load_44 | 21 | 0.0014819 | 0.0003714 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2401-1_0_4_load_61 | 22 | 0.0016934 | 0.00042439 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2401-1_0_4_load_112 | 23 | 0.0036466 | 0.00091391 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2401-1_0_4_load_45 | 24 | 0.0020847 | 0.00052248 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2401-1_0_4_load_83 | 25 | 0.0031319 | 0.00078492 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2401-1_0_4_load_17 | 26 | 0.0033746 | 0.00084575 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2401-1_0_4_load_96 | 27 | 0.0024999 | 0.00062653 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2401-1_0_4_load_97 | 28 | 0.0019502 | 0.00048878 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2401-1_0_4_load_19 | 30 | 0.0011308 | 0.00028341 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2401-1_0_4_load_20 | 31 | 0.0018656 | 0.00046756 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2401-1_0_4_load_21 | 32 | 0.0020818 | 0.00052176 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2401-1_0_4_load_64 | 34 | 0.0010598 | 0.00026562 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2401-1_0_4_load_62 | 35 | 0.00292 | 0.00073181 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2401-1_0_4_load_63 | 37 | 0.0018946 | 0.00047483 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2401-1_0_4_load_23 | 38 | 0.001334 | 0.00033434 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2401-1_0_4_load_24 | 39 | 0.0041577 | 0.001042 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2401-1_0_4_load_25 | 40 | 0.0027633 | 0.00069254 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2401-1_0_4_load_26 | 41 | 0.0017673 | 0.00044294 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2401-1_0_4_load_27 | 42 | 0.0017216 | 0.00043146 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2401-1_0_4_load_51 | 43 | 0.0016019 | 0.00040147 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2401-1_0_4_load_52 | 44 | 0.001616 | 0.000405 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2401-1_0_4_load_30 | 45 | 0.0013567 | 0.00034001 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2401-1_0_4_load_31 | 46 | 0.0012831 | 0.00032158 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2401-1_0_4_load_48 | 47 | 0.0028382 | 0.00071132 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2401-1_0_4_load_32 | 49 | 0.0018687 | 0.00046835 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2401-1_0_4_load_33 | 50 | 0.0024772 | 0.00062085 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2401-1_0_4_load_34 | 51 | 0.001351 | 0.0003386 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2401-1_0_4_load_35 | 52 | 0.0021783 | 0.00054592 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2401-1_0_4_load_36 | 53 | 0.0018426 | 0.00046181 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2401-1_0_4_load_122 | 54 | 0.0040505 | 0.0010151 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2401-1_0_4_load_37 | 58 | 0.0027608 | 0.00069191 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2401-1_0_4_load_38 | 59 | 0.002633 | 0.0006599 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2401-1_0_4_load_40 | 61 | 0.0046042 | 0.0011539 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2401-1_0_4_load_41 | 62 | 0.0042973 | 0.001077 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2401-1_0_4_load_123 | 65 | 0.0042959 | 0.0010767 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2401-1_0_4_load_53 | 66 | 0.004246 | 0.0010642 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2401-1_0_4_load_57 | 68 | 0.0050665 | 0.0012698 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2401-1_0_4_load_56 | 69 | 0.0023176 | 0.00058086 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2401-1_0_4_load_86 | 72 | 0.0030713 | 0.00076974 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2401-1_0_4_load_54 | 73 | 0.0015573 | 0.0003903 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2401-1_0_4_load_46 | 74 | 0.0012675 | 0.00031767 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2401-1_0_4_load_75 | 75 | 0.0015113 | 0.00037878 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2401-1_0_4_load_73 | 76 | 0.0031633 | 0.00079281 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2401-1_0_4_load_110 | 78 | 0.0022278 | 0.00055834 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2401-1_0_4_load_80 | 79 | 0.0022045 | 0.00055251 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2401-1_0_4_load_55 | 80 | 0.0016719 | 0.00041901 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2401-1_0_4_load_84 | 81 | 0.0016795 | 0.00042093 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2401-1_0_4_load_121 | 82 | 0.0034981 | 0.0008767 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2401-1_0_4_load_60 | 84 | 0.00506 | 0.0012682 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2401-1_0_4_load_69 | 85 | 0.0020841 | 0.00052232 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2401-1_0_4_load_70 | 86 | 0.0019559 | 0.0004902 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2401-1_0_4_load_65 | 88 | 0.0024858 | 0.00062299 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2401-1_0_4_load_66 | 89 | 0.0031099 | 0.00077942 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2401-1_0_4_load_68 | 90 | 0.0026474 | 0.00066349 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2401-1_0_4_load_109 | 91 | 0.0024619 | 0.00061702 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2401-1_0_4_load_107 | 92 | 0.0012929 | 0.00032402 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2401-1_0_4_load_71 | 93 | 0.0016954 | 0.00042492 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2401-1_0_4_load_99 | 95 | 0.0020745 | 0.00051992 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2401-1_0_4_load_105 | 96 | 0.0029309 | 0.00073454 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2401-1_0_4_load_72 | 97 | 0.0053347 | 0.001337 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2401-1_0_4_load_74 | 98 | 0.00086114 | 0.00021582 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2401-1_0_4_load_76 | 99 | 0.002652 | 0.00066465 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2401-1_0_4_load_79 | 100 | 0.0035213 | 0.00088253 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2401-1_0_4_load_108 | 101 | 0.0011126 | 0.00027883 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2401-1_0_4_load_113 | 102 | 0.0010952 | 0.00027449 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2401-1_0_4_load_87 | 103 | 0.0054523 | 0.0013665 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2401-1_0_4_load_94 | 104 | 0.0024602 | 0.00061659 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2401-1_0_4_load_90 | 105 | 0.0036896 | 0.00092469 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2401-1_0_4_load_91 | 106 | 0.0021757 | 0.00054527 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2401-1_0_4_load_93 | 107 | 0.0041372 | 0.0010369 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2401-1_0_4_load_119 | 108 | 0.0021829 | 0.0005471 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2401-1_0_4_load_100 | 110 | 0.0030346 | 0.00076054 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2401-1_0_4_load_101 | 111 | 0.0020754 | 0.00052015 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2401-1_0_4_load_103 | 113 | 0.0023437 | 0.00058739 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2401-1_0_4_load_117 | 114 | 0.0019801 | 0.00049626 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2401-1_0_4_load_124 | 115 | 0.0028812 | 0.00072211 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2401-1_0_4_load_116 | 116 | 0.0027065 | 0.00067831 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2401-1_0_4_load_106 | 117 | 0.0019548 | 0.00048991 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2401-1_0_4_load_114 | 118 | 0.0015955 | 0.00039988 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2401-1_0_4_load_115 | 119 | 0.0027394 | 0.00068656 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2401-1_0_4_load_120 | 120 | 0.0051215 | 0.0012836 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2401-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0096674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2401-1_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0097299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2401-1_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0021261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2401-1_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.015507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2401-1_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0098421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2401-1_0_4_line_5 | NAYY 4x150 SE | 5 | 6 | 0.014074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2401-1_0_4_line_6 | NAYY 4x150 SE | 6 | 29 | 0.01649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2401-1_0_4_line_7 | NAYY 4x150 SE | 7 | 8 | 0.0041709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2401-1_0_4_line_8 | NAYY 4x150 SE | 8 | 9 | 0.03135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2401-1_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.00064257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2401-1_0_4_line_10 | NAYY 4x150 SE | 10 | 11 | 0.015109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2401-1_0_4_line_11 | NAYY 4x150 SE | 11 | 26 | 0.025012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2401-1_0_4_line_12 | NAYY 4x150 SE | 12 | 13 | 0.0026707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2401-1_0_4_line_13 | NAYY 4x150 SE | 13 | 14 | 0.0062269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2401-1_0_4_line_14 | NAYY 4x150 SE | 14 | 45 | 0.015924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2401-1_0_4_line_15 | NAYY 4x150 SE | 15 | 16 | 0.0079672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2401-1_0_4_line_16 | NAYY 4x150 SE | 15 | 17 | 0.015058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2401-1_0_4_line_17 | NAYY 4x150 SE | 16 | 18 | 0.0080467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2401-1_0_4_line_18 | NAYY 4x150 SE | 17 | 19 | 0.033341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2401-1_0_4_line_19 | NAYY 4x150 SE | 18 | 20 | 0.040244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2401-1_0_4_line_20 | NAYY 4x150 SE | 18 | 21 | 0.015364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2401-1_0_4_line_21 | NAYY 4x150 SE | 19 | 22 | 0.025338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2401-1_0_4_line_22 | NAYY 4x150 SE | 20 | 23 | 0.078037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2401-1_0_4_line_23 | NAYY 4x150 SE | 21 | 24 | 0.0012842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2401-1_0_4_line_24 | NAYY 4x150 SE | 22 | 25 | 0.00077471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2401-1_0_4_line_25 | NAYY 4x150 SE | 24 | 74 | 0.022113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2401-1_0_4_line_26 | NAYY 4x150 SE | 25 | 87 | 0.022441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2401-1_0_4_line_27 | NAYY 4x150 SE | 26 | 27 | 3.3683e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2401-1_0_4_line_28 | NAYY 4x150 SE | 27 | 28 | 0.020518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2401-1_0_4_line_29 | NAYY 4x150 SE | 28 | 95 | 0.00038793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2401-1_0_4_line_30 | NAYY 4x150 SE | 29 | 87 | 0.040278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2401-1_0_4_line_31 | NAYY 4x150 SE | 30 | 31 | 0.016106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2401-1_0_4_line_32 | NAYY 4x150 SE | 30 | 32 | 0.0067228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2401-1_0_4_line_33 | NAYY 4x150 SE | 32 | 33 | 0.0062609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2401-1_0_4_line_34 | NAYY 4x150 SE | 33 | 34 | 0.016404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2401-1_0_4_line_35 | NAYY 4x150 SE | 33 | 35 | 0.012001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2401-1_0_4_line_36 | NAYY 4x150 SE | 34 | 36 | 0.017305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2401-1_0_4_line_37 | NAYY 4x150 SE | 35 | 37 | 0.0032017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2401-1_0_4_line_38 | NAYY 4x150 SE | 36 | 77 | 0.016656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2401-1_0_4_line_39 | NAYY 4x150 SE | 36 | 48 | 0.008642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2401-1_0_4_line_40 | NAYY 4x150 SE | 38 | 39 | 0.00073199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2401-1_0_4_line_41 | NAYY 4x150 SE | 38 | 40 | 0.022928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2401-1_0_4_line_42 | NAYY 4x150 SE | 39 | 41 | 0.014577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2401-1_0_4_line_43 | NAYY 4x150 SE | 40 | 42 | 0.0054339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2401-1_0_4_line_44 | NAYY 4x150 SE | 42 | 43 | 0.015076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2401-1_0_4_line_45 | NAYY 4x150 SE | 43 | 44 | 0.025836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2401-1_0_4_line_46 | NAYY 4x150 SE | 44 | 64 | 0.026145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2401-1_0_4_line_47 | NAYY 4x150 SE | 45 | 46 | 0.003828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2401-1_0_4_line_48 | NAYY 4x150 SE | 46 | 47 | 0.044461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2401-1_0_4_line_49 | NAYY 4x150 SE | 47 | 48 | 0.011947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2401-1_0_4_line_50 | NAYY 4x150 SE | 48 | 75 | 0.015673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2401-1_0_4_line_51 | NAYY 4x150 SE | 49 | 50 | 0.0030601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_2401-1_0_4_line_52 | NAYY 4x150 SE | 49 | 51 | 0.015893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_2401-1_0_4_line_53 | NAYY 4x150 SE | 50 | 52 | 0.022509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_2401-1_0_4_line_54 | NAYY 4x150 SE | 51 | 53 | 0.0077925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_2401-1_0_4_line_55 | NAYY 4x150 SE | 52 | 54 | 0.0043819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_2401-1_0_4_line_56 | NAYY 4x150 SE | 53 | 55 | 0.01548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_2401-1_0_4_line_57 | NAYY 4x150 SE | 54 | 56 | 0.008714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_2401-1_0_4_line_58 | NAYY 4x150 SE | 55 | 57 | 0.029723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_2401-1_0_4_line_59 | NAYY 4x150 SE | 56 | 83 | 0.029138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_2401-1_0_4_line_60 | NAYY 4x150 SE | 56 | 106 | 0.012006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2401-1_0_4_line_61 | NAYY 4x150 SE | 57 | 84 | 0.0033161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_2401-1_0_4_line_62 | NAYY 4x150 SE | 57 | 69 | 0.011115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2401-1_0_4_line_63 | NAYY 4x150 SE | 58 | 59 | 0.0021132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2401-1_0_4_line_64 | NAYY 4x150 SE | 58 | 60 | 0.036806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2401-1_0_4_line_65 | NAYY 4x150 SE | 59 | 61 | 0.01954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2401-1_0_4_line_66 | NAYY 4x150 SE | 60 | 62 | 0.017977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2401-1_0_4_line_67 | NAYY 4x150 SE | 60 | 63 | 0.032643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
68 | LV_2401-1_0_4_line_68 | NAYY 4x150 SE | 61 | 64 | 0.0051043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2401-1_0_4_line_69 | NAYY 4x150 SE | 62 | 65 | 0.021587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2401-1_0_4_line_70 | NAYY 4x150 SE | 63 | 66 | 0.024845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
71 | LV_2401-1_0_4_line_71 | NAYY 4x150 SE | 64 | 67 | 0.030792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2401-1_0_4_line_72 | NAYY 4x150 SE | 66 | 73 | 0.016644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
73 | LV_2401-1_0_4_line_73 | NAYY 4x150 SE | 67 | 78 | 0.0048887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2401-1_0_4_line_74 | NAYY 4x150 SE | 67 | 79 | 0.021724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2401-1_0_4_line_75 | NAYY 4x150 SE | 68 | 69 | 0.003182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2401-1_0_4_line_76 | NAYY 4x150 SE | 70 | 71 | 0.022956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2401-1_0_4_line_77 | NAYY 4x150 SE | 70 | 72 | 0.014588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2401-1_0_4_line_78 | NAYY 4x150 SE | 71 | 77 | 0.012556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2401-1_0_4_line_79 | NAYY 4x150 SE | 71 | 104 | 0.019272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2401-1_0_4_line_80 | NAYY 4x150 SE | 72 | 103 | 0.0018764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2401-1_0_4_line_81 | NAYY 4x150 SE | 73 | 80 | 0.017177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
82 | LV_2401-1_0_4_line_82 | NAYY 4x150 SE | 75 | 76 | 0.013536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2401-1_0_4_line_83 | NAYY 4x150 SE | 76 | 97 | 0.0015315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2401-1_0_4_line_84 | NAYY 4x150 SE | 77 | 96 | 0.016174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2401-1_0_4_line_85 | NAYY 4x150 SE | 78 | 101 | 0.0031684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2401-1_0_4_line_86 | NAYY 4x150 SE | 79 | 100 | 0.0032115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2401-1_0_4_line_87 | NAYY 4x150 SE | 80 | 81 | 0.015534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_2401-1_0_4_line_88 | NAYY 4x150 SE | 80 | 82 | 0.020998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2401-1_0_4_line_89 | NAYY 4x150 SE | 81 | 83 | 0.0058067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_2401-1_0_4_line_90 | NAYY 4x150 SE | 83 | 102 | 0.023006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2401-1_0_4_line_91 | NAYY 4x150 SE | 84 | 85 | 0.012272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
92 | LV_2401-1_0_4_line_92 | NAYY 4x150 SE | 85 | 86 | 0.013569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
93 | LV_2401-1_0_4_line_93 | NAYY 4x150 SE | 86 | 93 | 0.014342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
94 | LV_2401-1_0_4_line_94 | NAYY 4x150 SE | 87 | 100 | 0.0099915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2401-1_0_4_line_95 | NAYY 4x150 SE | 88 | 89 | 0.0082005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2401-1_0_4_line_96 | NAYY 4x150 SE | 89 | 90 | 0.018104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2401-1_0_4_line_97 | NAYY 4x150 SE | 90 | 91 | 0.017777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2401-1_0_4_line_98 | NAYY 4x150 SE | 91 | 92 | 0.023618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2401-1_0_4_line_99 | NAYY 4x150 SE | 92 | 117 | 0.0017793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2401-1_0_4_line_100 | NAYY 4x150 SE | 93 | 94 | 0.015394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
101 | LV_2401-1_0_4_line_101 | NAYY 4x150 SE | 94 | 95 | 0.0090169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2401-1_0_4_line_102 | NAYY 4x150 SE | 94 | 96 | 0.023476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
103 | LV_2401-1_0_4_line_103 | NAYY 4x150 SE | 97 | 98 | 0.021555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2401-1_0_4_line_104 | NAYY 4x150 SE | 98 | 99 | 0.026136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2401-1_0_4_line_105 | NAYY 4x150 SE | 101 | 117 | 0.02065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2401-1_0_4_line_106 | NAYY 4x150 SE | 102 | 118 | 0.013389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2401-1_0_4_line_107 | NAYY 4x150 SE | 105 | 106 | 0.016718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2401-1_0_4_line_108 | NAYY 4x150 SE | 107 | 108 | 0.028902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2401-1_0_4_line_109 | NAYY 4x150 SE | 108 | 109 | 0.027191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2401-1_0_4_line_110 | NAYY 4x150 SE | 109 | 116 | 0.01816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2401-1_0_4_line_111 | NAYY 4x150 SE | 109 | 120 | 0.0056638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2401-1_0_4_line_112 | NAYY 4x150 SE | 110 | 111 | 0.012282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2401-1_0_4_line_113 | NAYY 4x150 SE | 110 | 112 | 0.026135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2401-1_0_4_line_114 | NAYY 4x150 SE | 112 | 113 | 0.02052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2401-1_0_4_line_115 | NAYY 4x150 SE | 113 | 114 | 0.012518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2401-1_0_4_line_116 | NAYY 4x150 SE | 113 | 115 | 0.04807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2401-1_0_4_line_117 | NAYY 4x150 SE | 114 | 116 | 0.016312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2401-1_0_4_line_118 | NAYY 4x150 SE | 118 | 119 | 0.0063554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2401-1_0_4_line_119 | NAYY 4x150 SE | 119 | 120 | 0.02127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2401-1_0_4_trafo_39 | 0.25 MVA 20/0.4 kV | 121 | 60 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2627061.1517 | 1241486.4424 | 2627066.8504 | 1241489.6206 | 2627068.7558 | 1241492.1194
1 | 2627061.1517 | 1241486.4424 | 2627052.654 | 1241481.7032
2 | 2627068.7558 | 1241492.1194 | 2627070.0449 | 1241493.8101
3 | 2627039.1109 | 1241474.1502 | 2627052.654 | 1241481.7032
4 | 2627078.4274 | 1241498.8135 | 2627070.653 | 1241494.6077 | 2627070.0449 | 1241493.8101
5 | 2627089.7253 | 1241496.5291 | 2627083.918 | 1241501.7838 | 2627078.4274 | 1241498.8135
6 | 2627089.7253 | 1241496.5291 | 2627105.1275 | 1241502.5364
7 | 2627194.7956 | 1241795.531 | 2627191.3389 | 1241793.197
8 | 2627191.3389 | 1241793.197 | 2627165.3569 | 1241775.6542
9 | 2627165.3569 | 1241775.6542 | 2627164.8243 | 1241775.2946
10 | 2627154.7012 | 1241764.7065 | 2627157.676 | 1241770.4682 | 2627164.8243 | 1241775.2946
11 | 2627154.7012 | 1241764.7065 | 2627158.7694 | 1241757.8429 | 2627162.83 | 1241750.9682 | 2627167.8765 | 1241743.4572
12 | 2627239.378 | 1241781.8662 | 2627239.1277 | 1241779.2072
13 | 2627238.5442 | 1241773.0078 | 2627239.1277 | 1241779.2072
14 | 2627238.5442 | 1241773.0078 | 2627237.0521 | 1241757.1534
15 | 2627192.6389 | 1241559.6724 | 2627200.0749 | 1241562.5329
16 | 2627178.5851 | 1241554.2662 | 2627192.6389 | 1241559.6724
17 | 2627207.5851 | 1241565.4219 | 2627200.0749 | 1241562.5329
18 | 2627178.5851 | 1241554.2662 | 2627159.7027 | 1241547.0025 | 2627149.3023 | 1241543.2971 | 2627147.3148 | 1241542.7212
19 | 2627207.5851 | 1241565.4219 | 2627214.4802 | 1241547.1197 | 2627213.6899 | 1241543.069 | 2627210.867 | 1241540.4322 | 2627207.2232 | 1241538.7923 | 2627199.1267 | 1241535.6078
20 | 2627207.5851 | 1241565.4219 | 2627222.161 | 1241570.2798
21 | 2627122.3948 | 1241538.6995 | 2627125.5024 | 1241538.6967 | 2627133.2022 | 1241539.499 | 2627142.4018 | 1241541.2977 | 2627147.3148 | 1241542.7212
22 | 2627199.1267 | 1241535.6078 | 2627182.824 | 1241459.293
23 | 2627222.161 | 1241570.2798 | 2627223.3793 | 1241570.6859
24 | 2627122.3948 | 1241538.6995 | 2627121.6201 | 1241538.7003
25 | 2627223.3793 | 1241570.6859 | 2627244.3579 | 1241577.6776
26 | 2627099.563 | 1241542.4252 | 2627117.3983 | 1241538.7042 | 2627121.6201 | 1241538.7003
27 | 2627167.8765 | 1241743.4572 | 2627167.8953 | 1241743.4293
28 | 2627167.8953 | 1241743.4293 | 2627179.3382 | 1241726.398
29 | 2627179.3382 | 1241726.398 | 2627179.5545 | 1241726.076
30 | 2627105.1275 | 1241502.5364 | 2627099.563 | 1241542.4252
31 | 2627220.3739 | 1241656.3297 | 2627205.7081 | 1241649.6735
32 | 2627220.3739 | 1241656.3297 | 2627226.4957 | 1241659.1081
33 | 2627232.1969 | 1241661.6956 | 2627226.4957 | 1241659.1081
34 | 2627232.1969 | 1241661.6956 | 2627226.3253 | 1241677.0129
35 | 2627232.1969 | 1241661.6956 | 2627243.1145 | 1241666.6785
36 | 2627220.1312 | 1241693.1714 | 2627226.3253 | 1241677.0129
37 | 2627243.1145 | 1241666.6785 | 2627246.0271 | 1241668.0079
38 | 2627220.1312 | 1241693.1714 | 2627205.5939 | 1241684.9663
39 | 2627226.8646 | 1241698.6057 | 2627224.7113 | 1241696.6946 | 2627220.1312 | 1241693.1714
40 | 2627177.7179 | 1241600.1916 | 2627177.0539 | 1241599.8834
41 | 2627156.2558 | 1241590.2324 | 2627177.0539 | 1241599.8834
42 | 2627190.9404 | 1241606.3273 | 2627177.7179 | 1241600.1916
43 | 2627156.2558 | 1241590.2324 | 2627151.3268 | 1241587.9451
44 | 2627137.0157 | 1241583.4297 | 2627146.4401 | 1241585.6775 | 2627151.3268 | 1241587.9451
45 | 2627137.0157 | 1241583.4297 | 2627115.5016 | 1241578.2984 | 2627111.79 | 1241578.0696
46 | 2627085.6944 | 1241576.4614 | 2627111.79 | 1241578.0696
47 | 2627236.6934 | 1241753.3422 | 2627237.0521 | 1241757.1534
48 | 2627236.6934 | 1241753.3422 | 2627232.6828 | 1241710.7289 | 2627232.1761 | 1241709.1487
49 | 2627226.8646 | 1241698.6057 | 2627230.3798 | 1241703.5471 | 2627232.1761 | 1241709.1487
50 | 2627226.8646 | 1241698.6057 | 2627230.3935 | 1241697.2543 | 2627235.0195 | 1241697.3644 | 2627241.7916 | 1241699.9987
51 | 2627067.8045 | 1241677.8428 | 2627065.4534 | 1241675.8841
52 | 2627080.0153 | 1241688.0155 | 2627067.8045 | 1241677.8428
53 | 2627065.4534 | 1241675.8841 | 2627048.1593 | 1241661.4765
54 | 2627080.0153 | 1241688.0155 | 2627086.0024 | 1241693.0033 | 2627086.0024 | 1241693.0033
55 | 2627044.7926 | 1241658.6717 | 2627048.1593 | 1241661.4765
56 | 2627100.6314 | 1241697.7062 | 2627099.3028 | 1241697.2999 | 2627094.2037 | 1241696.4984 | 2627090.3018 | 1241695.102 | 2627086.0024 | 1241693.0033
57 | 2627039.8586 | 1241651.4892 | 2627044.7926 | 1241658.6717
58 | 2627130.1 | 1241697.396 | 2627124.3984 | 1241696.1025 | 2627120.0998 | 1241695.5047 | 2627116.2969 | 1241695.5985 | 2627111.5996 | 1241696.1997 | 2627106.1976 | 1241697.1979 | 2627100.6314 | 1241697.7062
59 | 2627037.1708 | 1241622.503 | 2627039.2524 | 1241638.5115 | 2627039.8586 | 1241651.4892
60 | 2627039.8586 | 1241651.4892 | 2627029.0909 | 1241646.1786
61 | 2627130.1 | 1241697.396 | 2627133.2691 | 1241698.3724
62 | 2627130.1 | 1241697.396 | 2627134.6077 | 1241687.2364
63 | 2627097.9014 | 1241597.8701 | 2627098.9481 | 1241599.7059
64 | 2627114.6629 | 1241632.8847 | 2627112.9867 | 1241627.4625 | 2627105.1562 | 1241610.5939 | 2627098.9481 | 1241599.7059
65 | 2627097.9014 | 1241597.8701 | 2627088.2227 | 1241580.8955
66 | 2627114.6629 | 1241632.8847 | 2627118.7368 | 1241633.0478 | 2627120.9456 | 1241637.7053 | 2627129.6101 | 1241638.8902
67 | 2627109.7838 | 1241641.857 | 2627119.0606 | 1241651.5388 | 2627118.1121 | 1241644.0519 | 2627114.6629 | 1241632.8847
68 | 2627085.6944 | 1241576.4614 | 2627088.2227 | 1241580.8955
69 | 2627129.6101 | 1241638.8902 | 2627150.998 | 1241641.8152
70 | 2627109.7838 | 1241641.857 | 2627106.9011 | 1241642.3998 | 2627105.3972 | 1241642.304 | 2627103.7968 | 1241641.7963 | 2627101.7994 | 1241640.4975 | 2627096.9025 | 1241636.8062 | 2627091.2043 | 1241633.1001 | 2627088.2454 | 1241631.3983
71 | 2627066.1851 | 1241552.713 | 2627073.1999 | 1241559.5048 | 2627085.6944 | 1241576.4614
72 | 2627088.2454 | 1241631.3983 | 2627073.8171 | 1241623.1
73 | 2627066.1851 | 1241552.713 | 2627061.3103 | 1241553.0816
74 | 2627066.1851 | 1241552.713 | 2627086.9457 | 1241546.3142
75 | 2627134.6077 | 1241687.2364 | 2627135.8981 | 1241684.3279
76 | 2627172.8487 | 1241671.0856 | 2627174.2609 | 1241671.4145 | 2627188.9979 | 1241677.2856 | 2627194.1729 | 1241679.6774
77 | 2627172.8487 | 1241671.0856 | 2627175.7725 | 1241656.7936
78 | 2627205.5939 | 1241684.9663 | 2627194.1729 | 1241679.6774
79 | 2627194.1729 | 1241679.6774 | 2627201.9876 | 1241662.0613
80 | 2627175.7725 | 1241656.7936 | 2627176.1486 | 1241654.9553
81 | 2627073.8171 | 1241623.1 | 2627073.297 | 1241622.8009 | 2627067.701 | 1241619.8958 | 2627064.2975 | 1241618.6017 | 2627059.8022 | 1241618.0031 | 2627057.7066 | 1241617.961
82 | 2627241.7916 | 1241699.9987 | 2627254.4068 | 1241704.9057
83 | 2627255.8342 | 1241705.4609 | 2627254.4068 | 1241704.9057
84 | 2627205.5939 | 1241684.9663 | 2627197.0234 | 1241698.6824
85 | 2627061.3103 | 1241553.0816 | 2627058.1509 | 1241553.3205
86 | 2627090.0147 | 1241545.3682 | 2627086.9457 | 1241546.3142
87 | 2627057.7066 | 1241617.961 | 2627054.7982 | 1241617.9025 | 2627047.4016 | 1241618.6026 | 2627043.8974 | 1241619.4984 | 2627042.4198 | 1241620.0546
88 | 2627057.7066 | 1241617.961 | 2627048.476 | 1241599.1007
89 | 2627037.1708 | 1241622.503 | 2627039.8991 | 1241621.0034 | 2627042.4198 | 1241620.0546
90 | 2627037.1708 | 1241622.503 | 2627030.3032 | 1241616.6014 | 2627024.8993 | 1241612.9968 | 2627018.5373 | 1241609.1095
91 | 2627144.1509 | 1241703.9596 | 2627135.3012 | 1241698.9985 | 2627133.2691 | 1241698.3724
92 | 2627144.1509 | 1241703.9596 | 2627151.8973 | 1241708.3024 | 2627156.2279 | 1241710.0975
93 | 2627156.2279 | 1241710.0975 | 2627165.4034 | 1241713.9009 | 2627169.5582 | 1241715.3772
94 | 2627099.563 | 1241542.4252 | 2627090.0147 | 1241545.3682
95 | 2626969.1057 | 1241544.3252 | 2626977.2424 | 1241545.3466
96 | 2626995.2055 | 1241547.6014 | 2626977.2424 | 1241545.3466
97 | 2627012.6477 | 1241550.8658 | 2627004.0017 | 1241548.7056 | 2626995.2055 | 1241547.6014
98 | 2627012.6477 | 1241550.8658 | 2627024.3974 | 1241553.8015 | 2627029.0043 | 1241554.8008 | 2627032.9038 | 1241555.0965 | 2627035.7832 | 1241554.968
99 | 2627037.56 | 1241554.8775 | 2627037.1986 | 1241554.9048 | 2627035.7832 | 1241554.968
100 | 2627184.5832 | 1241718.5916 | 2627172.2186 | 1241716.3225 | 2627169.5582 | 1241715.3772
101 | 2627184.5832 | 1241718.5916 | 2627179.5545 | 1241726.076
102 | 2627184.5832 | 1241718.5916 | 2627197.0234 | 1241698.6824
103 | 2627255.8342 | 1241705.4609 | 2627275.9229 | 1241713.2749
104 | 2627299.3303 | 1241724.8739 | 2627295.5984 | 1241722.8028 | 2627277.7983 | 1241714.0044 | 2627275.9229 | 1241713.2749
105 | 2627037.56 | 1241554.8775 | 2627058.1509 | 1241553.3205
106 | 2627018.5373 | 1241609.1095 | 2627015.898 | 1241607.4968 | 2627008.5993 | 1241603.3055 | 2627007.025 | 1241602.2781
107 | 2627014.2049 | 1241638.5711 | 2627023.3853 | 1241643.3647 | 2627029.0909 | 1241646.1786
108 | 2626987.2009 | 1241617.6063 | 2626958.7534 | 1241622.7138
109 | 2626975.4353 | 1241593.2263 | 2626977.3031 | 1241599.7834 | 2626987.2009 | 1241617.6063
110 | 2626975.4353 | 1241593.2263 | 2626961.1982 | 1241581.9522
111 | 2626975.4353 | 1241593.2263 | 2626981.0218 | 1241594.1593
112 | 2626944.626 | 1241564.3135 | 2626954.7652 | 1241566.9827 | 2626956.5594 | 1241567.0968
113 | 2626920.119 | 1241555.285 | 2626941.4004 | 1241563.4643 | 2626944.626 | 1241564.3135
114 | 2626920.119 | 1241555.285 | 2626925.3332 | 1241560.7343 | 2626936.9574 | 1241566.5047
115 | 2626936.9574 | 1241566.5047 | 2626945.6534 | 1241570.8216 | 2626947.9443 | 1241572.4474
116 | 2626936.9574 | 1241566.5047 | 2626909.0352 | 1241605.6334
117 | 2626961.1982 | 1241581.9522 | 2626960.001 | 1241581.0042 | 2626947.9443 | 1241572.4474
118 | 2627007.025 | 1241602.2781 | 2627001.7026 | 1241598.8046 | 2627001.7026 | 1241598.8046
119 | 2627001.7026 | 1241598.8046 | 2626996.065 | 1241596.7222 | 2626985.8372 | 1241594.9635 | 2626981.0218 | 1241594.1593

## bus_geodata
| x | y | coords
0 | 2627061.1517 | 1241486.4424
1 | 2627068.7558 | 1241492.1194
2 | 2627052.654 | 1241481.7032
3 | 2627070.0449 | 1241493.8101
4 | 2627039.1109 | 1241474.1502
5 | 2627078.4274 | 1241498.8135
6 | 2627089.7253 | 1241496.5291
7 | 2627194.7956 | 1241795.531
8 | 2627191.3389 | 1241793.197
9 | 2627165.3569 | 1241775.6542
10 | 2627164.8243 | 1241775.2946
11 | 2627154.7012 | 1241764.7065
12 | 2627239.378 | 1241781.8662
13 | 2627239.1277 | 1241779.2072
14 | 2627238.5442 | 1241773.0078
15 | 2627192.6389 | 1241559.6724
16 | 2627200.0749 | 1241562.5329
17 | 2627178.5851 | 1241554.2662
18 | 2627207.5851 | 1241565.4219
19 | 2627147.3148 | 1241542.7212
20 | 2627199.1267 | 1241535.6078
21 | 2627222.161 | 1241570.2798
22 | 2627122.3948 | 1241538.6995
23 | 2627182.824 | 1241459.293
24 | 2627223.3793 | 1241570.6859
25 | 2627121.6201 | 1241538.7003
26 | 2627167.8765 | 1241743.4572
27 | 2627167.8953 | 1241743.4293
28 | 2627179.3382 | 1241726.398
29 | 2627105.1275 | 1241502.5364
30 | 2627220.3739 | 1241656.3297
31 | 2627205.7081 | 1241649.6735
32 | 2627226.4957 | 1241659.1081
33 | 2627232.1969 | 1241661.6956
34 | 2627226.3253 | 1241677.0129
35 | 2627243.1145 | 1241666.6785
36 | 2627220.1312 | 1241693.1714
37 | 2627246.0271 | 1241668.0079
38 | 2627177.0539 | 1241599.8834
39 | 2627177.7179 | 1241600.1916
40 | 2627156.2558 | 1241590.2324
41 | 2627190.9404 | 1241606.3273
42 | 2627151.3268 | 1241587.9451
43 | 2627137.0157 | 1241583.4297
44 | 2627111.79 | 1241578.0696
45 | 2627237.0521 | 1241757.1534
46 | 2627236.6934 | 1241753.3422
47 | 2627232.1761 | 1241709.1487
48 | 2627226.8646 | 1241698.6057
49 | 2627067.8045 | 1241677.8428
50 | 2627065.4534 | 1241675.8841
51 | 2627080.0153 | 1241688.0155
52 | 2627048.1593 | 1241661.4765
53 | 2627086.0024 | 1241693.0033
54 | 2627044.7926 | 1241658.6717
55 | 2627100.6314 | 1241697.7062
56 | 2627039.8586 | 1241651.4892
57 | 2627130.1 | 1241697.396
58 | 2627098.9481 | 1241599.7059
59 | 2627097.9014 | 1241597.8701
60 | 2627114.6629 | 1241632.8847
61 | 2627088.2227 | 1241580.8955
62 | 2627129.6101 | 1241638.8902
63 | 2627109.7838 | 1241641.857
64 | 2627085.6944 | 1241576.4614
65 | 2627150.998 | 1241641.8152
66 | 2627088.2454 | 1241631.3983
67 | 2627066.1851 | 1241552.713
68 | 2627135.8981 | 1241684.3279
69 | 2627134.6077 | 1241687.2364
70 | 2627172.8487 | 1241671.0856
71 | 2627194.1729 | 1241679.6774
72 | 2627175.7725 | 1241656.7936
73 | 2627073.8171 | 1241623.1
74 | 2627244.3579 | 1241577.6776
75 | 2627241.7916 | 1241699.9987
76 | 2627254.4069 | 1241704.9057
77 | 2627205.5939 | 1241684.9663
78 | 2627061.3103 | 1241553.0816
79 | 2627086.9457 | 1241546.3142
80 | 2627057.7066 | 1241617.961
81 | 2627042.4198 | 1241620.0546
82 | 2627048.476 | 1241599.1007
83 | 2627037.1708 | 1241622.503
84 | 2627133.2691 | 1241698.3724
85 | 2627144.1509 | 1241703.9596
86 | 2627156.2279 | 1241710.0975
87 | 2627099.563 | 1241542.4252
88 | 2626969.1057 | 1241544.3252
89 | 2626977.2424 | 1241545.3466
90 | 2626995.2055 | 1241547.6014
91 | 2627012.6477 | 1241550.8658
92 | 2627035.7832 | 1241554.968
93 | 2627169.5582 | 1241715.3772
94 | 2627184.5832 | 1241718.5916
95 | 2627179.5545 | 1241726.076
96 | 2627197.0234 | 1241698.6824
97 | 2627255.8341 | 1241705.4609
98 | 2627275.9229 | 1241713.2749
99 | 2627299.3303 | 1241724.8739
100 | 2627090.0147 | 1241545.3682
101 | 2627058.1509 | 1241553.3205
102 | 2627018.5373 | 1241609.1095
103 | 2627176.1486 | 1241654.9553
104 | 2627201.9876 | 1241662.0613
105 | 2627014.2049 | 1241638.5711
106 | 2627029.0909 | 1241646.1786
107 | 2626958.7534 | 1241622.7138
108 | 2626987.2009 | 1241617.6063
109 | 2626975.4353 | 1241593.2263
110 | 2626944.626 | 1241564.3135
111 | 2626956.5594 | 1241567.0968
112 | 2626920.119 | 1241555.285
113 | 2626936.9574 | 1241566.5047
114 | 2626947.9443 | 1241572.4474
115 | 2626909.0352 | 1241605.6334
116 | 2626961.1982 | 1241581.9522
117 | 2627037.56 | 1241554.8775
118 | 2627007.025 | 1241602.2781
119 | 2627001.7026 | 1241598.8046
120 | 2626981.0218 | 1241594.1593
121 | 2627119.0606 | 1241651.5388

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98831 | -0.081956 | 0.00083452 | 0.00020915
1 | 0.98835 | -0.081709 | 0.0018128 | 0.00045432
2 | 0.98829 | -0.082121 | 0.0008337 | 0.00020895
3 | 0.98836 | -0.081615 | 0.0013178 | 0.00033027
4 | 0.98827 | -0.082253 | 0.00083098 | 0.00020826
5 | 0.98844 | -0.081048 | 0.0013175 | 0.00033019
6 | 0.98858 | -0.080049 | 0 | 0
7 | 0.97266 | -0.19205 | 0.0017984 | 0.00045072
8 | 0.97268 | -0.19197 | 0.0033835 | 0.00084798
9 | 0.97291 | -0.19026 | 0.00434 | 0.0010877
10 | 0.97292 | -0.19019 | 0.0034293 | 0.00085945
11 | 0.97321 | -0.18813 | 0 | 0
12 | 0.97048 | -0.20776 | 0.0014409 | 0.00036111
13 | 0.97049 | -0.20772 | 0.0020289 | 0.00050849
14 | 0.97052 | -0.20749 | 0.0021583 | 0.00054093
15 | 0.98671 | -0.093312 | 0.0016632 | 0.00041683
16 | 0.98657 | -0.094307 | 0.00091827 | 0.00023014
17 | 0.98701 | -0.091176 | 0.0016996 | 0.00042597
18 | 0.98644 | -0.095236 | 0 | 0
19 | 0.98776 | -0.085871 | 0.0020586 | 0.00051594
20 | 0.98607 | -0.097886 | 0.0027627 | 0.00069241
21 | 0.98633 | -0.095998 | 0.0014819 | 0.0003714
22 | 0.9884 | -0.081311 | 0.0016934 | 0.00042439
23 | 0.98566 | -0.10081 | 0.0036466 | 0.00091391
24 | 0.98633 | -0.096042 | 0.0020847 | 0.00052248
25 | 0.98843 | -0.081158 | 0.0031319 | 0.00078492
26 | 0.97368 | -0.18471 | 0.0033746 | 0.00084575
27 | 0.97368 | -0.18471 | 0.0024999 | 0.00062653
28 | 0.97425 | -0.18064 | 0.0019502 | 0.00048878
29 | 0.98875 | -0.078878 | 0 | 0
30 | 0.97114 | -0.20298 | 0.0011308 | 0.00028341
31 | 0.9711 | -0.2033 | 0.0018656 | 0.00046756
32 | 0.97117 | -0.20277 | 0.0020818 | 0.00052176
33 | 0.97122 | -0.20243 | 0 | 0
34 | 0.97146 | -0.20072 | 0.0010598 | 0.00026562
35 | 0.97113 | -0.20304 | 0.00292 | 0.00073181
36 | 0.97174 | -0.19871 | 0 | 0
37 | 0.97113 | -0.20311 | 0.0018946 | 0.00047483
38 | 0.99152 | -0.059308 | 0.001334 | 0.00033434
39 | 0.99152 | -0.059352 | 0.0041577 | 0.001042
40 | 0.99176 | -0.057618 | 0.0027633 | 0.00069254
41 | 0.99148 | -0.059614 | 0.0017673 | 0.00044294
42 | 0.99184 | -0.057066 | 0.0017216 | 0.00043146
43 | 0.9921 | -0.055269 | 0.0016019 | 0.00040147
44 | 0.99259 | -0.051773 | 0.001616 | 0.000405
45 | 0.97065 | -0.20654 | 0.0013567 | 0.00034001
46 | 0.97069 | -0.20626 | 0.0012831 | 0.00032158
47 | 0.97123 | -0.20237 | 0.0028382 | 0.00071132
48 | 0.97142 | -0.20096 | 0 | 0
49 | 0.98243 | -0.12237 | 0.0018687 | 0.00046835
50 | 0.98265 | -0.12085 | 0.0024772 | 0.00062085
51 | 0.98134 | -0.13008 | 0.001351 | 0.0003386
52 | 0.98426 | -0.10945 | 0.0021783 | 0.00054592
53 | 0.98082 | -0.13381 | 0.0018426 | 0.00046181
54 | 0.98459 | -0.10719 | 0.0040505 | 0.0010151
55 | 0.97979 | -0.1411 | 0 | 0
56 | 0.98525 | -0.10251 | 0 | 0
57 | 0.97782 | -0.15512 | 0 | 0
58 | 0.9959 | -0.02855 | 0.0027608 | 0.00069191
59 | 0.99567 | -0.030137 | 0.002633 | 0.0006599
60 | 1 | 0 | -0.24556 | -0.061866
61 | 0.99365 | -0.044331 | 0.0046042 | 0.0011539
62 | 0.99978 | -0.0015426 | 0.0042973 | 0.001077
63 | 0.99632 | -0.025316 | 0 | 0
64 | 0.99315 | -0.04781 | 0 | 0
65 | 0.99965 | -0.0024689 | 0.0042959 | 0.0010767
66 | 0.99352 | -0.044709 | 0.004246 | 0.0010642
67 | 0.99083 | -0.064182 | 0 | 0
68 | 0.97768 | -0.15615 | 0.0050665 | 0.0012698
69 | 0.9777 | -0.15598 | 0.0023176 | 0.00058086
70 | 0.97212 | -0.19597 | 0 | 0
71 | 0.9724 | -0.1939 | 0 | 0
72 | 0.97193 | -0.19728 | 0.0030713 | 0.00076974
73 | 0.99169 | -0.057403 | 0.0015573 | 0.0003903
74 | 0.98629 | -0.09633 | 0.0012675 | 0.00031767
75 | 0.97111 | -0.20321 | 0.0015113 | 0.00037878
76 | 0.97087 | -0.20493 | 0.0031633 | 0.00079281
77 | 0.97261 | -0.19245 | 0 | 0
78 | 0.99071 | -0.065042 | 0.0022278 | 0.00055834
79 | 0.98973 | -0.071947 | 0.0022045 | 0.00055251
80 | 0.98983 | -0.070417 | 0.0016719 | 0.00041901
81 | 0.9882 | -0.081817 | 0.0016795 | 0.00042093
82 | 0.98972 | -0.071165 | 0.0034981 | 0.0008767
83 | 0.9876 | -0.086038 | 0 | 0
84 | 0.97762 | -0.15656 | 0.00506 | 0.0012682
85 | 0.97691 | -0.16157 | 0.0020841 | 0.00052232
86 | 0.97616 | -0.16697 | 0.0019559 | 0.0004902
87 | 0.98915 | -0.076019 | 0 | 0
88 | 0.98944 | -0.073988 | 0.0024858 | 0.00062299
89 | 0.98947 | -0.073781 | 0.0031099 | 0.00077942
90 | 0.98962 | -0.072748 | 0.0026474 | 0.00066349
91 | 0.98983 | -0.071254 | 0.0024619 | 0.00061702
92 | 0.99019 | -0.068678 | 0.0012929 | 0.00032402
93 | 0.97538 | -0.17254 | 0.0016954 | 0.00042492
94 | 0.97456 | -0.17839 | 0 | 0
95 | 0.97426 | -0.18056 | 0.0020745 | 0.00051992
96 | 0.97371 | -0.18451 | 0.0029309 | 0.00073454
97 | 0.97085 | -0.20507 | 0.0053347 | 0.001337
98 | 0.97074 | -0.20587 | 0.00086114 | 0.00021582
99 | 0.97064 | -0.20661 | 0.002652 | 0.00066465
100 | 0.98958 | -0.073025 | 0.0035213 | 0.00088253
101 | 0.99064 | -0.065528 | 0.0011126 | 0.00027883
102 | 0.98654 | -0.09356 | 0.0010952 | 0.00027449
103 | 0.97192 | -0.19739 | 0.0054523 | 0.0013665
104 | 0.97233 | -0.19441 | 0.0024602 | 0.00061659
105 | 0.98506 | -0.10387 | 0.0036896 | 0.00092469
106 | 0.98515 | -0.10324 | 0.0021757 | 0.00054527
107 | 0.98426 | -0.10974 | 0.0041372 | 0.0010369
108 | 0.98443 | -0.10851 | 0.0021829 | 0.0005471
109 | 0.98468 | -0.10674 | 0 | 0
110 | 0.98346 | -0.11542 | 0.0030346 | 0.00076054
111 | 0.98342 | -0.11568 | 0.0020754 | 0.00052015
112 | 0.98365 | -0.11404 | 0 | 0
113 | 0.98381 | -0.11296 | 0.0023437 | 0.00058739
114 | 0.98399 | -0.11162 | 0.0019801 | 0.00049626
115 | 0.9836 | -0.11439 | 0.0028812 | 0.00072211
116 | 0.98428 | -0.10955 | 0.0027065 | 0.00067831
117 | 0.99022 | -0.068461 | 0.0019548 | 0.00048991
118 | 0.98594 | -0.097795 | 0.0015955 | 0.00039988
119 | 0.98567 | -0.099702 | 0.0027394 | 0.00068656
120 | 0.98485 | -0.10549 | 0.0051215 | 0.0012836
121 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0024993 | -0.00062606 | 0.0024993 | 0.00062597 | 8.5411e-08 | -9.1037e-08 | 0.0037628 | 0.0037628 | 0.0037628 | 0.98831 | -0.081956 | 0.98835 | -0.081709 | 1.3936
1 | 0.0016647 | 0.00041691 | -0.0016647 | -0.00041702 | 3.814e-08 | -1.1001e-07 | 0.0025063 | 0.0025064 | 0.0025064 | 0.98831 | -0.081956 | 0.98829 | -0.082121 | 0.92829
2 | -0.0043121 | -0.0010803 | 0.0043122 | 0.0010803 | 5.5913e-08 | -5.7417e-09 | 0.006492 | 0.006492 | 0.006492 | 0.98835 | -0.081709 | 0.98836 | -0.081615 | 2.4044
3 | 0.000831 | 0.00020807 | -0.00083098 | -0.00020826 | 1.5147e-08 | -1.9287e-07 | 0.0012511 | 0.0012512 | 0.0012512 | 0.98829 | -0.082121 | 0.98827 | -0.082253 | 0.4634
4 | -0.00563 | -0.0014106 | 0.0056304 | 0.0014106 | 4.4121e-07 | 4.3553e-08 | 0.008476 | 0.0084759 | 0.008476 | 0.98836 | -0.081615 | 0.98844 | -0.081048 | 3.1392
5 | -0.0069479 | -0.0017408 | 0.0069489 | 0.001741 | 9.6075e-07 | 1.8909e-07 | 0.010459 | 0.010459 | 0.010459 | 0.98844 | -0.081048 | 0.98858 | -0.080049 | 3.8738
6 | -0.0069489 | -0.001741 | 0.00695 | 0.0017412 | 1.1256e-06 | 2.2148e-07 | 0.010459 | 0.010459 | 0.010459 | 0.98858 | -0.080049 | 0.98875 | -0.078878 | 3.8738
7 | -0.0017984 | -0.00045072 | 0.0017984 | 0.00045068 | 1.97e-08 | -4.4192e-08 | 0.0027513 | 0.0027512 | 0.0027513 | 0.97266 | -0.19205 | 0.97268 | -0.19197 | 1.019
8 | -0.0051819 | -0.0012987 | 0.0051831 | 0.0012987 | 1.2293e-06 | 8.3607e-08 | 0.0079274 | 0.0079272 | 0.0079274 | 0.97268 | -0.19197 | 0.97291 | -0.19026 | 2.9361
9 | -0.0095231 | -0.0023864 | 0.0095232 | 0.0023865 | 8.5059e-08 | 2.4736e-08 | 0.014565 | 0.014565 | 0.014565 | 0.97291 | -0.19026 | 0.97292 | -0.19019 | 5.3944
10 | -0.012952 | -0.0032459 | 0.012956 | 0.0032472 | 3.6999e-06 | 1.2354e-06 | 0.01981 | 0.01981 | 0.01981 | 0.97292 | -0.19019 | 0.97321 | -0.18813 | 7.3369
11 | -0.012956 | -0.0032472 | 0.012962 | 0.0032492 | 6.1247e-06 | 2.0447e-06 | 0.01981 | 0.01981 | 0.01981 | 0.97321 | -0.18813 | 0.97368 | -0.18471 | 7.3369
12 | -0.0014409 | -0.00036111 | 0.0014409 | 0.00036108 | 8.1338e-09 | -2.9871e-08 | 0.0022092 | 0.0022092 | 0.0022092 | 0.97048 | -0.20776 | 0.97049 | -0.20772 | 0.81823
13 | -0.0034698 | -0.00086958 | 0.0034699 | 0.00086954 | 1.0997e-07 | -3.4646e-08 | 0.0053201 | 0.0053201 | 0.0053201 | 0.97049 | -0.20772 | 0.97052 | -0.20749 | 1.9704
14 | -0.0056282 | -0.0014105 | 0.005629 | 0.0014106 | 7.3994e-07 | 8.7784e-08 | 0.0086293 | 0.0086292 | 0.0086293 | 0.97052 | -0.20749 | 0.97065 | -0.20654 | 3.196
15 | 0.012169 | 0.0030487 | -0.012168 | -0.0030482 | 1.6743e-06 | 5.4221e-07 | 0.018351 | 0.018352 | 0.018352 | 0.98671 | -0.093312 | 0.98657 | -0.094307 | 6.7969
16 | -0.013832 | -0.0034655 | 0.013837 | 0.0034669 | 4.0885e-06 | 1.3801e-06 | 0.02086 | 0.02086 | 0.02086 | 0.98671 | -0.093312 | 0.98701 | -0.091176 | 7.7258
17 | 0.011249 | 0.002818 | -0.011248 | -0.0028176 | 1.4454e-06 | 4.5319e-07 | 0.016967 | 0.016967 | 0.016967 | 0.98657 | -0.094307 | 0.98644 | -0.095236 | 6.2839
18 | -0.015536 | -0.0038929 | 0.015548 | 0.0038968 | 1.1413e-05 | 3.9633e-06 | 0.023422 | 0.023422 | 0.023422 | 0.98701 | -0.091176 | 0.98776 | -0.085871 | 8.6748
19 | 0.0064131 | 0.0016063 | -0.0064108 | -0.0016059 | 2.35e-06 | 3.903e-07 | 0.0096736 | 0.0096738 | 0.0096738 | 0.98644 | -0.095236 | 0.98607 | -0.097886 | 3.5829
20 | 0.0048347 | 0.0012113 | -0.0048342 | -0.0012113 | 5.0992e-07 | 5.1058e-12 | 0.0072929 | 0.007293 | 0.007293 | 0.98644 | -0.095236 | 0.98633 | -0.095998 | 2.7011
21 | -0.017606 | -0.0044128 | 0.017617 | 0.0044167 | 1.1122e-05 | 3.9533e-06 | 0.026523 | 0.026523 | 0.026523 | 0.98776 | -0.085871 | 0.9884 | -0.081311 | 9.8233
22 | 0.003648 | 0.00091349 | -0.0036466 | -0.00091391 | 1.4757e-06 | -4.2748e-07 | 0.0055047 | 0.0055051 | 0.0055051 | 0.98607 | -0.097886 | 0.98566 | -0.10081 | 2.0389
23 | 0.0033523 | 0.00083988 | -0.0033523 | -0.00083989 | 2.0495e-08 | -8.5073e-09 | 0.0050573 | 0.0050573 | 0.0050573 | 0.98633 | -0.095998 | 0.98633 | -0.096042 | 1.8731
24 | -0.019311 | -0.0048411 | 0.019311 | 0.0048413 | 4.0858e-07 | 1.4722e-07 | 0.029072 | 0.029072 | 0.029072 | 0.9884 | -0.081311 | 0.98843 | -0.081158 | 10.7675
25 | 0.0012676 | 0.00031741 | -0.0012675 | -0.00031767 | 5.0459e-08 | -2.6281e-07 | 0.0019122 | 0.0019123 | 0.0019123 | 0.98633 | -0.096042 | 0.98629 | -0.09633 | 0.70827
26 | -0.022443 | -0.0056262 | 0.022459 | 0.0056321 | 1.5986e-05 | 5.8605e-06 | 0.033787 | 0.033787 | 0.033787 | 0.98843 | -0.081158 | 0.98915 | -0.076019 | 12.5137
27 | -0.016337 | -0.0040949 | 0.016337 | 0.0040949 | 1.31e-08 | 4.6202e-09 | 0.024967 | 0.024967 | 0.024967 | 0.97368 | -0.18471 | 0.97368 | -0.18471 | 9.2469
28 | -0.018837 | -0.0047215 | 0.018847 | 0.0047253 | 1.061e-05 | 3.8255e-06 | 0.028787 | 0.028787 | 0.028787 | 0.97368 | -0.18471 | 0.97425 | -0.18064 | 10.6619
29 | -0.020798 | -0.0052141 | 0.020798 | 0.0052142 | 2.4426e-07 | 8.9117e-08 | 0.031766 | 0.031766 | 0.031766 | 0.97425 | -0.18064 | 0.97426 | -0.18056 | 11.7651
30 | -0.00695 | -0.0017412 | 0.0069527 | 0.0017417 | 2.7494e-06 | 5.4065e-07 | 0.010459 | 0.010459 | 0.010459 | 0.98875 | -0.078878 | 0.98915 | -0.076019 | 3.8738
31 | 0.0018657 | 0.0004674 | -0.0018656 | -0.00046756 | 8.2126e-08 | -1.6768e-07 | 0.0028586 | 0.0028587 | 0.0028587 | 0.97114 | -0.20298 | 0.9711 | -0.2033 | 1.0588
32 | -0.0029965 | -0.00075081 | 0.0029966 | 0.00075076 | 8.8431e-08 | -4.9172e-08 | 0.0045913 | 0.0045913 | 0.0045913 | 0.97114 | -0.20298 | 0.97117 | -0.20277 | 1.7005
33 | -0.0050784 | -0.0012725 | 0.0050787 | 0.0012725 | 2.3653e-07 | 1.35e-08 | 0.007781 | 0.007781 | 0.007781 | 0.97117 | -0.20277 | 0.97122 | -0.20243 | 2.8819
34 | -0.0098937 | -0.0024791 | 0.009896 | 0.0024798 | 2.3519e-06 | 7.0153e-07 | 0.015158 | 0.015158 | 0.015158 | 0.97122 | -0.20243 | 0.97146 | -0.20072 | 5.6141
35 | 0.004815 | 0.0012066 | -0.0048146 | -0.0012066 | 4.0754e-07 | 8.2463e-09 | 0.007377 | 0.0073771 | 0.0073771 | 0.97122 | -0.20243 | 0.97113 | -0.20304 | 2.7323
36 | -0.010956 | -0.0027455 | 0.010959 | 0.0027464 | 3.0409e-06 | 9.5527e-07 | 0.016781 | 0.016781 | 0.016781 | 0.97146 | -0.20072 | 0.97174 | -0.19871 | 6.2153
37 | 0.0018946 | 0.0004748 | -0.0018946 | -0.00047483 | 1.6837e-08 | -3.3138e-08 | 0.002903 | 0.002903 | 0.002903 | 0.97113 | -0.20304 | 0.97113 | -0.20311 | 1.0752
38 | -0.035611 | -0.0089258 | 0.035642 | 0.0089375 | 3.0906e-05 | 1.168e-05 | 0.054531 | 0.054531 | 0.054531 | 0.97174 | -0.19871 | 0.97261 | -0.19245 | 20.1967
39 | 0.024652 | 0.0061794 | -0.024644 | -0.0061765 | 7.6847e-06 | 2.8486e-06 | 0.03775 | 0.03775 | 0.03775 | 0.97174 | -0.19871 | 0.97142 | -0.20096 | 13.9814
40 | 0.0059251 | 0.0014848 | -0.0059251 | -0.0014848 | 3.6114e-08 | 4.4492e-09 | 0.0088919 | 0.0088919 | 0.0088919 | 0.99152 | -0.059308 | 0.99152 | -0.059352 | 3.2933
41 | -0.0072591 | -0.0018191 | 0.0072608 | 0.0018195 | 1.6979e-06 | 3.5726e-07 | 0.010894 | 0.010894 | 0.010894 | 0.99152 | -0.059308 | 0.99176 | -0.057618 | 4.0348
42 | 0.0017674 | 0.00044277 | -0.0017673 | -0.00044294 | 6.3991e-08 | -1.6339e-07 | 0.0026524 | 0.0026524 | 0.0026524 | 0.99152 | -0.059352 | 0.99148 | -0.059614 | 0.98238
43 | -0.010024 | -0.002512 | 0.010025 | 0.0025122 | 7.6697e-07 | 2.2486e-07 | 0.01504 | 0.01504 | 0.01504 | 0.99176 | -0.057618 | 0.99184 | -0.057066 | 5.5703
44 | -0.011746 | -0.0029437 | 0.011749 | 0.0029446 | 2.9215e-06 | 9.2903e-07 | 0.017623 | 0.017623 | 0.017623 | 0.99184 | -0.057066 | 0.9921 | -0.055269 | 6.5269
45 | -0.013351 | -0.0033461 | 0.013358 | 0.0033483 | 6.4649e-06 | 2.1527e-06 | 0.020025 | 0.020025 | 0.020025 | 0.9921 | -0.055269 | 0.99259 | -0.051773 | 7.4167
46 | -0.014974 | -0.0037533 | 0.014982 | 0.0037561 | 8.2207e-06 | 2.8237e-06 | 0.022448 | 0.022447 | 0.022448 | 0.99259 | -0.051773 | 0.99315 | -0.04781 | 8.3139
47 | -0.0069856 | -0.0017506 | 0.0069859 | 0.0017506 | 2.7394e-07 | 5.8043e-08 | 0.010709 | 0.010709 | 0.010709 | 0.97065 | -0.20654 | 0.97069 | -0.20626 | 3.9663
48 | -0.008269 | -0.0020722 | 0.0082735 | 0.0020734 | 4.4577e-06 | 1.1646e-06 | 0.012676 | 0.012676 | 0.012676 | 0.97069 | -0.20626 | 0.97123 | -0.20237 | 4.6948
49 | -0.011112 | -0.0027847 | 0.011114 | 0.0027854 | 2.1605e-06 | 6.831e-07 | 0.017024 | 0.017024 | 0.017024 | 0.97123 | -0.20237 | 0.97142 | -0.20096 | 6.3052
50 | 0.01353 | 0.0033911 | -0.013526 | -0.0033897 | 4.201e-06 | 1.4218e-06 | 0.020726 | 0.020726 | 0.020726 | 0.97142 | -0.20096 | 0.97111 | -0.20321 | 7.6762
51 | -0.096444 | -0.024276 | 0.096465 | 0.024284 | 2.0384e-05 | 7.7623e-06 | 0.14611 | 0.14611 | 0.14611 | 0.98243 | -0.12237 | 0.98265 | -0.12085 | 27.0582
52 | 0.094576 | 0.023808 | -0.094474 | -0.023769 | 0.0001018 | 3.8752e-05 | 0.14328 | 0.14328 | 0.14328 | 0.98243 | -0.12237 | 0.98134 | -0.13008 | 26.5341
53 | -0.098942 | -0.024905 | 0.0991 | 0.024965 | 0.00015773 | 6.0095e-05 | 0.14987 | 0.14987 | 0.14987 | 0.98265 | -0.12085 | 0.98426 | -0.10945 | 27.7528
54 | 0.093123 | 0.023431 | -0.093074 | -0.023412 | 4.8497e-05 | 1.8456e-05 | 0.14124 | 0.14124 | 0.14124 | 0.98134 | -0.13008 | 0.98082 | -0.13381 | 26.1547
55 | -0.10128 | -0.025511 | 0.10131 | 0.025523 | 3.207e-05 | 1.2223e-05 | 0.15316 | 0.15316 | 0.15316 | 0.98426 | -0.10945 | 0.98459 | -0.10719 | 28.3626
56 | 0.091232 | 0.02295 | -0.091139 | -0.022915 | 9.2563e-05 | 3.5211e-05 | 0.13844 | 0.13844 | 0.13844 | 0.98082 | -0.13381 | 0.97979 | -0.1411 | 25.637
57 | -0.10536 | -0.026538 | 0.10543 | 0.026565 | 6.8975e-05 | 2.6307e-05 | 0.15928 | 0.15928 | 0.15928 | 0.98459 | -0.10719 | 0.98525 | -0.10251 | 29.4962
58 | 0.091139 | 0.022915 | -0.090961 | -0.022847 | 0.00017773 | 6.7612e-05 | 0.13844 | 0.13844 | 0.13844 | 0.97979 | -0.1411 | 0.97782 | -0.15512 | 25.6371
59 | -0.1113 | -0.028034 | 0.11155 | 0.028133 | 0.00025701 | 9.8106e-05 | 0.16814 | 0.16814 | 0.16814 | 0.98525 | -0.10251 | 0.9876 | -0.086038 | 31.1369
60 | 0.0058662 | 0.00147 | -0.0058656 | -0.0014699 | 5.8804e-07 | 7.3287e-08 | 0.0088595 | 0.0088596 | 0.0088596 | 0.98525 | -0.10251 | 0.98515 | -0.10324 | 3.2813
61 | 0.083576 | 0.020997 | -0.083559 | -0.02099 | 1.674e-05 | 6.3555e-06 | 0.1272 | 0.1272 | 0.1272 | 0.97782 | -0.15512 | 0.97762 | -0.15656 | 23.5559
62 | 0.0073852 | 0.0018509 | -0.0073843 | -0.0018507 | 8.7599e-07 | 1.9752e-07 | 0.011239 | 0.011239 | 0.011239 | 0.97782 | -0.15512 | 0.9777 | -0.15598 | 4.1624
63 | 0.075032 | 0.018857 | -0.075015 | -0.018851 | 1.6579e-05 | 6.3489e-06 | 0.11213 | 0.11213 | 0.11213 | 0.9959 | -0.02855 | 0.99567 | -0.030137 | 41.5283
64 | -0.077792 | -0.019549 | 0.078103 | 0.019668 | 0.00031039 | 0.0001189 | 0.11625 | 0.11625 | 0.11625 | 0.9959 | -0.02855 | 1 | 0 | 43.056
65 | 0.072382 | 0.018191 | -0.072239 | -0.018136 | 0.00014272 | 5.464e-05 | 0.10819 | 0.10819 | 0.10819 | 0.99567 | -0.030137 | 0.99365 | -0.044331 | 40.0709
66 | 0.0085955 | 0.002154 | -0.0085937 | -0.0021536 | 1.8351e-06 | 4.7002e-07 | 0.01279 | 0.01279 | 0.01279 | 1 | 0 | 0.99978 | -0.0015426 | 4.7372
67 | 0.15806 | 0.040043 | -0.15749 | -0.039827 | 0.0005641 | 0.00021611 | 0.23534 | 0.23534 | 0.23534 | 1 | 0 | 0.99632 | -0.025316 | 43.5822
68 | 0.067635 | 0.016982 | -0.067602 | -0.01697 | 3.2682e-05 | 1.2504e-05 | 0.1013 | 0.1013 | 0.1013 | 0.99365 | -0.044331 | 0.99315 | -0.04781 | 37.5172
69 | 0.0042964 | 0.0010766 | -0.0042959 | -0.0010767 | 5.508e-07 | -7.1196e-08 | 0.0063945 | 0.0063946 | 0.0063946 | 0.99978 | -0.0015426 | 0.99965 | -0.0024689 | 2.3684
70 | 0.15749 | 0.039827 | -0.15706 | -0.039663 | 0.00042934 | 0.00016448 | 0.23534 | 0.23534 | 0.23534 | 0.99632 | -0.025316 | 0.99352 | -0.044709 | 43.5822
71 | 0.05262 | 0.013214 | -0.052501 | -0.013168 | 0.00011946 | 4.5548e-05 | 0.078849 | 0.078849 | 0.078849 | 0.99315 | -0.04781 | 0.99083 | -0.064182 | 29.2034
72 | 0.15282 | 0.038599 | -0.15255 | -0.038494 | 0.00027229 | 0.0001043 | 0.22898 | 0.22898 | 0.22898 | 0.99352 | -0.044709 | 0.99169 | -0.057403 | 42.4046
73 | 0.017308 | 0.0043387 | -0.017306 | -0.004338 | 2.0612e-06 | 7.2982e-07 | 0.025994 | 0.025994 | 0.025994 | 0.99083 | -0.064182 | 0.99071 | -0.065042 | 9.6274
74 | 0.035193 | 0.0088295 | -0.035155 | -0.0088153 | 3.7871e-05 | 1.4286e-05 | 0.052855 | 0.052855 | 0.052855 | 0.99083 | -0.064182 | 0.98973 | -0.071947 | 19.576
75 | -0.0050665 | -0.0012698 | 0.0050667 | 0.0012698 | 1.1807e-07 | 5.5072e-09 | 0.0077112 | 0.0077112 | 0.0077112 | 0.97768 | -0.15615 | 0.9777 | -0.15598 | 2.856
76 | -0.0085252 | -0.0021366 | 0.0085277 | 0.0021373 | 2.4393e-06 | 6.5351e-07 | 0.01305 | 0.013049 | 0.01305 | 0.97212 | -0.19597 | 0.9724 | -0.1939 | 4.8332
77 | 0.0085252 | 0.0021366 | -0.0085237 | -0.0021362 | 1.5501e-06 | 4.1538e-07 | 0.01305 | 0.01305 | 0.01305 | 0.97212 | -0.19597 | 0.97193 | -0.19728 | 4.8332
78 | -0.010988 | -0.0027537 | 0.01099 | 0.0027544 | 2.2151e-06 | 6.9617e-07 | 0.016814 | 0.016814 | 0.016814 | 0.9724 | -0.1939 | 0.97261 | -0.19245 | 6.2275
79 | 0.0024604 | 0.00061641 | -0.0024602 | -0.00061659 | 1.7046e-07 | -1.7349e-07 | 0.0037649 | 0.003765 | 0.003765 | 0.9724 | -0.1939 | 0.97233 | -0.19441 | 1.3944
80 | 0.0054524 | 0.0013665 | -0.0054523 | -0.0013665 | 8.1589e-08 | 8.1256e-09 | 0.0083475 | 0.0083475 | 0.0083475 | 0.97193 | -0.19728 | 0.97192 | -0.19739 | 3.0917
81 | 0.15099 | 0.038104 | -0.15071 | -0.037999 | 0.00027531 | 0.00010544 | 0.22665 | 0.22665 | 0.22665 | 0.99169 | -0.057403 | 0.98983 | -0.070417 | 41.9719
82 | 0.012015 | 0.0030109 | -0.012012 | -0.00301 | 2.8628e-06 | 9.3363e-07 | 0.01841 | 0.01841 | 0.01841 | 0.97111 | -0.20321 | 0.97087 | -0.20493 | 6.8186
83 | 0.0088487 | 0.0022172 | -0.0088485 | -0.0022171 | 1.7576e-07 | 4.8663e-08 | 0.013562 | 0.013562 | 0.013562 | 0.97087 | -0.20493 | 0.97085 | -0.20507 | 5.0229
84 | -0.046632 | -0.011692 | 0.046683 | 0.011711 | 5.1371e-05 | 1.9557e-05 | 0.071345 | 0.071345 | 0.071345 | 0.97261 | -0.19245 | 0.97371 | -0.18451 | 26.4242
85 | 0.015079 | 0.0037797 | -0.015078 | -0.0037793 | 1.0141e-06 | 3.4925e-07 | 0.022648 | 0.022648 | 0.022648 | 0.99071 | -0.065042 | 0.99064 | -0.065528 | 8.3881
86 | 0.03295 | 0.0082627 | -0.032945 | -0.0082609 | 4.9184e-06 | 1.8504e-06 | 0.049541 | 0.049541 | 0.049541 | 0.98973 | -0.071947 | 0.98958 | -0.073025 | 18.3485
87 | 0.14554 | 0.036703 | -0.14531 | -0.036614 | 0.00023219 | 8.8905e-05 | 0.21888 | 0.21888 | 0.21888 | 0.98983 | -0.070417 | 0.9882 | -0.081817 | 40.5326
88 | 0.0034985 | 0.00087657 | -0.0034981 | -0.0008767 | 3.6241e-07 | -1.3048e-07 | 0.0052592 | 0.0052593 | 0.0052593 | 0.98983 | -0.070417 | 0.98972 | -0.071165 | 1.9479
89 | 0.14363 | 0.036193 | -0.14355 | -0.036161 | 8.4798e-05 | 3.2466e-05 | 0.21635 | 0.21635 | 0.21635 | 0.9882 | -0.081817 | 0.9876 | -0.086038 | 40.0642
90 | 0.031993 | 0.0080281 | -0.03196 | -0.0080156 | 3.3364e-05 | 1.2538e-05 | 0.048208 | 0.048208 | 0.048208 | 0.9876 | -0.086038 | 0.98654 | -0.09356 | 17.8549
91 | 0.078499 | 0.019722 | -0.078445 | -0.019701 | 5.4676e-05 | 2.0722e-05 | 0.1195 | 0.1195 | 0.1195 | 0.97762 | -0.15656 | 0.97691 | -0.16157 | 22.1296
92 | 0.076361 | 0.019179 | -0.076303 | -0.019157 | 5.7285e-05 | 2.1693e-05 | 0.11633 | 0.11633 | 0.11633 | 0.97691 | -0.16157 | 0.97616 | -0.16697 | 21.5418
93 | 0.074347 | 0.018667 | -0.07429 | -0.018645 | 5.7486e-05 | 2.1752e-05 | 0.11334 | 0.11334 | 0.11334 | 0.97616 | -0.16697 | 0.97538 | -0.17254 | 20.9897
94 | -0.029412 | -0.0073738 | 0.029424 | 0.0073784 | 1.2206e-05 | 4.5662e-06 | 0.044246 | 0.044246 | 0.044246 | 0.98915 | -0.076019 | 0.98958 | -0.073025 | 16.3874
95 | -0.0024858 | -0.00062299 | 0.0024858 | 0.00062291 | 7.1512e-08 | -7.7824e-08 | 0.0037383 | 0.0037383 | 0.0037383 | 0.98944 | -0.073988 | 0.98947 | -0.073781 | 1.3846
96 | -0.0055958 | -0.0014023 | 0.0055966 | 0.0014024 | 7.9998e-07 | 7.5115e-08 | 0.0084152 | 0.0084151 | 0.0084152 | 0.98947 | -0.073781 | 0.98962 | -0.072748 | 3.1167
97 | -0.0082439 | -0.0020659 | 0.0082456 | 0.0020663 | 1.7045e-06 | 4.2711e-07 | 0.012396 | 0.012396 | 0.012396 | 0.98962 | -0.072748 | 0.98983 | -0.071254 | 4.591
98 | -0.010708 | -0.0026833 | 0.010711 | 0.0026845 | 3.8185e-06 | 1.165e-06 | 0.016097 | 0.016097 | 0.016097 | 0.98983 | -0.071254 | 0.99019 | -0.068678 | 5.9617
99 | -0.012004 | -0.0030085 | 0.012005 | 0.0030087 | 3.613e-07 | 1.1608e-07 | 0.018039 | 0.018039 | 0.018039 | 0.99019 | -0.068678 | 0.99022 | -0.068461 | 6.6813
100 | 0.072594 | 0.01822 | -0.072536 | -0.018198 | 5.892e-05 | 2.2278e-05 | 0.11076 | 0.11076 | 0.11076 | 0.97538 | -0.17254 | 0.97456 | -0.17839 | 20.5107
101 | 0.022879 | 0.0057366 | -0.022872 | -0.0057341 | 6.8666e-06 | 2.5287e-06 | 0.034934 | 0.034934 | 0.034934 | 0.97456 | -0.17839 | 0.97426 | -0.18056 | 12.9386
102 | 0.049656 | 0.012462 | -0.049614 | -0.012446 | 4.2111e-05 | 1.5612e-05 | 0.075824 | 0.075824 | 0.075824 | 0.97456 | -0.17839 | 0.97371 | -0.18451 | 14.0415
103 | 0.0035138 | 0.00088013 | -0.0035134 | -0.00088025 | 3.9009e-07 | -1.1648e-07 | 0.0053853 | 0.0053854 | 0.0053854 | 0.97085 | -0.20507 | 0.97074 | -0.20587 | 1.9946
104 | 0.0026522 | 0.00066443 | -0.002652 | -0.00066465 | 2.6956e-07 | -2.1941e-07 | 0.0040654 | 0.0040655 | 0.0040655 | 0.97074 | -0.20587 | 0.97064 | -0.20661 | 1.5058
105 | 0.013965 | 0.0035005 | -0.013959 | -0.0034986 | 5.6699e-06 | 1.915e-06 | 0.020977 | 0.020977 | 0.020977 | 0.99064 | -0.065528 | 0.99022 | -0.068461 | 7.7692
106 | 0.030865 | 0.0077411 | -0.030847 | -0.0077343 | 1.8109e-05 | 6.7943e-06 | 0.046556 | 0.046556 | 0.046556 | 0.98654 | -0.09356 | 0.98594 | -0.097795 | 17.2431
107 | -0.0036896 | -0.00092469 | 0.0036899 | 0.00092461 | 3.2405e-07 | -8.8212e-08 | 0.0055734 | 0.0055733 | 0.0055734 | 0.98506 | -0.10387 | 0.98515 | -0.10324 | 2.0642
108 | -0.0041372 | -0.0010369 | 0.0041379 | 0.0010368 | 7.0553e-07 | -9.6041e-08 | 0.0062547 | 0.0062545 | 0.0062547 | 0.98426 | -0.10974 | 0.98443 | -0.10851 | 2.3165
109 | -0.0063208 | -0.0015839 | 0.0063224 | 0.0015841 | 1.5488e-06 | 2.4989e-07 | 0.0095542 | 0.009554 | 0.0095542 | 0.98443 | -0.10851 | 0.98468 | -0.10674 | 3.5386
110 | 0.015035 | 0.0037681 | -0.015029 | -0.003766 | 5.85e-06 | 2.0191e-06 | 0.022721 | 0.022721 | 0.022721 | 0.98468 | -0.10674 | 0.98428 | -0.10955 | 8.4151
111 | -0.021358 | -0.0053522 | 0.021361 | 0.0053535 | 3.6814e-06 | 1.3439e-06 | 0.032275 | 0.032275 | 0.032275 | 0.98468 | -0.10674 | 0.98485 | -0.10549 | 11.9536
112 | 0.0020755 | 0.00052002 | -0.0020754 | -0.00052015 | 7.5581e-08 | -1.2678e-07 | 0.0031403 | 0.0031403 | 0.0031403 | 0.98346 | -0.11542 | 0.98342 | -0.11568 | 1.1631
113 | -0.0051101 | -0.0012806 | 0.0051111 | 0.0012806 | 9.7487e-07 | 4.3266e-08 | 0.0077317 | 0.0077316 | 0.0077317 | 0.98346 | -0.11542 | 0.98365 | -0.11404 | 2.8636
114 | -0.0051111 | -0.0012806 | 0.0051118 | 0.0012806 | 7.6541e-07 | 3.3871e-08 | 0.0077316 | 0.0077315 | 0.0077316 | 0.98365 | -0.11404 | 0.98381 | -0.11296 | 2.8636
115 | -0.010337 | -0.0025897 | 0.010339 | 0.0025903 | 1.9094e-06 | 5.7541e-07 | 0.015635 | 0.015635 | 0.015635 | 0.98381 | -0.11296 | 0.98399 | -0.11162 | 5.7907
116 | 0.0028818 | 0.00072172 | -0.0028812 | -0.00072211 | 5.6986e-07 | -3.9108e-07 | 0.0043586 | 0.0043588 | 0.0043588 | 0.98381 | -0.11296 | 0.9836 | -0.11439 | 1.6144
117 | -0.012319 | -0.0030866 | 0.012323 | 0.0030877 | 3.5324e-06 | 1.1514e-06 | 0.018629 | 0.018629 | 0.018629 | 0.98399 | -0.11162 | 0.98428 | -0.10955 | 6.8997
118 | 0.029251 | 0.0073344 | -0.029243 | -0.0073316 | 7.7296e-06 | 2.8919e-06 | 0.044148 | 0.044148 | 0.044148 | 0.98594 | -0.097795 | 0.98567 | -0.099702 | 16.3512
119 | 0.026504 | 0.006645 | -0.026483 | -0.0066371 | 2.1249e-05 | 7.902e-06 | 0.040013 | 0.040013 | 0.040013 | 0.98567 | -0.099702 | 0.98485 | -0.10549 | 14.8195

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24556 | 0.061866

## res_load
| p_mw | q_mvar
0 | 0.00083452 | 0.00020915
1 | 0.0018128 | 0.00045432
2 | 0.0008337 | 0.00020895
3 | 0.0013178 | 0.00033027
4 | 0.00083098 | 0.00020826
5 | 0.0013175 | 0.00033019
6 | 0.0017984 | 0.00045072
7 | 0.0033835 | 0.00084798
8 | 0.00434 | 0.0010877
9 | 0.0034293 | 0.00085945
10 | 0.0014409 | 0.00036111
11 | 0.0020289 | 0.00050849
12 | 0.0021583 | 0.00054093
13 | 0.0016632 | 0.00041683
14 | 0.00091827 | 0.00023014
15 | 0.0016996 | 0.00042597
16 | 0.0020586 | 0.00051594
17 | 0.0027627 | 0.00069241
18 | 0.0014819 | 0.0003714
19 | 0.0016934 | 0.00042439
20 | 0.0036466 | 0.00091391
21 | 0.0020847 | 0.00052248
22 | 0.0031319 | 0.00078492
23 | 0.0033746 | 0.00084575
24 | 0.0024999 | 0.00062653
25 | 0.0019502 | 0.00048878
26 | 0.0011308 | 0.00028341
27 | 0.0018656 | 0.00046756
28 | 0.0020818 | 0.00052176
29 | 0.0010598 | 0.00026562
30 | 0.00292 | 0.00073181
31 | 0.0018946 | 0.00047483
32 | 0.001334 | 0.00033434
33 | 0.0041577 | 0.001042
34 | 0.0027633 | 0.00069254
35 | 0.0017673 | 0.00044294
36 | 0.0017216 | 0.00043146
37 | 0.0016019 | 0.00040147
38 | 0.001616 | 0.000405
39 | 0.0013567 | 0.00034001
40 | 0.0012831 | 0.00032158
41 | 0.0028382 | 0.00071132
42 | 0.0018687 | 0.00046835
43 | 0.0024772 | 0.00062085
44 | 0.001351 | 0.0003386
45 | 0.0021783 | 0.00054592
46 | 0.0018426 | 0.00046181
47 | 0.0040505 | 0.0010151
48 | 0.0027608 | 0.00069191
49 | 0.002633 | 0.0006599
50 | 0.0046042 | 0.0011539
51 | 0.0042973 | 0.001077
52 | 0.0042959 | 0.0010767
53 | 0.004246 | 0.0010642
54 | 0.0050665 | 0.0012698
55 | 0.0023176 | 0.00058086
56 | 0.0030713 | 0.00076974
57 | 0.0015573 | 0.0003903
58 | 0.0012675 | 0.00031767
59 | 0.0015113 | 0.00037878
60 | 0.0031633 | 0.00079281
61 | 0.0022278 | 0.00055834
62 | 0.0022045 | 0.00055251
63 | 0.0016719 | 0.00041901
64 | 0.0016795 | 0.00042093
65 | 0.0034981 | 0.0008767
66 | 0.00506 | 0.0012682
67 | 0.0020841 | 0.00052232
68 | 0.0019559 | 0.0004902
69 | 0.0024858 | 0.00062299
70 | 0.0031099 | 0.00077942
71 | 0.0026474 | 0.00066349
72 | 0.0024619 | 0.00061702
73 | 0.0012929 | 0.00032402
74 | 0.0016954 | 0.00042492
75 | 0.0020745 | 0.00051992
76 | 0.0029309 | 0.00073454
77 | 0.0053347 | 0.001337
78 | 0.00086114 | 0.00021582
79 | 0.002652 | 0.00066465
80 | 0.0035213 | 0.00088253
81 | 0.0011126 | 0.00027883
82 | 0.0010952 | 0.00027449
83 | 0.0054523 | 0.0013665
84 | 0.0024602 | 0.00061659
85 | 0.0036896 | 0.00092469
86 | 0.0021757 | 0.00054527
87 | 0.0041372 | 0.0010369
88 | 0.0021829 | 0.0005471
89 | 0.0030346 | 0.00076054
90 | 0.0020754 | 0.00052015
91 | 0.0023437 | 0.00058739
92 | 0.0019801 | 0.00049626
93 | 0.0028812 | 0.00072211
94 | 0.0027065 | 0.00067831
95 | 0.0019548 | 0.00048991
96 | 0.0015955 | 0.00039988
97 | 0.0027394 | 0.00068656
98 | 0.0051215 | 0.0012836

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1