## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2402-11_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2402-11_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2402-11_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2402-11_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2402-11_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2402-11_0_6_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_2402-11_0_6_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2402-11_0_6_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_2402-11_0_6_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_2402-11_0_6_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_2402-11_0_6_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_2402-11_0_6_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_2402-11_0_6_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2402-11_0_6_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2402-11_0_6_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_2402-11_0_6_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2402-11_0_6_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2402-11_0_6_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2402-11_0_6_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_2402-11_0_6_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_2402-11_0_6_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_2402-11_0_6_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_2402-11_0_6_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_2402-11_0_6_node_21 | 0.4 | n |  | TRUE
24 | bus_MV_334_0_node_262 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2402-11_0_6_load_0 | 0 | 0.0069198 | 0.0017343 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2402-11_0_6_load_1 | 1 | 0.00073329 | 0.00018378 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2402-11_0_6_load_2 | 2 | 0.0010322 | 0.00025869 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2402-11_0_6_load_4 | 4 | 0.007512 | 0.0018827 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2402-11_0_6_load_5 | 6 | 0.0041066 | 0.0010292 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2402-11_0_6_load_17 | 8 | 0.018127 | 0.0045431 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2402-11_0_6_load_18 | 10 | 0.01198 | 0.0030025 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2402-11_0_6_load_19 | 11 | 0.0063979 | 0.0016035 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2402-11_0_6_load_11 | 13 | 0.00064085 | 0.00016061 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2402-11_0_6_load_24 | 14 | 0.0031776 | 0.00079638 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2402-11_0_6_load_12 | 15 | 0.0095426 | 0.0023916 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2402-11_0_6_load_15 | 17 | 0.0088845 | 0.0022267 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2402-11_0_6_load_20 | 19 | 0.032289 | 0.0080925 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2402-11_0_6_load_25 | 21 | 0.045742 | 0.011464 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2402-11_0_6_load_21 | 23 | 0.080493 | 0.020173 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2402-11_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0013517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2402-11_0_6_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0082355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2402-11_0_6_line_2 | NAYY 4x150 SE | 1 | 3 | 0.012979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2402-11_0_6_line_3 | NAYY 4x150 SE | 2 | 4 | 0.015727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2402-11_0_6_line_4 | NAYY 4x150 SE | 3 | 5 | 0.041929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2402-11_0_6_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0074073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2402-11_0_6_line_6 | NAYY 4x150 SE | 5 | 7 | 0.029431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2402-11_0_6_line_7 | NAYY 4x150 SE | 5 | 8 | 0.019188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2402-11_0_6_line_8 | NAYY 4x150 SE | 6 | 12 | 0.016991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2402-11_0_6_line_9 | NAYY 4x150 SE | 7 | 11 | 0.022179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2402-11_0_6_line_10 | NAYY 4x150 SE | 8 | 9 | 0.0056632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2402-11_0_6_line_11 | NAYY 4x150 SE | 9 | 10 | 0.0056719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_2402-11_0_6_line_12 | NAYY 4x150 SE | 10 | 14 | 0.017339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_2402-11_0_6_line_13 | NAYY 4x150 SE | 12 | 13 | 0.016615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2402-11_0_6_line_14 | NAYY 4x150 SE | 14 | 17 | 0.011557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_2402-11_0_6_line_15 | NAYY 4x150 SE | 15 | 16 | 0.030061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2402-11_0_6_line_16 | NAYY 4x150 SE | 16 | 17 | 0.02026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_2402-11_0_6_line_17 | NAYY 4x150 SE | 16 | 18 | 0.64095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_2402-11_0_6_line_18 | NAYY 4x150 SE | 18 | 19 | 0.10034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_2402-11_0_6_line_19 | NAYY 4x150 SE | 19 | 23 | 0.074799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_2402-11_0_6_line_20 | NAYY 4x150 SE | 20 | 21 | 0.051124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2402-11_0_6_line_21 | NAYY 4x150 SE | 20 | 22 | 0.29622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_2402-11_0_6_line_22 | NAYY 4x150 SE | 22 | 23 | 0.12177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2402-11_0_6_trafo_16 | 0.25 MVA 20/0.4 kV | 24 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2628754.5329 | 1239914.284 | 2628753.1953 | 1239914.0894
1 | 2628754.5329 | 1239914.284 | 2628762.6826 | 1239915.4695
2 | 2628740.4361 | 1239911.7319 | 2628749.4411 | 1239913.5433 | 2628753.1953 | 1239914.0894
3 | 2628778.2762 | 1239917.5167 | 2628762.9597 | 1239915.5099 | 2628762.6826 | 1239915.4695
4 | 2628700.1306 | 1239908.7576 | 2628701.801 | 1239910.4668 | 2628703.7986 | 1239911.7772 | 2628706.0252 | 1239912.633 | 2628708.3904 | 1239912.989 | 2628710.7807 | 1239912.8338 | 2628713.0751 | 1239912.1778 | 2628714.4849 | 1239911.4842 | 2628719.1983 | 1239910.9955 | 2628726.2736 | 1239911.5523 | 2628730.287 | 1239911.9497 | 2628740.4361 | 1239911.7319
5 | 2628778.2762 | 1239917.5167 | 2628783.1371 | 1239918.1536 | 2628785.6329 | 1239918.3657
6 | 2628676.2466 | 1239892.2654 | 2628681.9381 | 1239897.4961 | 2628688.9252 | 1239900.654 | 2628694.7479 | 1239903.7618 | 2628699.0197 | 1239907.029 | 2628700.1306 | 1239908.7576
7 | 2628700.1306 | 1239908.7576 | 2628701.276 | 1239914.2666 | 2628700.8586 | 1239920.8465 | 2628700.4484 | 1239924.369 | 2628700.4917 | 1239927.7903
8 | 2628802.5631 | 1239919.8042 | 2628785.6329 | 1239918.3657
9 | 2628676.2466 | 1239892.2654 | 2628657.2397 | 1239885.2249 | 2628655.4623 | 1239884.5243
10 | 2628700.5633 | 1239933.4531 | 2628700.4917 | 1239927.7903
11 | 2628700.5633 | 1239933.4531 | 2628698.7854 | 1239938.839
12 | 2628692.8646 | 1239955.1295 | 2628695.4469 | 1239948.5045 | 2628696.4116 | 1239946.0298 | 2628698.7854 | 1239938.839
13 | 2628802.5631 | 1239919.8042 | 2628803.8037 | 1239911.9053 | 2628805.4039 | 1239904.6974 | 2628805.9065 | 1239903.5683
14 | 2628692.8646 | 1239955.1295 | 2628688.6672 | 1239965.8979
15 | 2628680.6563 | 1239984.4892 | 2628707.8491 | 1239997.3043
16 | 2628680.6563 | 1239984.4892 | 2628684.4903 | 1239976.6138 | 2628688.6672 | 1239965.8979
17 | 2628337.055 | 1240478.1091 | 2628359.1078 | 1240489.8438 | 2628364.1486 | 1240490.3682 | 2628365.7734 | 1240490.5316 | 2628370.8249 | 1240491.99 | 2628371.7755 | 1240489.2595 | 2628377.9037 | 1240490.0559 | 2628384.8057 | 1240488.7547 | 2628391.3406 | 1240485.1502 | 2628400.5785 | 1240476.033 | 2628490.2577 | 1240315.8942 | 2628541.2313 | 1240225.615 | 2628574.3223 | 1240167.0036 | 2628661.2359 | 1240013.0692 | 2628675.334 | 1239985.8088 | 2628680.6563 | 1239984.4892
18 | 2628337.055 | 1240478.1091 | 2628329.1206 | 1240492.9584 | 2628349.6682 | 1240503.2184 | 2628355.9827 | 1240510.9312 | 2628357.6877 | 1240516.4984 | 2628356.5006 | 1240522.83 | 2628348.9249 | 1240536.9806 | 2628338.3596 | 1240556.5673
19 | 2628338.3596 | 1240556.5673 | 2628316.3057 | 1240597.4523 | 2628291.4466 | 1240583.8325
20 | 2628272.5148 | 1240643.0505 | 2628292.9836 | 1240653.8881 | 2628279.8081 | 1240678.6299
21 | 2628185.1055 | 1240524.5163 | 2628161.6358 | 1240567.6323 | 2628135.4232 | 1240616.8282 | 2628132.9552 | 1240622.2867 | 2628132.674 | 1240627.3886 | 2628135.5548 | 1240632.1497 | 2628140.9997 | 1240636.7339 | 2628161.8074 | 1240647.895 | 2628189.4403 | 1240662.7242 | 2628224.9721 | 1240681.171 | 2628231.3804 | 1240669.1383 | 2628267.8077 | 1240688.4346 | 2628274.712 | 1240688.1895 | 2628279.8081 | 1240678.6299
22 | 2628185.1055 | 1240524.5163 | 2628259.2328 | 1240566.1833 | 2628291.4466 | 1240583.8325

## bus_geodata
| x | y | coords
0 | 2628754.5329 | 1239914.284
1 | 2628753.1953 | 1239914.0894
2 | 2628762.6826 | 1239915.4695
3 | 2628740.4361 | 1239911.7319
4 | 2628778.2762 | 1239917.5167
5 | 2628700.1306 | 1239908.7576
6 | 2628785.6329 | 1239918.3657
7 | 2628676.2466 | 1239892.2654
8 | 2628700.4917 | 1239927.7903
9 | 2628700.5633 | 1239933.4531
10 | 2628698.7854 | 1239938.839
11 | 2628655.4623 | 1239884.5243
12 | 2628802.5631 | 1239919.8042
13 | 2628805.9065 | 1239903.5683
14 | 2628692.8646 | 1239955.1295
15 | 2628707.8491 | 1239997.3043
16 | 2628680.6563 | 1239984.4892
17 | 2628688.6672 | 1239965.8979
18 | 2628337.055 | 1240478.1091
19 | 2628338.3596 | 1240556.5673
20 | 2628279.8081 | 1240678.6299
21 | 2628272.5148 | 1240643.0505
22 | 2628185.1055 | 1240524.5163
23 | 2628291.4466 | 1240583.8325
24 | 2628359.1078 | 1240489.8438

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97067 | -0.20606 | 0.0069198 | 0.0017343
1 | 0.97071 | -0.20577 | 0.00073329 | 0.00018378
2 | 0.97051 | -0.20722 | 0.0010322 | 0.00025869
3 | 0.97111 | -0.2029 | 0 | 0
4 | 0.97022 | -0.20927 | 0.007512 | 0.0018827
5 | 0.9724 | -0.19361 | 0 | 0
6 | 0.97017 | -0.20964 | 0.0041066 | 0.0010292
7 | 0.97212 | -0.1956 | 0 | 0
8 | 0.97317 | -0.18807 | 0.018127 | 0.0045431
9 | 0.97354 | -0.18536 | 0 | 0
10 | 0.97373 | -0.184 | 0.01198 | 0.0030025
11 | 0.97191 | -0.1971 | 0.0063979 | 0.0016035
12 | 0.97015 | -0.20976 | 0 | 0
13 | 0.97014 | -0.20987 | 0.00064085 | 0.00016061
14 | 0.97422 | -0.18051 | 0.0031776 | 0.00079638
15 | 0.97483 | -0.17613 | 0.0095426 | 0.0023916
16 | 0.97525 | -0.17312 | 0 | 0
17 | 0.97456 | -0.17805 | 0.0088845 | 0.0022267
18 | 1 | 0 | -0.24302 | -0.06128
19 | 0.99232 | -0.053371 | 0.032289 | 0.0080925
20 | 0.97509 | -0.17497 | 0 | 0
21 | 0.97166 | -0.1996 | 0.045742 | 0.011464
22 | 0.98503 | -0.10452 | 0 | 0
23 | 0.98775 | -0.085446 | 0.080493 | 0.020173
24 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.020217 | -0.0050669 | 0.020218 | 0.0050672 | 8.102e-07 | 2.9491e-07 | 0.030993 | 0.030993 | 0.030993 | 0.97067 | -0.20606 | 0.97071 | -0.20577 | 11.4788
1 | 0.013298 | 0.0033327 | -0.013295 | -0.0033319 | 2.1355e-06 | 7.1955e-07 | 0.020385 | 0.020385 | 0.020385 | 0.97067 | -0.20606 | 0.97051 | -0.20722 | 7.55
2 | -0.020951 | -0.005251 | 0.02096 | 0.005254 | 8.354e-06 | 3.0526e-06 | 0.032117 | 0.032117 | 0.032117 | 0.97071 | -0.20577 | 0.97111 | -0.2029 | 11.8951
3 | 0.012263 | 0.0030732 | -0.01226 | -0.0030721 | 3.4695e-06 | 1.1401e-06 | 0.018802 | 0.018802 | 0.018802 | 0.97051 | -0.20722 | 0.97022 | -0.20927 | 6.9639
4 | -0.02096 | -0.005254 | 0.020987 | 0.0052639 | 2.6988e-05 | 9.8604e-06 | 0.032117 | 0.032117 | 0.032117 | 0.97111 | -0.2029 | 0.9724 | -0.19361 | 11.8951
5 | 0.0047477 | 0.0011894 | -0.0047475 | -0.0011894 | 2.4505e-07 | 2.7801e-09 | 0.0072813 | 0.0072813 | 0.0072813 | 0.97022 | -0.20927 | 0.97017 | -0.20964 | 2.6968
6 | 0.006401 | 0.001604 | -0.0063993 | -0.0016037 | 1.762e-06 | 3.1272e-07 | 0.0097951 | 0.0097953 | 0.0097953 | 0.9724 | -0.19361 | 0.97212 | -0.1956 | 3.6279
7 | -0.027388 | -0.0068679 | 0.027409 | 0.0068758 | 2.1032e-05 | 7.851e-06 | 0.041912 | 0.041912 | 0.041912 | 0.9724 | -0.19361 | 0.97317 | -0.18807 | 15.5229
8 | 0.00064087 | 0.0001602 | -0.00064086 | -0.00016041 | 1.0242e-08 | -2.0587e-07 | 0.00098279 | 0.00098287 | 0.00098287 | 0.97017 | -0.20964 | 0.97015 | -0.20976 | 0.36403
9 | 0.0063993 | 0.0016037 | -0.0063979 | -0.0016035 | 1.3279e-06 | 2.3582e-07 | 0.0097953 | 0.0097954 | 0.0097954 | 0.97212 | -0.1956 | 0.97191 | -0.1971 | 3.6279
10 | -0.045536 | -0.011419 | 0.045553 | 0.011425 | 1.7133e-05 | 6.5191e-06 | 0.069629 | 0.069629 | 0.069629 | 0.97317 | -0.18807 | 0.97354 | -0.18536 | 25.7884
11 | -0.045553 | -0.011425 | 0.045562 | 0.011429 | 8.5794e-06 | 3.1587e-06 | 0.069629 | 0.069629 | 0.069629 | 0.97354 | -0.18536 | 0.97373 | -0.184 | 12.8942
12 | -0.057541 | -0.014431 | 0.057569 | 0.014441 | 2.7888e-05 | 1.0079e-05 | 0.087936 | 0.087936 | 0.087936 | 0.97373 | -0.184 | 0.97422 | -0.18051 | 10.8563
13 | 0.00064086 | 0.00016041 | -0.00064085 | -0.00016061 | 1.0016e-08 | -2.013e-07 | 0.00098287 | 0.00098294 | 0.00098294 | 0.97015 | -0.20976 | 0.97014 | -0.20987 | 0.36405
14 | -0.060747 | -0.015237 | 0.060768 | 0.015245 | 2.0698e-05 | 7.5287e-06 | 0.092789 | 0.092789 | 0.092789 | 0.97422 | -0.18051 | 0.97456 | -0.17805 | 11.4554
15 | -0.0095426 | -0.0023916 | 0.0095466 | 0.0023928 | 3.98e-06 | 1.1558e-06 | 0.014566 | 0.014566 | 0.014566 | 0.97483 | -0.17613 | 0.97525 | -0.17312 | 5.3949
16 | 0.0697 | 0.017489 | -0.069652 | -0.017472 | 4.7667e-05 | 1.7576e-05 | 0.10635 | 0.10635 | 0.10635 | 0.97525 | -0.17312 | 0.97456 | -0.17805 | 13.1301
17 | -0.079246 | -0.019882 | 0.081196 | 0.020607 | 0.0019492 | 0.00072507 | 0.12092 | 0.12091 | 0.12092 | 0.97525 | -0.17312 | 1 | 0 | 14.9284
18 | 0.16103 | 0.040673 | -0.15983 | -0.040216 | 0.0011994 | 0.00045738 | 0.23972 | 0.23972 | 0.23972 | 1 | 0 | 0.99232 | -0.053371 | 29.5955
19 | 0.12754 | 0.032123 | -0.12697 | -0.031907 | 0.0005694 | 0.00021611 | 0.1913 | 0.19131 | 0.19131 | 0.99232 | -0.053371 | 0.98775 | -0.085446 | 23.618
20 | 0.045898 | 0.011523 | -0.045742 | -0.011464 | 0.00015654 | 5.9571e-05 | 0.070049 | 0.07005 | 0.07005 | 0.97509 | -0.17497 | 0.97166 | -0.1996 | 25.9443
21 | -0.045898 | -0.011523 | 0.046352 | 0.01169 | 0.00045348 | 0.00016695 | 0.070049 | 0.070047 | 0.070049 | 0.97509 | -0.17497 | 0.98503 | -0.10452 | 12.9721
22 | -0.046352 | -0.01169 | 0.046476 | 0.011734 | 0.00012427 | 4.3132e-05 | 0.070047 | 0.070045 | 0.070047 | 0.98503 | -0.10452 | 0.98775 | -0.085446 | 8.6477

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24302 | 0.06128

## res_load
| p_mw | q_mvar
0 | 0.0069198 | 0.0017343
1 | 0.00073329 | 0.00018378
2 | 0.0010322 | 0.00025869
3 | 0.007512 | 0.0018827
4 | 0.0041066 | 0.0010292
5 | 0.018127 | 0.0045431
6 | 0.01198 | 0.0030025
7 | 0.0063979 | 0.0016035
8 | 0.00064085 | 0.00016061
9 | 0.0031776 | 0.00079638
10 | 0.0095426 | 0.0023916
11 | 0.0088845 | 0.0022267
12 | 0.032289 | 0.0080925
13 | 0.045742 | 0.011464
14 | 0.080493 | 0.020173

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1