## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2402-9_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2402-9_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2402-9_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2402-9_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2402-9_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2402-9_0_2_node_42 | 0.4 | n |  | TRUE
6 | bus_LV_2402-9_0_2_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_2402-9_0_2_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_2402-9_0_2_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_2402-9_0_2_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2402-9_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2402-9_0_2_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2402-9_0_2_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2402-9_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2402-9_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2402-9_0_2_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_2402-9_0_2_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_2402-9_0_2_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2402-9_0_2_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2402-9_0_2_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2402-9_0_2_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_2402-9_0_2_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_2402-9_0_2_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_2402-9_0_2_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_2402-9_0_2_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_2402-9_0_2_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2402-9_0_2_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_2402-9_0_2_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2402-9_0_2_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_2402-9_0_2_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2402-9_0_2_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_2402-9_0_2_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_2402-9_0_2_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_2402-9_0_2_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_2402-9_0_2_node_46 | 0.4 | n |  | TRUE
35 | bus_LV_2402-9_0_2_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_2402-9_0_2_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_2402-9_0_2_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_2402-9_0_2_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_2402-9_0_2_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_2402-9_0_2_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_2402-9_0_2_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_2402-9_0_2_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_2402-9_0_2_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_2402-9_0_2_node_40 | 0.4 | n |  | TRUE
45 | bus_MV_334_0_node_94 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2402-9_0_2_load_0 | 0 | 0.0018032 | 0.00045193 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2402-9_0_2_load_1 | 1 | 0.0041064 | 0.0010292 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2402-9_0_2_load_2 | 2 | 0.0025908 | 0.00064932 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2402-9_0_2_load_3 | 3 | 0.0018019 | 0.00045161 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2402-9_0_2_load_4 | 4 | 0.00051556 | 0.00012921 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2402-9_0_2_load_42 | 5 | 0.001797 | 0.00045038 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2402-9_0_2_load_23 | 6 | 0.0042028 | 0.0010533 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2402-9_0_2_load_15 | 7 | 0.0045421 | 0.0011384 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2402-9_0_2_load_22 | 8 | 0.00073647 | 0.00018458 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2402-9_0_2_load_5 | 9 | 0.00034083 | 8.542e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2402-9_0_2_load_6 | 10 | 0.0002685 | 6.7292e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2402-9_0_2_load_7 | 11 | 0.00041986 | 0.00010523 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2402-9_0_2_load_8 | 12 | 0.00053259 | 0.00013348 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2402-9_0_2_load_9 | 13 | 0.0034445 | 0.00086328 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2402-9_0_2_load_10 | 14 | 0.00028751 | 7.2056e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2402-9_0_2_load_27 | 15 | 0.0005287 | 0.0001325 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2402-9_0_2_load_28 | 16 | 0.00032135 | 8.0537e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2402-9_0_2_load_11 | 17 | 0.0042899 | 0.0010751 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2402-9_0_2_load_14 | 19 | 0.0022026 | 0.00055201 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2402-9_0_2_load_34 | 20 | 0.00347 | 0.00086968 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2402-9_0_2_load_35 | 21 | 0.0079399 | 0.0019899 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2402-9_0_2_load_44 | 22 | 0.0017831 | 0.00044688 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2402-9_0_2_load_17 | 24 | 0.0020162 | 0.00050531 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2402-9_0_2_load_18 | 25 | 0.00179 | 0.00044861 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2402-9_0_2_load_20 | 27 | 0.0020358 | 0.00051022 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2402-9_0_2_load_21 | 28 | 0.00062864 | 0.00015755 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2402-9_0_2_load_25 | 29 | 0.0096276 | 0.0024129 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2402-9_0_2_load_38 | 32 | 0.0013669 | 0.00034257 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2402-9_0_2_load_32 | 33 | 0.0010607 | 0.00026584 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2402-9_0_2_load_46 | 34 | 0.020234 | 0.005071 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2402-9_0_2_load_30 | 35 | 0.00080863 | 0.00020266 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2402-9_0_2_load_29 | 36 | 0.0022548 | 0.0005651 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2402-9_0_2_load_33 | 37 | 0.0024716 | 0.00061945 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2402-9_0_2_load_31 | 38 | 0.00077876 | 0.00019517 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2402-9_0_2_load_41 | 41 | 0.0077867 | 0.0019515 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2402-9_0_2_load_47 | 42 | 0.0010445 | 0.00026177 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2402-9_0_2_load_39 | 43 | 0.011663 | 0.0029229 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2402-9_0_2_load_40 | 44 | 0.0030725 | 0.00077005 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2402-9_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0078135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2402-9_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0078575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2402-9_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0058866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2402-9_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0059024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2402-9_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.013657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2402-9_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.014508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2402-9_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.018285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2402-9_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0068462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2402-9_0_2_line_8 | NAYY 4x150 SE | 7 | 18 | 0.039873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2402-9_0_2_line_9 | NAYY 4x150 SE | 8 | 30 | 0.017795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2402-9_0_2_line_10 | NAYY 4x150 SE | 9 | 10 | 0.0083491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2402-9_0_2_line_11 | NAYY 4x150 SE | 9 | 11 | 0.021629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2402-9_0_2_line_12 | NAYY 4x150 SE | 10 | 12 | 0.02001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2402-9_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.010218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2402-9_0_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.0072455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2402-9_0_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0095061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2402-9_0_2_line_16 | NAYY 4x150 SE | 15 | 16 | 0.029917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2402-9_0_2_line_17 | NAYY 4x150 SE | 16 | 36 | 0.029688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2402-9_0_2_line_18 | NAYY 4x150 SE | 17 | 18 | 0.018915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2402-9_0_2_line_19 | NAYY 4x150 SE | 18 | 19 | 0.043264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2402-9_0_2_line_20 | NAYY 4x150 SE | 19 | 20 | 0.036712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2402-9_0_2_line_21 | NAYY 4x150 SE | 20 | 21 | 0.054678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2402-9_0_2_line_22 | NAYY 4x150 SE | 22 | 23 | 0.0068754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2402-9_0_2_line_23 | NAYY 4x150 SE | 23 | 27 | 0.03072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2402-9_0_2_line_24 | NAYY 4x150 SE | 24 | 25 | 0.029756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2402-9_0_2_line_25 | NAYY 4x150 SE | 24 | 26 | 0.023748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2402-9_0_2_line_26 | NAYY 4x150 SE | 25 | 27 | 0.01163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2402-9_0_2_line_27 | NAYY 4x150 SE | 26 | 28 | 0.030574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2402-9_0_2_line_28 | NAYY 4x150 SE | 28 | 29 | 0.046227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2402-9_0_2_line_29 | NAYY 4x150 SE | 29 | 30 | 0.0027309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2402-9_0_2_line_30 | NAYY 4x150 SE | 30 | 31 | 0.03298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2402-9_0_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.0026678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2402-9_0_2_line_32 | NAYY 4x150 SE | 31 | 33 | 0.01742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2402-9_0_2_line_33 | NAYY 4x150 SE | 32 | 34 | 0.043017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2402-9_0_2_line_34 | NAYY 4x150 SE | 33 | 35 | 0.012344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2402-9_0_2_line_35 | NAYY 4x150 SE | 34 | 40 | 0.03127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2402-9_0_2_line_36 | NAYY 4x150 SE | 35 | 38 | 0.016179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2402-9_0_2_line_37 | NAYY 4x150 SE | 36 | 37 | 0.0045643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2402-9_0_2_line_38 | NAYY 4x150 SE | 37 | 38 | 0.017083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2402-9_0_2_line_39 | NAYY 4x150 SE | 39 | 40 | 0.013789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2402-9_0_2_line_40 | NAYY 4x150 SE | 39 | 41 | 0.063982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2402-9_0_2_line_41 | NAYY 4x150 SE | 40 | 42 | 0.026317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2402-9_0_2_line_42 | NAYY 4x150 SE | 41 | 43 | 0.026846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2402-9_0_2_line_43 | NAYY 4x150 SE | 43 | 44 | 0.021881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2402-9_0_2_trafo_38 | 0.25 MVA 20/0.4 kV | 45 | 32 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2628251.1089 | 1239886.4248 | 2628254.5987 | 1239879.434
1 | 2628251.1089 | 1239886.4248 | 2628247.5995 | 1239893.4549
2 | 2628257.228 | 1239874.1671 | 2628254.5987 | 1239879.434
3 | 2628244.9632 | 1239898.7359 | 2628247.5995 | 1239893.4549
4 | 2628257.228 | 1239874.1671 | 2628263.101 | 1239862.4022 | 2628263.3247 | 1239861.9466
5 | 2628244.9632 | 1239898.7359 | 2628238.4835 | 1239911.7161
6 | 2628271.3835 | 1239845.5334 | 2628263.3247 | 1239861.9466
7 | 2628238.4835 | 1239911.7161 | 2628235.4257 | 1239917.8415
8 | 2628283.0989 | 1239809.097 | 2628284.604 | 1239812.2061 | 2628285.0043 | 1239815.499 | 2628284.5977 | 1239818.2988 | 2628282.397 | 1239823.1025 | 2628271.3835 | 1239845.5334
9 | 2628227.9988 | 1239934.0028 | 2628231.6008 | 1239925.5035 | 2628235.4257 | 1239917.8415
10 | 2628124.0852 | 1240074.4618 | 2628120.547 | 1240082.0242
11 | 2628124.0852 | 1240074.4618 | 2628133.2511 | 1240054.8711
12 | 2628112.067 | 1240100.149 | 2628120.547 | 1240082.0242
13 | 2628133.2511 | 1240054.8711 | 2628137.5812 | 1240045.6161
14 | 2628112.067 | 1240100.149 | 2628108.9965 | 1240106.7117
15 | 2628137.5812 | 1240045.6161 | 2628138.1024 | 1240044.502 | 2628141.7004 | 1240037.049
16 | 2628154.7066 | 1240010.1069 | 2628141.7004 | 1240037.049
17 | 2628154.7066 | 1240010.1069 | 2628167.6131 | 1239983.3717
18 | 2628283.0989 | 1239809.097 | 2628301.1289 | 1239803.3783
19 | 2628283.0989 | 1239809.097 | 2628271.8985 | 1239812.5015 | 2628264.1011 | 1239814.2989 | 2628253.8006 | 1239816.1066 | 2628243.7025 | 1239816.7035 | 2628240.7216 | 1239816.8007
20 | 2628204.1635 | 1239819.5559 | 2628210.7011 | 1239818.5036 | 2628219.3038 | 1239817.4993 | 2628240.7216 | 1239816.8007
21 | 2628204.1635 | 1239819.5559 | 2628198.7591 | 1239820.4259 | 2628183.8995 | 1239828.4828 | 2628166.7988 | 1239841.8991 | 2628159.0032 | 1239849.0306
22 | 2628343.8037 | 1239874.7051 | 2628346.6256 | 1239868.4355
23 | 2628343.8037 | 1239874.7051 | 2628331.8998 | 1239900.3979 | 2628330.8608 | 1239902.5657
24 | 2628325.8342 | 1239913.0531 | 2628319.1981 | 1239926.8986 | 2628312.9702 | 1239939.8845
25 | 2628302.7008 | 1239961.2973 | 2628312.9702 | 1239939.8845
26 | 2628330.8608 | 1239902.5657 | 2628325.8342 | 1239913.0531
27 | 2628302.7008 | 1239961.2973 | 2628273.9834 | 1239950.8046
28 | 2628230.5639 | 1239934.94 | 2628273.9834 | 1239950.8046
29 | 2628227.9988 | 1239934.0028 | 2628230.5639 | 1239934.94
30 | 2628196.9969 | 1239922.5041 | 2628202.0997 | 1239924.3961 | 2628227.9988 | 1239934.0028
31 | 2628196.9969 | 1239922.5041 | 2628194.4938 | 1239921.5813
32 | 2628196.9969 | 1239922.5041 | 2628189.4239 | 1239938.1914
33 | 2628154.0737 | 1239906.8615 | 2628169.8066 | 1239912.48 | 2628194.4938 | 1239921.5813
34 | 2628189.4239 | 1239938.1914 | 2628184.0575 | 1239949.3075
35 | 2628124.6253 | 1239896.3449 | 2628154.0737 | 1239906.8615
36 | 2628177.0239 | 1239963.8775 | 2628184.0575 | 1239949.3075
37 | 2628169.5974 | 1239979.2613 | 2628167.6131 | 1239983.3717
38 | 2628177.0239 | 1239963.8775 | 2628169.5974 | 1239979.2613
39 | 2628111.603 | 1239891.7027 | 2628124.6253 | 1239896.3449
40 | 2628111.603 | 1239891.7027 | 2628082.3012 | 1239915.6015 | 2628060.9996 | 1239930.8042
41 | 2628124.6253 | 1239896.3449 | 2628112.1519 | 1239919.5339
42 | 2628037.6863 | 1239944.0086 | 2628041.8039 | 1239942.0049 | 2628051.7032 | 1239937.0039 | 2628058.9016 | 1239932.3016 | 2628060.9996 | 1239930.8042
43 | 2628037.6863 | 1239944.0086 | 2628033.9973 | 1239945.8038 | 2628025.703 | 1239948.7999 | 2628017.1009 | 1239951.3054

## bus_geodata
| x | y | coords
0 | 2628251.1089 | 1239886.4248
1 | 2628254.5987 | 1239879.434
2 | 2628247.5995 | 1239893.4549
3 | 2628257.228 | 1239874.1671
4 | 2628244.9632 | 1239898.7359
5 | 2628263.3247 | 1239861.9466
6 | 2628238.4835 | 1239911.7161
7 | 2628271.3835 | 1239845.5334
8 | 2628235.4257 | 1239917.8415
9 | 2628124.0852 | 1240074.4618
10 | 2628120.547 | 1240082.0242
11 | 2628133.2511 | 1240054.8711
12 | 2628112.067 | 1240100.149
13 | 2628137.5812 | 1240045.6161
14 | 2628108.9965 | 1240106.7117
15 | 2628141.7004 | 1240037.049
16 | 2628154.7066 | 1240010.1069
17 | 2628301.1289 | 1239803.3783
18 | 2628283.0989 | 1239809.097
19 | 2628240.7216 | 1239816.8007
20 | 2628204.1635 | 1239819.5559
21 | 2628159.0032 | 1239849.0306
22 | 2628346.6256 | 1239868.4355
23 | 2628343.8037 | 1239874.7051
24 | 2628312.9702 | 1239939.8845
25 | 2628325.8342 | 1239913.0531
26 | 2628302.7008 | 1239961.2973
27 | 2628330.8608 | 1239902.5657
28 | 2628273.9834 | 1239950.8046
29 | 2628230.5639 | 1239934.94
30 | 2628227.9988 | 1239934.0028
31 | 2628196.9969 | 1239922.5041
32 | 2628194.4938 | 1239921.5813
33 | 2628189.4239 | 1239938.1914
34 | 2628154.0737 | 1239906.8615
35 | 2628184.0575 | 1239949.3075
36 | 2628167.6131 | 1239983.3717
37 | 2628169.5974 | 1239979.2613
38 | 2628177.0239 | 1239963.8775
39 | 2628111.603 | 1239891.7027
40 | 2628124.6253 | 1239896.3449
41 | 2628060.9996 | 1239930.8042
42 | 2628112.1519 | 1239919.5339
43 | 2628037.6863 | 1239944.0086
44 | 2628017.1009 | 1239951.3054
45 | 2628196.9969 | 1239922.5041

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9942 | -0.040622 | 0.0018032 | 0.00045193
1 | 0.99386 | -0.043003 | 0.0041064 | 0.0010292
2 | 0.99456 | -0.038086 | 0.0025908 | 0.00064932
3 | 0.99364 | -0.044554 | 0.0018019 | 0.00045161
4 | 0.99485 | -0.036028 | 0.00051556 | 0.00012921
5 | 0.99316 | -0.047905 | 0.001797 | 0.00045038
6 | 0.99558 | -0.030899 | 0.0042028 | 0.0010533
7 | 0.99257 | -0.052064 | 0.0045421 | 0.0011384
8 | 0.99597 | -0.028192 | 0.00073647 | 0.00018458
9 | 0.99793 | -0.014513 | 0.00034083 | 8.542e-05
10 | 0.99792 | -0.014604 | 0.0002685 | 6.7292e-05
11 | 0.99797 | -0.014202 | 0.00041986 | 0.00010523
12 | 0.99789 | -0.014769 | 0.00053259 | 0.00013348
13 | 0.998 | -0.014012 | 0.0034445 | 0.00086328
14 | 0.99789 | -0.01479 | 0.00028751 | 7.2056e-05
15 | 0.99807 | -0.013507 | 0.0005287 | 0.0001325
16 | 0.99832 | -0.011759 | 0.00032135 | 8.0537e-05
17 | 0.99143 | -0.060133 | 0.0042899 | 0.0010751
18 | 0.99154 | -0.059309 | 0 | 0
19 | 0.99069 | -0.065298 | 0.0022026 | 0.00055201
20 | 0.99009 | -0.069563 | 0.00347 | 0.00086968
21 | 0.98947 | -0.073987 | 0.0079399 | 0.0019899
22 | 0.99538 | -0.032342 | 0.0017831 | 0.00044688
23 | 0.9954 | -0.032219 | 0 | 0
24 | 0.99578 | -0.029537 | 0.0020162 | 0.00050531
25 | 0.99554 | -0.031219 | 0.00179 | 0.00044861
26 | 0.99604 | -0.027712 | 0 | 0
27 | 0.99548 | -0.031667 | 0.0020358 | 0.00051022
28 | 0.99637 | -0.025365 | 0.00062864 | 0.00015755
29 | 0.99692 | -0.021524 | 0.0096276 | 0.0024129
30 | 0.99699 | -0.021033 | 0 | 0
31 | 0.99973 | -0.0019034 | 0 | 0
32 | 1 | 0 | -0.11659 | -0.029085
33 | 0.99939 | -0.004259 | 0.0010607 | 0.00026584
34 | 0.9973 | -0.018864 | 0.020234 | 0.005071
35 | 0.99917 | -0.005798 | 0.00080863 | 0.00020266
36 | 0.99858 | -0.0099299 | 0.0022548 | 0.0005651
37 | 0.99864 | -0.0095456 | 0.0024716 | 0.00061945
38 | 0.9989 | -0.0076853 | 0.00077876 | 0.00019517
39 | 0.9958 | -0.029397 | 0 | 0
40 | 0.99624 | -0.026272 | 0 | 0
41 | 0.99373 | -0.043936 | 0.0077867 | 0.0019515
42 | 0.9962 | -0.026548 | 0.0010445 | 0.00026177
43 | 0.99316 | -0.047937 | 0.011663 | 0.0029229
44 | 0.99307 | -0.048618 | 0.0030725 | 0.00077005
45 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.030231 | 0.0075844 | -0.030221 | -0.0075807 | 9.983e-06 | 3.7383e-06 | 0.04525 | 0.04525 | 0.04525 | 0.9942 | -0.040622 | 0.99386 | -0.043003 | 16.7592
1 | -0.032034 | -0.0080364 | 0.032046 | 0.0080406 | 1.1272e-05 | 4.2336e-06 | 0.047949 | 0.047949 | 0.047949 | 0.9942 | -0.040622 | 0.99456 | -0.038086 | 17.7588
2 | 0.026115 | 0.0065515 | -0.026109 | -0.0065494 | 5.6162e-06 | 2.0838e-06 | 0.039102 | 0.039102 | 0.039102 | 0.99386 | -0.043003 | 0.99364 | -0.044554 | 14.4821
3 | -0.034636 | -0.0086899 | 0.034646 | 0.0086936 | 9.8922e-06 | 3.7281e-06 | 0.051825 | 0.051825 | 0.051825 | 0.99456 | -0.038086 | 0.99485 | -0.036028 | 19.1944
4 | 0.024307 | 0.0060978 | -0.024296 | -0.0060937 | 1.1293e-05 | 4.1667e-06 | 0.036403 | 0.036403 | 0.036403 | 0.99364 | -0.044554 | 0.99316 | -0.047905 | 13.4827
5 | -0.035162 | -0.0088229 | 0.035187 | 0.0088323 | 2.5043e-05 | 9.4434e-06 | 0.052596 | 0.052596 | 0.052596 | 0.99485 | -0.036028 | 0.99558 | -0.030899 | 19.48
6 | 0.022499 | 0.0056433 | -0.022486 | -0.0056385 | 1.2966e-05 | 4.7506e-06 | 0.033711 | 0.033711 | 0.033711 | 0.99316 | -0.047905 | 0.99257 | -0.052064 | 12.4855
7 | -0.03939 | -0.0098856 | 0.039405 | 0.0098912 | 1.4809e-05 | 5.6068e-06 | 0.058878 | 0.058878 | 0.058878 | 0.99558 | -0.030899 | 0.99597 | -0.028192 | 21.8065
8 | 0.017944 | 0.0045002 | -0.017926 | -0.0044938 | 1.8006e-05 | 6.4107e-06 | 0.026902 | 0.026902 | 0.026902 | 0.99257 | -0.052064 | 0.99154 | -0.059309 | 9.9636
9 | -0.040141 | -0.010076 | 0.040181 | 0.010091 | 3.9945e-05 | 1.5131e-05 | 0.059978 | 0.059978 | 0.059978 | 0.99597 | -0.028192 | 0.99699 | -0.021033 | 22.214
10 | 0.0010886 | 0.00027238 | -0.0010886 | -0.00027248 | 1.3725e-08 | -1.038e-07 | 0.0016231 | 0.0016231 | 0.0016231 | 0.99793 | -0.014513 | 0.99792 | -0.014604 | 0.60116
11 | -0.0014295 | -0.0003578 | 0.0014295 | 0.00035754 | 6.1305e-08 | -2.5902e-07 | 0.0021313 | 0.0021312 | 0.0021313 | 0.99793 | -0.014513 | 0.99797 | -0.014202 | 0.78937
12 | 0.00082012 | 0.00020519 | -0.0008201 | -0.00020544 | 1.8671e-08 | -2.5424e-07 | 0.0012228 | 0.0012229 | 0.0012229 | 0.99792 | -0.014604 | 0.99789 | -0.014769 | 0.45291
13 | -0.0018494 | -0.00046276 | 0.0018494 | 0.00046265 | 4.8471e-08 | -1.1487e-07 | 0.0027572 | 0.0027572 | 0.0027572 | 0.99797 | -0.014202 | 0.998 | -0.014012 | 1.0212
14 | 0.00028751 | 7.1962e-05 | -0.00028751 | -7.2056e-05 | 8.3096e-10 | -9.4336e-08 | 0.00042869 | 0.00042872 | 0.00042872 | 0.99789 | -0.014769 | 0.99789 | -0.01479 | 0.15879
15 | -0.005294 | -0.0013259 | 0.0052943 | 0.001326 | 3.6954e-07 | 1.7908e-08 | 0.007893 | 0.0078929 | 0.007893 | 0.998 | -0.014012 | 0.99807 | -0.013507 | 2.9233
16 | -0.005823 | -0.0014585 | 0.0058244 | 0.0014586 | 1.4069e-06 | 1.5003e-07 | 0.0086812 | 0.008681 | 0.0086812 | 0.99807 | -0.013507 | 0.99832 | -0.011759 | 3.2152
17 | -0.0061458 | -0.0015391 | 0.0061473 | 0.0015394 | 1.5543e-06 | 2.0955e-07 | 0.00916 | 0.0091599 | 0.00916 | 0.99832 | -0.011759 | 0.99858 | -0.0099299 | 3.3926
18 | -0.0042898 | -0.0010751 | 0.0042903 | 0.0010751 | 4.8929e-07 | -5.5756e-08 | 0.0064386 | 0.0064385 | 0.0064386 | 0.99143 | -0.060133 | 0.99154 | -0.059309 | 2.3847
19 | 0.013635 | 0.0034187 | -0.013624 | -0.0034149 | 1.1305e-05 | 3.7905e-06 | 0.020463 | 0.020464 | 0.020464 | 0.99154 | -0.059309 | 0.99069 | -0.065298 | 7.5791
20 | 0.011422 | 0.0028629 | -0.011415 | -0.0028608 | 6.7421e-06 | 2.1207e-06 | 0.017155 | 0.017155 | 0.017155 | 0.99069 | -0.065298 | 0.99009 | -0.069563 | 6.3539
21 | 0.0079448 | 0.0019911 | -0.0079399 | -0.0019899 | 4.8645e-06 | 1.1682e-06 | 0.01194 | 0.011941 | 0.011941 | 0.99009 | -0.069563 | 0.98947 | -0.073987 | 4.4224
22 | -0.0017831 | -0.00044687 | 0.0017831 | 0.0004468 | 3.0482e-08 | -7.7647e-08 | 0.0026655 | 0.0026655 | 0.0026655 | 0.99538 | -0.032342 | 0.9954 | -0.032219 | 0.98723
23 | -0.0017831 | -0.0004468 | 0.0017832 | 0.00044645 | 1.3619e-07 | -3.4698e-07 | 0.0026655 | 0.0026654 | 0.0026655 | 0.9954 | -0.032219 | 0.99548 | -0.031667 | 0.98722
24 | 0.0056105 | 0.0014053 | -0.0056092 | -0.0014052 | 1.3051e-06 | 1.1495e-07 | 0.0083837 | 0.0083838 | 0.0083838 | 0.99578 | -0.029537 | 0.99554 | -0.031219 | 3.1051
25 | -0.0076267 | -0.0019106 | 0.0076287 | 0.0019111 | 1.9247e-06 | 4.3124e-07 | 0.011397 | 0.011396 | 0.011397 | 0.99578 | -0.029537 | 0.99604 | -0.027712 | 4.2209
26 | 0.0038193 | 0.00095661 | -0.003819 | -0.00095667 | 2.3648e-07 | -6.0255e-08 | 0.0057084 | 0.0057084 | 0.0057084 | 0.99554 | -0.031219 | 0.99548 | -0.031667 | 2.1142
27 | -0.0076287 | -0.0019111 | 0.0076311 | 0.0019116 | 2.4778e-06 | 5.5494e-07 | 0.011396 | 0.011396 | 0.011396 | 0.99604 | -0.027712 | 0.99637 | -0.025365 | 4.2209
28 | -0.0082598 | -0.0020692 | 0.0082642 | 0.0020703 | 4.3889e-06 | 1.0856e-06 | 0.012335 | 0.012335 | 0.012335 | 0.99637 | -0.025365 | 0.99692 | -0.021524 | 4.5686
29 | -0.017892 | -0.0044832 | 0.017893 | 0.0044836 | 1.2153e-06 | 4.3181e-07 | 0.026705 | 0.026705 | 0.026705 | 0.99692 | -0.021524 | 0.99699 | -0.021033 | 9.8908
30 | -0.058074 | -0.014575 | 0.058229 | 0.014634 | 0.00015463 | 5.9043e-05 | 0.086683 | 0.086683 | 0.086683 | 0.99699 | -0.021033 | 0.99973 | -0.0019034 | 32.1048
31 | -0.071764 | -0.018025 | 0.071783 | 0.018033 | 1.8998e-05 | 7.272e-06 | 0.10683 | 0.10683 | 0.10683 | 0.99973 | -0.0019034 | 1 | 0 | 39.5662
32 | 0.013535 | 0.0033918 | -0.013531 | -0.0033904 | 4.4116e-06 | 1.4684e-06 | 0.020146 | 0.020146 | 0.020146 | 0.99973 | -0.0019034 | 0.99939 | -0.004259 | 7.4615
33 | 0.044003 | 0.011052 | -0.043888 | -0.011009 | 0.00011511 | 4.3711e-05 | 0.065486 | 0.065486 | 0.065486 | 1 | 0 | 0.9973 | -0.018864 | 24.2541
34 | 0.01247 | 0.0031245 | -0.012467 | -0.0031237 | 2.6552e-06 | 8.5953e-07 | 0.018567 | 0.018567 | 0.018567 | 0.99939 | -0.004259 | 0.99917 | -0.005798 | 6.8766
35 | 0.023654 | 0.0059378 | -0.02363 | -0.0059288 | 2.431e-05 | 8.9423e-06 | 0.035297 | 0.035297 | 0.035297 | 0.9973 | -0.018864 | 0.99624 | -0.026272 | 13.0729
36 | 0.011659 | 0.002921 | -0.011656 | -0.00292 | 3.0434e-06 | 9.5869e-07 | 0.017362 | 0.017363 | 0.017363 | 0.99917 | -0.005798 | 0.9989 | -0.0076853 | 6.4306
37 | -0.0084021 | -0.0021044 | 0.0084026 | 0.0021046 | 4.4643e-07 | 1.1199e-07 | 0.01252 | 0.01252 | 0.01252 | 0.99858 | -0.0099299 | 0.99864 | -0.0095456 | 4.6369
38 | -0.010874 | -0.002724 | 0.010877 | 0.0027249 | 2.7984e-06 | 8.5273e-07 | 0.016203 | 0.016202 | 0.016203 | 0.99864 | -0.0095456 | 0.9989 | -0.0076853 | 6.001
39 | -0.022576 | -0.0056638 | 0.022586 | 0.0056674 | 9.7933e-06 | 3.5872e-06 | 0.033737 | 0.033737 | 0.033737 | 0.9958 | -0.029397 | 0.99624 | -0.026272 | 12.4952
40 | 0.022576 | 0.0056638 | -0.02253 | -0.0056471 | 4.5442e-05 | 1.6647e-05 | 0.033737 | 0.033737 | 0.033737 | 0.9958 | -0.029397 | 0.99373 | -0.043936 | 12.4953
41 | 0.0010445 | 0.00026144 | -0.0010445 | -0.00026177 | 3.9967e-08 | -3.2729e-07 | 0.00156 | 0.0015601 | 0.0015601 | 0.99624 | -0.026272 | 0.9962 | -0.026548 | 0.57782
42 | 0.014744 | 0.0036956 | -0.014735 | -0.0036928 | 8.165e-06 | 2.7928e-06 | 0.022077 | 0.022077 | 0.022077 | 0.99373 | -0.043936 | 0.99316 | -0.047937 | 8.1768
43 | 0.0030728 | 0.00076987 | -0.0030725 | -0.00077005 | 2.8939e-07 | -1.7182e-07 | 0.0046038 | 0.0046039 | 0.0046039 | 0.99316 | -0.047937 | 0.99307 | -0.048618 | 1.7051

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11795 | 0.029428

## res_load
| p_mw | q_mvar
0 | 0.0018032 | 0.00045193
1 | 0.0041064 | 0.0010292
2 | 0.0025908 | 0.00064932
3 | 0.0018019 | 0.00045161
4 | 0.00051556 | 0.00012921
5 | 0.001797 | 0.00045038
6 | 0.0042028 | 0.0010533
7 | 0.0045421 | 0.0011384
8 | 0.00073647 | 0.00018458
9 | 0.00034083 | 8.542e-05
10 | 0.0002685 | 6.7292e-05
11 | 0.00041986 | 0.00010523
12 | 0.00053259 | 0.00013348
13 | 0.0034445 | 0.00086328
14 | 0.00028751 | 7.2056e-05
15 | 0.0005287 | 0.0001325
16 | 0.00032135 | 8.0537e-05
17 | 0.0042899 | 0.0010751
18 | 0.0022026 | 0.00055201
19 | 0.00347 | 0.00086968
20 | 0.0079399 | 0.0019899
21 | 0.0017831 | 0.00044688
22 | 0.0020162 | 0.00050531
23 | 0.00179 | 0.00044861
24 | 0.0020358 | 0.00051022
25 | 0.00062864 | 0.00015755
26 | 0.0096276 | 0.0024129
27 | 0.0013669 | 0.00034257
28 | 0.0010607 | 0.00026584
29 | 0.020234 | 0.005071
30 | 0.00080863 | 0.00020266
31 | 0.0022548 | 0.0005651
32 | 0.0024716 | 0.00061945
33 | 0.00077876 | 0.00019517
34 | 0.0077867 | 0.0019515
35 | 0.0010445 | 0.00026177
36 | 0.011663 | 0.0029229
37 | 0.0030725 | 0.00077005

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1