## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2405-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2405-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2405-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2405-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2405-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2405-1_0_4_node_39 | 0.4 | n |  | TRUE
6 | bus_LV_2405-1_0_4_node_53 | 0.4 | n |  | TRUE
7 | bus_LV_2405-1_0_4_node_40 | 0.4 | n |  | TRUE
8 | bus_LV_2405-1_0_4_node_54 | 0.4 | n |  | TRUE
9 | bus_LV_2405-1_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2405-1_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2405-1_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2405-1_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2405-1_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2405-1_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_2405-1_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2405-1_0_4_node_95 | 0.4 | n |  | TRUE
17 | bus_LV_2405-1_0_4_node_98 | 0.4 | n |  | TRUE
18 | bus_LV_2405-1_0_4_node_97 | 0.4 | n |  | TRUE
19 | bus_LV_2405-1_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2405-1_0_4_node_64 | 0.4 | n |  | TRUE
21 | bus_LV_2405-1_0_4_node_91 | 0.4 | n |  | TRUE
22 | bus_LV_2405-1_0_4_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_2405-1_0_4_node_94 | 0.4 | n |  | TRUE
24 | bus_LV_2405-1_0_4_node_66 | 0.4 | n |  | TRUE
25 | bus_LV_2405-1_0_4_node_60 | 0.4 | n |  | TRUE
26 | bus_LV_2405-1_0_4_node_62 | 0.4 | n |  | TRUE
27 | bus_LV_2405-1_0_4_node_90 | 0.4 | n |  | TRUE
28 | bus_LV_2405-1_0_4_node_137 | 0.4 | n |  | TRUE
29 | bus_LV_2405-1_0_4_node_59 | 0.4 | n |  | TRUE
30 | bus_LV_2405-1_0_4_node_13 | 0.4 | n |  | TRUE
31 | bus_LV_2405-1_0_4_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_2405-1_0_4_node_15 | 0.4 | n |  | TRUE
33 | bus_LV_2405-1_0_4_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_2405-1_0_4_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_2405-1_0_4_node_141 | 0.4 | n |  | TRUE
36 | bus_LV_2405-1_0_4_node_135 | 0.4 | n |  | TRUE
37 | bus_LV_2405-1_0_4_node_77 | 0.4 | n |  | TRUE
38 | bus_LV_2405-1_0_4_node_134 | 0.4 | n |  | TRUE
39 | bus_LV_2405-1_0_4_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_2405-1_0_4_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_2405-1_0_4_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_2405-1_0_4_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_2405-1_0_4_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_2405-1_0_4_node_73 | 0.4 | n |  | TRUE
45 | bus_LV_2405-1_0_4_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_2405-1_0_4_node_78 | 0.4 | n |  | TRUE
47 | bus_LV_2405-1_0_4_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_2405-1_0_4_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_2405-1_0_4_node_79 | 0.4 | n |  | TRUE
50 | bus_LV_2405-1_0_4_node_23 | 0.4 | n |  | TRUE
51 | bus_LV_2405-1_0_4_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_2405-1_0_4_node_26 | 0.4 | n |  | TRUE
53 | bus_LV_2405-1_0_4_node_27 | 0.4 | n |  | TRUE
54 | bus_LV_2405-1_0_4_node_115 | 0.4 | n |  | TRUE
55 | bus_LV_2405-1_0_4_node_116 | 0.4 | n |  | TRUE
56 | bus_LV_2405-1_0_4_node_29 | 0.4 | n |  | TRUE
57 | bus_LV_2405-1_0_4_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_2405-1_0_4_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_2405-1_0_4_node_93 | 0.4 | n |  | TRUE
60 | bus_LV_2405-1_0_4_node_110 | 0.4 | n |  | TRUE
61 | bus_LV_2405-1_0_4_node_33 | 0.4 | n |  | TRUE
62 | bus_LV_2405-1_0_4_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_2405-1_0_4_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_2405-1_0_4_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_2405-1_0_4_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_2405-1_0_4_node_125 | 0.4 | n |  | TRUE
67 | bus_LV_2405-1_0_4_node_128 | 0.4 | n |  | TRUE
68 | bus_LV_2405-1_0_4_node_124 | 0.4 | n |  | TRUE
69 | bus_LV_2405-1_0_4_node_129 | 0.4 | n |  | TRUE
70 | bus_LV_2405-1_0_4_node_127 | 0.4 | n |  | TRUE
71 | bus_LV_2405-1_0_4_node_109 | 0.4 | n |  | TRUE
72 | bus_LV_2405-1_0_4_node_41 | 0.4 | n |  | TRUE
73 | bus_LV_2405-1_0_4_node_140 | 0.4 | n |  | TRUE
74 | bus_LV_2405-1_0_4_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_2405-1_0_4_node_104 | 0.4 | n |  | TRUE
76 | bus_LV_2405-1_0_4_node_80 | 0.4 | n |  | TRUE
77 | bus_LV_2405-1_0_4_node_50 | 0.4 | n |  | TRUE
78 | bus_LV_2405-1_0_4_node_42 | 0.4 | n |  | TRUE
79 | bus_LV_2405-1_0_4_node_43 | 0.4 | n |  | TRUE
80 | bus_LV_2405-1_0_4_node_44 | 0.4 | n |  | TRUE
81 | bus_LV_2405-1_0_4_node_45 | 0.4 | n |  | TRUE
82 | bus_LV_2405-1_0_4_node_46 | 0.4 | n |  | TRUE
83 | bus_LV_2405-1_0_4_node_47 | 0.4 | n |  | TRUE
84 | bus_LV_2405-1_0_4_node_81 | 0.4 | n |  | TRUE
85 | bus_LV_2405-1_0_4_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_2405-1_0_4_node_96 | 0.4 | n |  | TRUE
87 | bus_LV_2405-1_0_4_node_82 | 0.4 | n |  | TRUE
88 | bus_LV_2405-1_0_4_node_88 | 0.4 | n |  | TRUE
89 | bus_LV_2405-1_0_4_node_123 | 0.4 | n |  | TRUE
90 | bus_LV_2405-1_0_4_node_48 | 0.4 | n |  | TRUE
91 | bus_LV_2405-1_0_4_node_49 | 0.4 | n |  | TRUE
92 | bus_LV_2405-1_0_4_node_51 | 0.4 | n |  | TRUE
93 | bus_LV_2405-1_0_4_node_55 | 0.4 | n |  | TRUE
94 | bus_LV_2405-1_0_4_node_56 | 0.4 | n |  | TRUE
95 | bus_LV_2405-1_0_4_node_130 | 0.4 | n |  | TRUE
96 | bus_LV_2405-1_0_4_node_83 | 0.4 | n |  | TRUE
97 | bus_LV_2405-1_0_4_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_2405-1_0_4_node_57 | 0.4 | n |  | TRUE
99 | bus_LV_2405-1_0_4_node_58 | 0.4 | n |  | TRUE
100 | bus_LV_2405-1_0_4_node_142 | 0.4 | n |  | TRUE
101 | bus_LV_2405-1_0_4_node_63 | 0.4 | n |  | TRUE
102 | bus_LV_2405-1_0_4_node_65 | 0.4 | n |  | TRUE
103 | bus_LV_2405-1_0_4_node_113 | 0.4 | n |  | TRUE
104 | bus_LV_2405-1_0_4_node_85 | 0.4 | n |  | TRUE
105 | bus_LV_2405-1_0_4_node_111 | 0.4 | n |  | TRUE
106 | bus_LV_2405-1_0_4_node_86 | 0.4 | n |  | TRUE
107 | bus_LV_2405-1_0_4_node_67 | 0.4 | n |  | TRUE
108 | bus_LV_2405-1_0_4_node_68 | 0.4 | n |  | TRUE
109 | bus_LV_2405-1_0_4_node_69 | 0.4 | n |  | TRUE
110 | bus_LV_2405-1_0_4_node_70 | 0.4 | n |  | TRUE
111 | bus_LV_2405-1_0_4_node_71 | 0.4 | n |  | TRUE
112 | bus_LV_2405-1_0_4_node_72 | 0.4 | n |  | TRUE
113 | bus_LV_2405-1_0_4_node_118 | 0.4 | n |  | TRUE
114 | bus_LV_2405-1_0_4_node_74 | 0.4 | n |  | TRUE
115 | bus_LV_2405-1_0_4_node_144 | 0.4 | n |  | TRUE
116 | bus_LV_2405-1_0_4_node_75 | 0.4 | n |  | TRUE
117 | bus_LV_2405-1_0_4_node_145 | 0.4 | n |  | TRUE
118 | bus_LV_2405-1_0_4_node_76 | 0.4 | n |  | TRUE
119 | bus_LV_2405-1_0_4_node_126 | 0.4 | n |  | TRUE
120 | bus_LV_2405-1_0_4_node_117 | 0.4 | n |  | TRUE
121 | bus_LV_2405-1_0_4_node_131 | 0.4 | n |  | TRUE
122 | bus_LV_2405-1_0_4_node_136 | 0.4 | n |  | TRUE
123 | bus_LV_2405-1_0_4_node_138 | 0.4 | n |  | TRUE
124 | bus_LV_2405-1_0_4_node_89 | 0.4 | n |  | TRUE
125 | bus_LV_2405-1_0_4_node_92 | 0.4 | n |  | TRUE
126 | bus_LV_2405-1_0_4_node_121 | 0.4 | n |  | TRUE
127 | bus_LV_2405-1_0_4_node_99 | 0.4 | n |  | TRUE
128 | bus_LV_2405-1_0_4_node_100 | 0.4 | n |  | TRUE
129 | bus_LV_2405-1_0_4_node_101 | 0.4 | n |  | TRUE
130 | bus_LV_2405-1_0_4_node_102 | 0.4 | n |  | TRUE
131 | bus_LV_2405-1_0_4_node_103 | 0.4 | n |  | TRUE
132 | bus_LV_2405-1_0_4_node_105 | 0.4 | n |  | TRUE
133 | bus_LV_2405-1_0_4_node_147 | 0.4 | n |  | TRUE
134 | bus_LV_2405-1_0_4_node_146 | 0.4 | n |  | TRUE
135 | bus_LV_2405-1_0_4_node_106 | 0.4 | n |  | TRUE
136 | bus_LV_2405-1_0_4_node_107 | 0.4 | n |  | TRUE
137 | bus_LV_2405-1_0_4_node_108 | 0.4 | n |  | TRUE
138 | bus_LV_2405-1_0_4_node_148 | 0.4 | n |  | TRUE
139 | bus_LV_2405-1_0_4_node_112 | 0.4 | n |  | TRUE
140 | bus_LV_2405-1_0_4_node_114 | 0.4 | n |  | TRUE
141 | bus_LV_2405-1_0_4_node_132 | 0.4 | n |  | TRUE
142 | bus_LV_2405-1_0_4_node_119 | 0.4 | n |  | TRUE
143 | bus_LV_2405-1_0_4_node_120 | 0.4 | n |  | TRUE
144 | bus_LV_2405-1_0_4_node_122 | 0.4 | n |  | TRUE
145 | bus_LV_2405-1_0_4_node_133 | 0.4 | n |  | TRUE
146 | bus_LV_2405-1_0_4_node_143 | 0.4 | n |  | TRUE
147 | bus_MV_334_0_node_130 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2405-1_0_4_load_0 | 0 | 0.00060656 | 0.00015202 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2405-1_0_4_load_1 | 1 | 0.00049207 | 0.00012332 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2405-1_0_4_load_2 | 2 | 0.0018305 | 0.00045876 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2405-1_0_4_load_3 | 3 | 0.0044192 | 0.0011075 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2405-1_0_4_load_4 | 4 | 0.0038072 | 0.00095416 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2405-1_0_4_load_39 | 5 | 0.001377 | 0.0003451 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2405-1_0_4_load_40 | 7 | 0.00099538 | 0.00024947 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2405-1_0_4_load_54 | 8 | 0.0014707 | 0.00036858 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2405-1_0_4_load_5 | 9 | 0.00034435 | 8.6302e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2405-1_0_4_load_10 | 13 | 0.00078405 | 0.0001965 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2405-1_0_4_load_12 | 14 | 0.0023743 | 0.00059506 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2405-1_0_4_load_95 | 16 | 0.0023149 | 0.00058018 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2405-1_0_4_load_98 | 17 | 0.0017571 | 0.00044037 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2405-1_0_4_load_97 | 18 | 0.00041566 | 0.00010417 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2405-1_0_4_load_91 | 21 | 0.0021497 | 0.00053876 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2405-1_0_4_load_94 | 23 | 0.0002013 | 5.045e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2405-1_0_4_load_66 | 24 | 0.0015535 | 0.00038935 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2405-1_0_4_load_60 | 25 | 0.0017523 | 0.00043916 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2405-1_0_4_load_62 | 26 | 0.00036961 | 9.2633e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2405-1_0_4_load_137 | 28 | 0.0055618 | 0.0013939 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2405-1_0_4_load_59 | 29 | 0.00035133 | 8.8052e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2405-1_0_4_load_13 | 30 | 0.0028258 | 0.00070822 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2405-1_0_4_load_14 | 31 | 0.0028548 | 0.00071549 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2405-1_0_4_load_15 | 32 | 0.014236 | 0.0035678 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2405-1_0_4_load_141 | 35 | 0.0104 | 0.0026064 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2405-1_0_4_load_135 | 36 | 0.0046186 | 0.0011575 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2405-1_0_4_load_77 | 37 | 0.0030056 | 0.00075328 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2405-1_0_4_load_134 | 38 | 0.0046261 | 0.0011594 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2405-1_0_4_load_18 | 39 | 0.00098111 | 0.00024589 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2405-1_0_4_load_19 | 40 | 0.0020238 | 0.0005072 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2405-1_0_4_load_20 | 41 | 0.00064783 | 0.00016236 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2405-1_0_4_load_22 | 43 | 0.00079893 | 0.00020023 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2405-1_0_4_load_73 | 44 | 0.0011339 | 0.00028419 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2405-1_0_4_load_78 | 46 | 0.0013986 | 0.00035053 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2405-1_0_4_load_32 | 47 | 0.0017586 | 0.00044074 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2405-1_0_4_load_28 | 48 | 0.000472 | 0.00011829 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2405-1_0_4_load_79 | 49 | 0.00086451 | 0.00021667 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2405-1_0_4_load_23 | 50 | 0.0039763 | 0.00099657 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2405-1_0_4_load_26 | 52 | 0.00072786 | 0.00018242 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2405-1_0_4_load_27 | 53 | 0.0011785 | 0.00029536 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2405-1_0_4_load_115 | 54 | 0.00092399 | 0.00023157 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2405-1_0_4_load_116 | 55 | 0.0012211 | 0.00030603 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2405-1_0_4_load_29 | 56 | 0.00057914 | 0.00014515 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2405-1_0_4_load_31 | 57 | 0.00084085 | 0.00021074 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2405-1_0_4_load_93 | 59 | 0.00022262 | 5.5795e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2405-1_0_4_load_110 | 60 | 0.0031227 | 0.00078261 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2405-1_0_4_load_33 | 61 | 0.00061873 | 0.00015507 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2405-1_0_4_load_34 | 62 | 0.0013762 | 0.00034492 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2405-1_0_4_load_35 | 63 | 0.0015129 | 0.00037918 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2405-1_0_4_load_36 | 64 | 0.00078017 | 0.00019553 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2405-1_0_4_load_37 | 65 | 0.0013227 | 0.00033151 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2405-1_0_4_load_125 | 66 | 0.0013787 | 0.00034554 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2405-1_0_4_load_124 | 68 | 0.00077022 | 0.00019303 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2405-1_0_4_load_129 | 69 | 0.0046087 | 0.001155 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2405-1_0_4_load_127 | 70 | 0.0015561 | 0.00039 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2405-1_0_4_load_109 | 71 | 0.0012225 | 0.00030639 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2405-1_0_4_load_140 | 73 | 0.0010449 | 0.00026187 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2405-1_0_4_load_104 | 75 | 0.0015518 | 0.00038891 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2405-1_0_4_load_80 | 76 | 0.006217 | 0.0015581 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2405-1_0_4_load_50 | 77 | 0.0023288 | 0.00058366 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2405-1_0_4_load_42 | 78 | 0.0016918 | 0.000424 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2405-1_0_4_load_43 | 79 | 0.00098866 | 0.00024778 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2405-1_0_4_load_45 | 81 | 0.0024733 | 0.00061986 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2405-1_0_4_load_46 | 82 | 0.0010126 | 0.00025379 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2405-1_0_4_load_81 | 84 | 0.0027654 | 0.00069308 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2405-1_0_4_load_87 | 85 | 0.0038674 | 0.00096927 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2405-1_0_4_load_96 | 86 | 0.0029578 | 0.00074129 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2405-1_0_4_load_88 | 88 | 0.00098891 | 0.00024784 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2405-1_0_4_load_123 | 89 | 0.0016364 | 0.00041012 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2405-1_0_4_load_48 | 90 | 0.0028166 | 0.00070591 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2405-1_0_4_load_49 | 91 | 0.00048513 | 0.00012159 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2405-1_0_4_load_51 | 92 | 0.00024333 | 6.0983e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2405-1_0_4_load_55 | 93 | 0.00068362 | 0.00017133 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2405-1_0_4_load_56 | 94 | 0.0008165 | 0.00020463 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2405-1_0_4_load_130 | 95 | 0.0010263 | 0.00025722 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2405-1_0_4_load_83 | 96 | 0.0015661 | 0.00039249 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2405-1_0_4_load_84 | 97 | 0.00051561 | 0.00012922 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2405-1_0_4_load_57 | 98 | 0.00059431 | 0.00014895 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2405-1_0_4_load_58 | 99 | 0.0017311 | 0.00043386 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2405-1_0_4_load_142 | 100 | 0.003288 | 0.00082404 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2405-1_0_4_load_63 | 101 | 0.0040497 | 0.001015 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2405-1_0_4_load_65 | 102 | 0.0010629 | 0.00026638 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2405-1_0_4_load_113 | 103 | 0.00081862 | 0.00020516 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2405-1_0_4_load_85 | 104 | 0.00039234 | 9.833e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2405-1_0_4_load_111 | 105 | 0.00036075 | 9.0414e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2405-1_0_4_load_86 | 106 | 0.00047129 | 0.00011812 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2405-1_0_4_load_67 | 107 | 0.0011172 | 0.00028 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2405-1_0_4_load_68 | 108 | 0.0022678 | 0.00056837 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2405-1_0_4_load_70 | 110 | 0.00055679 | 0.00013955 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2405-1_0_4_load_71 | 111 | 0.0022576 | 0.00056581 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2405-1_0_4_load_72 | 112 | 0.00044512 | 0.00011156 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2405-1_0_4_load_118 | 113 | 0.0020162 | 0.0005053 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2405-1_0_4_load_74 | 114 | 0.0014876 | 0.00037284 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2405-1_0_4_load_144 | 115 | 0.00057299 | 0.0001436 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2405-1_0_4_load_75 | 116 | 0.0010027 | 0.00025131 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2405-1_0_4_load_76 | 118 | 0.0014632 | 0.00036671 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2405-1_0_4_load_126 | 119 | 0.0020366 | 0.00051041 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2405-1_0_4_load_117 | 120 | 0.001205 | 0.00030201 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2405-1_0_4_load_131 | 121 | 0.0033612 | 0.0008424 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2405-1_0_4_load_138 | 123 | 0.0043533 | 0.001091 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2405-1_0_4_load_89 | 124 | 0.0013865 | 0.00034748 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2405-1_0_4_load_92 | 125 | 0.00044116 | 0.00011056 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2405-1_0_4_load_121 | 126 | 0.0011089 | 0.00027792 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2405-1_0_4_load_99 | 127 | 0.0015402 | 0.00038601 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2405-1_0_4_load_100 | 128 | 0.0012215 | 0.00030613 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2405-1_0_4_load_101 | 129 | 0.00132 | 0.00033082 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2405-1_0_4_load_102 | 130 | 0.0011513 | 0.00028855 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2405-1_0_4_load_105 | 132 | 0.0030484 | 0.000764 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2405-1_0_4_load_147 | 133 | 0.0088284 | 0.0022126 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2405-1_0_4_load_146 | 134 | 0.002915 | 0.00073058 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2405-1_0_4_load_106 | 135 | 0.00036356 | 9.1117e-05 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2405-1_0_4_load_107 | 136 | 0.00053855 | 0.00013497 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2405-1_0_4_load_112 | 139 | 0.0018471 | 0.00046294 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2405-1_0_4_load_114 | 140 | 0.00026969 | 6.759e-05 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2405-1_0_4_load_132 | 141 | 0.00055894 | 0.00014008 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2405-1_0_4_load_119 | 142 | 0.0013055 | 0.0003272 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2405-1_0_4_load_120 | 143 | 0.0014095 | 0.00035325 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2405-1_0_4_load_133 | 145 | 0.00074698 | 0.00018721 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2405-1_0_4_load_143 | 146 | 0.0016065 | 0.00040262 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 105 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2405-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.01574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_2405-1_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0046145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_2405-1_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0045705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_2405-1_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.024233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_2405-1_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0028432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_2405-1_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_2405-1_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0011977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_2405-1_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0073364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_2405-1_0_4_line_8 | NAYY 4x150 SE | 7 | 72 | 0.030046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_2405-1_0_4_line_9 | NAYY 4x150 SE | 8 | 34 | 0.012255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_2405-1_0_4_line_10 | NAYY 4x150 SE | 9 | 10 | 0.0312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2405-1_0_4_line_11 | NAYY 4x150 SE | 9 | 11 | 0.031137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2405-1_0_4_line_12 | NAYY 4x150 SE | 10 | 12 | 0.009959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2405-1_0_4_line_13 | NAYY 4x150 SE | 10 | 13 | 0.026904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2405-1_0_4_line_14 | NAYY 4x150 SE | 11 | 14 | 0.015692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2405-1_0_4_line_15 | NAYY 4x150 SE | 12 | 15 | 0.004589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2405-1_0_4_line_16 | NAYY 4x150 SE | 12 | 16 | 0.048047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2405-1_0_4_line_17 | NAYY 4x150 SE | 13 | 18 | 0.025714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2405-1_0_4_line_18 | NAYY 4x150 SE | 14 | 22 | 0.022498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2405-1_0_4_line_19 | NAYY 4x150 SE | 15 | 17 | 0.029219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2405-1_0_4_line_20 | NAYY 4x150 SE | 16 | 23 | 0.021003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2405-1_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.004853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2405-1_0_4_line_22 | NAYY 4x150 SE | 19 | 21 | 0.03451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2405-1_0_4_line_23 | NAYY 4x150 SE | 20 | 24 | 0.026342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2405-1_0_4_line_24 | NAYY 4x150 SE | 20 | 25 | 0.030925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2405-1_0_4_line_25 | NAYY 4x150 SE | 20 | 26 | 0.035956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2405-1_0_4_line_26 | NAYY 4x150 SE | 21 | 27 | 0.03043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2405-1_0_4_line_27 | NAYY 4x150 SE | 22 | 28 | 0.0067471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2405-1_0_4_line_28 | NAYY 4x150 SE | 22 | 29 | 0.016832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2405-1_0_4_line_29 | NAYY 4x150 SE | 23 | 59 | 0.0062911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2405-1_0_4_line_30 | NAYY 4x150 SE | 24 | 104 | 0.050818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2405-1_0_4_line_31 | NAYY 4x150 SE | 25 | 99 | 0.0091906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2405-1_0_4_line_32 | NAYY 4x150 SE | 26 | 101 | 0.0040965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2405-1_0_4_line_33 | NAYY 4x150 SE | 27 | 125 | 0.038905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2405-1_0_4_line_34 | NAYY 4x150 SE | 27 | 124 | 0.030459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2405-1_0_4_line_35 | NAYY 4x150 SE | 28 | 100 | 0.02253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2405-1_0_4_line_36 | NAYY 4x150 SE | 29 | 98 | 0.026747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2405-1_0_4_line_37 | NAYY 4x150 SE | 30 | 31 | 0.0082431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_2405-1_0_4_line_38 | NAYY 4x150 SE | 30 | 32 | 0.0018959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_2405-1_0_4_line_39 | NAYY 4x150 SE | 31 | 33 | 0.02728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_2405-1_0_4_line_40 | NAYY 4x150 SE | 32 | 34 | 0.029644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_2405-1_0_4_line_41 | NAYY 4x150 SE | 33 | 35 | 0.023531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2405-1_0_4_line_42 | NAYY 4x150 SE | 33 | 36 | 0.041737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_2405-1_0_4_line_43 | NAYY 4x150 SE | 34 | 37 | 0.021906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2405-1_0_4_line_44 | NAYY 4x150 SE | 36 | 38 | 0.041642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_2405-1_0_4_line_45 | NAYY 4x150 SE | 38 | 87 | 0.013811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_2405-1_0_4_line_46 | NAYY 4x150 SE | 39 | 40 | 0.0006185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2405-1_0_4_line_47 | NAYY 4x150 SE | 39 | 41 | 0.0012636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2405-1_0_4_line_48 | NAYY 4x150 SE | 40 | 42 | 0.039936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2405-1_0_4_line_49 | NAYY 4x150 SE | 41 | 43 | 0.016157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2405-1_0_4_line_50 | NAYY 4x150 SE | 42 | 44 | 0.019321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2405-1_0_4_line_51 | NAYY 4x150 SE | 42 | 45 | 0.004148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2405-1_0_4_line_52 | NAYY 4x150 SE | 43 | 46 | 0.018829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2405-1_0_4_line_53 | NAYY 4x150 SE | 45 | 47 | 0.032073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2405-1_0_4_line_54 | NAYY 4x150 SE | 45 | 48 | 0.04095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2405-1_0_4_line_55 | NAYY 4x150 SE | 46 | 49 | 0.0092645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2405-1_0_4_line_56 | NAYY 4x150 SE | 47 | 59 | 0.0078538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2405-1_0_4_line_57 | NAYY 4x150 SE | 48 | 56 | 0.0061204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2405-1_0_4_line_58 | NAYY 4x150 SE | 49 | 120 | 0.011283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2405-1_0_4_line_59 | NAYY 4x150 SE | 50 | 51 | 0.09007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2405-1_0_4_line_60 | NAYY 4x150 SE | 51 | 52 | 0.042259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2405-1_0_4_line_61 | NAYY 4x150 SE | 51 | 53 | 0.040644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2405-1_0_4_line_62 | NAYY 4x150 SE | 52 | 54 | 0.020515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2405-1_0_4_line_63 | NAYY 4x150 SE | 54 | 55 | 0.0077221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2405-1_0_4_line_64 | NAYY 4x150 SE | 55 | 120 | 0.011164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2405-1_0_4_line_65 | NAYY 4x150 SE | 56 | 57 | 0.020064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2405-1_0_4_line_66 | NAYY 4x150 SE | 57 | 58 | 0.017259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2405-1_0_4_line_67 | NAYY 4x150 SE | 58 | 60 | 0.046212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2405-1_0_4_line_68 | NAYY 4x150 SE | 60 | 71 | 0.033569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2405-1_0_4_line_69 | NAYY 4x150 SE | 61 | 62 | 0.0066998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2405-1_0_4_line_70 | NAYY 4x150 SE | 61 | 63 | 0.017083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2405-1_0_4_line_71 | NAYY 4x150 SE | 62 | 64 | 0.0065548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2405-1_0_4_line_72 | NAYY 4x150 SE | 63 | 65 | 0.014352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2405-1_0_4_line_73 | NAYY 4x150 SE | 64 | 66 | 0.0015917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2405-1_0_4_line_74 | NAYY 4x150 SE | 65 | 67 | 0.018588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2405-1_0_4_line_75 | NAYY 4x150 SE | 66 | 68 | 0.015583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
76 | LV_2405-1_0_4_line_76 | NAYY 4x150 SE | 67 | 69 | 0.020886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2405-1_0_4_line_77 | NAYY 4x150 SE | 67 | 70 | 0.044174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2405-1_0_4_line_78 | NAYY 4x150 SE | 68 | 119 | 0.0088003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_2405-1_0_4_line_79 | NAYY 4x150 SE | 70 | 128 | 0.0085413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2405-1_0_4_line_80 | NAYY 4x150 SE | 72 | 73 | 0.012298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2405-1_0_4_line_81 | NAYY 4x150 SE | 72 | 74 | 0.034584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
82 | LV_2405-1_0_4_line_82 | NAYY 4x150 SE | 73 | 75 | 0.011703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2405-1_0_4_line_83 | NAYY 4x150 SE | 74 | 76 | 0.031943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
84 | LV_2405-1_0_4_line_84 | NAYY 4x150 SE | 74 | 77 | 0.025705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2405-1_0_4_line_85 | NAYY 4x150 SE | 75 | 130 | 0.013574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2405-1_0_4_line_86 | NAYY 4x150 SE | 76 | 95 | 0.016462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_2405-1_0_4_line_87 | NAYY 4x150 SE | 77 | 90 | 0.0033317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2405-1_0_4_line_88 | NAYY 4x150 SE | 78 | 79 | 0.010037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_2405-1_0_4_line_89 | NAYY 4x150 SE | 78 | 80 | 0.014498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_2405-1_0_4_line_90 | NAYY 4x150 SE | 79 | 81 | 0.012317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_2405-1_0_4_line_91 | NAYY 4x150 SE | 80 | 82 | 0.022322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2405-1_0_4_line_92 | NAYY 4x150 SE | 80 | 83 | 0.004841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_2405-1_0_4_line_93 | NAYY 4x150 SE | 81 | 84 | 0.024276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_2405-1_0_4_line_94 | NAYY 4x150 SE | 82 | 85 | 0.013684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2405-1_0_4_line_95 | NAYY 4x150 SE | 83 | 86 | 0.021771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_2405-1_0_4_line_96 | NAYY 4x150 SE | 84 | 87 | 0.0080731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_2405-1_0_4_line_97 | NAYY 4x150 SE | 85 | 88 | 0.015156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2405-1_0_4_line_98 | NAYY 4x150 SE | 86 | 89 | 0.026542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_2405-1_0_4_line_99 | NAYY 4x150 SE | 87 | 122 | 0.0135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2405-1_0_4_line_100 | NAYY 4x150 SE | 89 | 126 | 0.013248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_2405-1_0_4_line_101 | NAYY 4x150 SE | 90 | 91 | 0.014322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2405-1_0_4_line_102 | NAYY 4x150 SE | 91 | 92 | 0.0031337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2405-1_0_4_line_103 | NAYY 4x150 SE | 92 | 93 | 0.0075327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2405-1_0_4_line_104 | NAYY 4x150 SE | 93 | 94 | 0.008801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2405-1_0_4_line_105 | NAYY 4x150 SE | 94 | 96 | 7.1906e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2405-1_0_4_line_106 | NAYY 4x150 SE | 95 | 121 | 0.0079248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_2405-1_0_4_line_107 | NAYY 4x150 SE | 96 | 97 | 0.0061743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2405-1_0_4_line_108 | NAYY 4x150 SE | 98 | 99 | 0.031093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2405-1_0_4_line_109 | NAYY 4x150 SE | 100 | 146 | 0.039983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2405-1_0_4_line_110 | NAYY 4x150 SE | 101 | 102 | 0.011611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2405-1_0_4_line_111 | NAYY 4x150 SE | 102 | 103 | 0.0017665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2405-1_0_4_line_112 | NAYY 4x150 SE | 103 | 105 | 0.018635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2405-1_0_4_line_113 | NAYY 4x150 SE | 104 | 106 | 0.0049271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2405-1_0_4_line_114 | NAYY 4x150 SE | 105 | 139 | 0.0073137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
115 | LV_2405-1_0_4_line_115 | NAYY 4x150 SE | 107 | 108 | 0.0029775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2405-1_0_4_line_116 | NAYY 4x150 SE | 107 | 109 | 0.027175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2405-1_0_4_line_117 | NAYY 4x150 SE | 108 | 110 | 0.0093242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2405-1_0_4_line_118 | NAYY 4x150 SE | 109 | 111 | 0.017626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
119 | LV_2405-1_0_4_line_119 | NAYY 4x150 SE | 109 | 112 | 0.016435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
120 | LV_2405-1_0_4_line_120 | NAYY 4x150 SE | 110 | 113 | 0.027013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2405-1_0_4_line_121 | NAYY 4x150 SE | 111 | 114 | 0.022805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
122 | LV_2405-1_0_4_line_122 | NAYY 4x150 SE | 112 | 115 | 0.067095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
123 | LV_2405-1_0_4_line_123 | NAYY 4x150 SE | 114 | 116 | 0.022349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
124 | LV_2405-1_0_4_line_124 | NAYY 4x150 SE | 115 | 117 | 0.028671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
125 | LV_2405-1_0_4_line_125 | NAYY 4x150 SE | 116 | 118 | 0.019561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
126 | LV_2405-1_0_4_line_126 | NAYY 4x150 SE | 117 | 145 | 0.012717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
127 | LV_2405-1_0_4_line_127 | NAYY 4x150 SE | 118 | 119 | 0.0091062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
128 | LV_2405-1_0_4_line_128 | NAYY 4x150 SE | 121 | 141 | 0.0039508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
129 | LV_2405-1_0_4_line_129 | NAYY 4x150 SE | 122 | 123 | 0.031115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_2405-1_0_4_line_130 | NAYY 4x150 SE | 126 | 142 | 0.016428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
131 | LV_2405-1_0_4_line_131 | NAYY 4x150 SE | 127 | 128 | 0.014904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_2405-1_0_4_line_132 | NAYY 4x150 SE | 129 | 130 | 0.015695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_2405-1_0_4_line_133 | NAYY 4x150 SE | 129 | 131 | 0.0062026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_2405-1_0_4_line_134 | NAYY 4x150 SE | 131 | 132 | 0.02374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_2405-1_0_4_line_135 | NAYY 4x150 SE | 132 | 133 | 0.027308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_2405-1_0_4_line_136 | NAYY 4x150 SE | 133 | 134 | 0.00080317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_2405-1_0_4_line_137 | NAYY 4x150 SE | 134 | 138 | 0.07118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_2405-1_0_4_line_138 | NAYY 4x150 SE | 135 | 136 | 0.042122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_2405-1_0_4_line_139 | NAYY 4x150 SE | 136 | 137 | 0.032468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_2405-1_0_4_line_140 | NAYY 4x150 SE | 137 | 138 | 0.052288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_2405-1_0_4_line_141 | NAYY 4x150 SE | 139 | 140 | 0.010722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
142 | LV_2405-1_0_4_line_142 | NAYY 4x150 SE | 140 | 141 | 0.0019774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
143 | LV_2405-1_0_4_line_143 | NAYY 4x150 SE | 142 | 143 | 0.023585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
144 | LV_2405-1_0_4_line_144 | NAYY 4x150 SE | 143 | 144 | 0.013706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
145 | LV_2405-1_0_4_line_145 | NAYY 4x150 SE | 144 | 145 | 0.0060041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2405-1_0_4_trafo_111 | 0.25 MVA 20/0.4 kV | 147 | 105 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2625137.1193 | 1238567.4871 | 2625144.3116 | 1238553.486
1 | 2625137.1193 | 1238567.4871 | 2625135.0108 | 1238571.5917
2 | 2625144.3116 | 1238553.486 | 2625146.4001 | 1238549.4205
3 | 2625124.7258 | 1238593.5244 | 2625131.1035 | 1238579.1981 | 2625135.0108 | 1238571.5917
4 | 2625147.6992 | 1238546.8915 | 2625146.4001 | 1238549.4205
5 | 2625116.1446 | 1238612.8003 | 2625124.7258 | 1238593.5244
6 | 2625148.2465 | 1238545.8261 | 2625147.6992 | 1238546.8915
7 | 2625116.1446 | 1238612.8003 | 2625113.3488 | 1238619.5831
8 | 2625161.2654 | 1238518.7545 | 2625153.5401 | 1238535.5212 | 2625148.2465 | 1238545.8261
9 | 2625108.6786 | 1238630.9135 | 2625113.3488 | 1238619.5831
10 | 2624879.387 | 1238398.9502 | 2624902.1027 | 1238412.9984 | 2624906.08 | 1238415.0837
11 | 2624934.3526 | 1238427.8649 | 2624924.6762 | 1238424.8336 | 2624906.08 | 1238415.0837
12 | 2624870.8998 | 1238393.7003 | 2624879.387 | 1238398.9502
13 | 2624879.387 | 1238398.9502 | 2624881.5884 | 1238395.2682 | 2624867.3366 | 1238386.6143 | 2624862.2512 | 1238383.5429
14 | 2624934.3526 | 1238427.8649 | 2624934.8162 | 1238438.1733 | 2624932.3513 | 1238442.9479
15 | 2624868.2594 | 1238397.4583 | 2624870.8998 | 1238393.7003
16 | 2624870.8998 | 1238393.7003 | 2624830.1006 | 1238368.403 | 2624830.066 | 1238368.3804
17 | 2624840.2402 | 1238370.249 | 2624862.2512 | 1238383.5429
18 | 2624920.8888 | 1238462.2522 | 2624926.7406 | 1238453.8159 | 2624932.3513 | 1238442.9479
19 | 2624868.2594 | 1238397.4583 | 2624853.8442 | 1238417.0547 | 2624850.881 | 1238420.9468
20 | 2624830.066 | 1238368.3804 | 2624817.3978 | 1238360.1004 | 2624812.9157 | 1238356.3114
21 | 2624991.5558 | 1238440.7462 | 2624986.8026 | 1238439.7034
22 | 2624986.8026 | 1238439.7034 | 2624984.697 | 1238431.4005 | 2624982.8998 | 1238428.9025 | 2624980.6012 | 1238426.9027 | 2624974.4032 | 1238422.296 | 2624964.0987 | 1238415.9571
23 | 2624991.5558 | 1238440.7462 | 2624996.7023 | 1238429.2051 | 2625004.2429 | 1238417.7611
24 | 2624991.5558 | 1238440.7462 | 2624974.7312 | 1238466.6936
25 | 2624991.5558 | 1238440.7462 | 2625004.2028 | 1238444.2237 | 2625013.5214 | 1238447.7985 | 2625020.4083 | 1238450.4513 | 2625025.3282 | 1238452.8613
26 | 2624938.0766 | 1238400.1855 | 2624947.5985 | 1238405.8067 | 2624964.0987 | 1238415.9571
27 | 2624920.8888 | 1238462.2522 | 2624917.046 | 1238467.798
28 | 2624920.8888 | 1238462.2522 | 2624928.6018 | 1238477.2126
29 | 2624808.1113 | 1238352.2499 | 2624812.9157 | 1238356.3114
30 | 2625032.2038 | 1238375.3266 | 2625004.2429 | 1238417.7611
31 | 2624974.7312 | 1238466.6936 | 2624969.7311 | 1238474.405
32 | 2625029.007 | 1238454.6634 | 2625025.3282 | 1238452.8613
33 | 2624938.0766 | 1238400.1855 | 2624920.0043 | 1238388.1356 | 2624929.3078 | 1238373.6878
34 | 2624938.0766 | 1238400.1855 | 2624920.0043 | 1238388.1356 | 2624924.7351 | 1238380.7889
35 | 2624917.046 | 1238467.798 | 2624904.2143 | 1238486.3164
36 | 2624947.4581 | 1238490.6211 | 2624940.6637 | 1238492.087 | 2624934.101 | 1238487.8791 | 2624928.6018 | 1238477.2126
37 | 2625136.5787 | 1238645.6222 | 2625143.8705 | 1238649.4664
38 | 2625134.9016 | 1238644.738 | 2625136.5787 | 1238645.6222
39 | 2625142.8801 | 1238670.3825 | 2625151.219 | 1238653.3405 | 2625143.8705 | 1238649.4664
40 | 2625108.6786 | 1238630.9135 | 2625134.9016 | 1238644.738
41 | 2625142.8801 | 1238670.3825 | 2625163.7803 | 1238681.1943
42 | 2625142.8801 | 1238670.3825 | 2625124.5261 | 1238707.8677
43 | 2625108.6786 | 1238630.9135 | 2625100.0253 | 1238651.0376
44 | 2625126.3847 | 1238739.242 | 2625115.6719 | 1238733.6738 | 2625113.088 | 1238731.2281 | 2625124.5261 | 1238707.8677
45 | 2625123.4984 | 1238750.1727 | 2625128.8486 | 1238740.5226 | 2625126.3847 | 1238739.242
46 | 2624813.9487 | 1238284.262 | 2624814.3263 | 1238283.7722
47 | 2624815.0978 | 1238282.7714 | 2624814.3263 | 1238283.7722
48 | 2624789.5657 | 1238315.8902 | 2624813.9487 | 1238284.262
49 | 2624815.0978 | 1238282.7714 | 2624824.9624 | 1238269.9757
50 | 2624789.5657 | 1238315.8902 | 2624799.4799 | 1238332.4735
51 | 2624789.5657 | 1238315.8902 | 2624786.6037 | 1238318.8019
52 | 2624824.9624 | 1238269.9757 | 2624836.4585 | 1238255.0636
53 | 2624786.6037 | 1238318.8019 | 2624798.8036 | 1238340.6997 | 2624803.0981 | 1238346.2355
54 | 2624786.6037 | 1238318.8019 | 2624766.6944 | 1238283.0169
55 | 2624842.115 | 1238247.7263 | 2624836.4585 | 1238255.0636
56 | 2624803.0981 | 1238346.2355 | 2624807.1019 | 1238351.3965 | 2624808.1113 | 1238352.2499
57 | 2624766.6944 | 1238283.0169 | 2624763.7188 | 1238277.6686
58 | 2624842.115 | 1238247.7263 | 2624849.004 | 1238238.7903
59 | 2624898.3316 | 1238173.7223 | 2624974.4767 | 1238221.8329
60 | 2624898.3316 | 1238173.7223 | 2624890.5561 | 1238184.4965 | 2624886.8354 | 1238189.7175 | 2624873.0606 | 1238207.5855
61 | 2624898.3316 | 1238173.7223 | 2624887.8327 | 1238170.1095 | 2624860.1959 | 1238165.9692 | 2624858.8015 | 1238165.1927
62 | 2624860.5351 | 1238223.8328 | 2624873.0606 | 1238207.5855
63 | 2624855.8204 | 1238229.9485 | 2624860.5351 | 1238223.8328
64 | 2624855.8204 | 1238229.9485 | 2624849.004 | 1238238.7903
65 | 2624752.265 | 1238261.2141 | 2624762.399 | 1238275.2962 | 2624763.7188 | 1238277.6686
66 | 2624742.184 | 1238247.2058 | 2624752.265 | 1238261.2141
67 | 2624742.184 | 1238247.2058 | 2624770.3395 | 1238210.5613
68 | 2624770.3395 | 1238210.5613 | 2624790.7918 | 1238183.9425
69 | 2624779.5371 | 1238549.8402 | 2624785.4379 | 1238553.0131
70 | 2624779.5371 | 1238549.8402 | 2624767.1982 | 1238543.2055 | 2624764.5256 | 1238541.6871
71 | 2624785.4379 | 1238553.0131 | 2624787.0988 | 1238553.9061 | 2624791.2589 | 1238556.026
72 | 2624752.067 | 1238534.5632 | 2624753.1028 | 1238535.1974 | 2624764.5256 | 1238541.6871
73 | 2624792.6771 | 1238556.7487 | 2624791.2589 | 1238556.026
74 | 2624736.2033 | 1238524.8985 | 2624737.9017 | 1238525.7061 | 2624743.3027 | 1238529.1974 | 2624752.067 | 1238534.5632
75 | 2624806.5613 | 1238563.8239 | 2624792.6771 | 1238556.7487
76 | 2624736.2033 | 1238524.8985 | 2624727.1031 | 1238537.9021 | 2624724.2128 | 1238542.0001
77 | 2624736.2033 | 1238524.8985 | 2624744.6026 | 1238514.905 | 2624758.9002 | 1238499.7995 | 2624766.1992 | 1238492.503
78 | 2624806.5613 | 1238563.8239 | 2624814.4022 | 1238567.8195
79 | 2624772.7639 | 1238487.0731 | 2624770.6028 | 1238488.4967 | 2624766.1992 | 1238492.503
80 | 2625161.2654 | 1238518.7545 | 2625172.8285 | 1238522.9416
81 | 2625161.2654 | 1238518.7545 | 2625129.8628 | 1238504.0682
82 | 2625172.8285 | 1238522.9416 | 2625174.6551 | 1238523.603 | 2625183.9174 | 1238526.6798
83 | 2625129.8628 | 1238504.0682 | 2625101.1765 | 1238490.016
84 | 2625129.8628 | 1238504.0682 | 2625141.1408 | 1238480.9697
85 | 2625196.7996 | 1238530.9591 | 2625183.9174 | 1238526.6798
86 | 2625086.3932 | 1238482.7743 | 2625101.1765 | 1238490.016
87 | 2625142.6026 | 1238477.9758 | 2625141.1408 | 1238480.9697
88 | 2625088.2656 | 1238722.8614 | 2625085.5829 | 1238719.8272 | 2625083.0658 | 1238714.3948
89 | 2625080.7722 | 1238700.2057 | 2625080.8611 | 1238706.032 | 2625082.5324 | 1238713.2435 | 2625083.0658 | 1238714.3948
90 | 2625097.5198 | 1238730.8956 | 2625091.2661 | 1238726.2551 | 2625088.2656 | 1238722.8614
91 | 2625080.7722 | 1238700.2057 | 2625073.0033 | 1238700.5065 | 2625070.3986 | 1238701.196 | 2625067.7998 | 1238702.2968 | 2625060.0343 | 1238706.907
92 | 2625081.3975 | 1238695.4054 | 2625080.7722 | 1238700.2057
93 | 2625117.0152 | 1238745.362 | 2625097.5198 | 1238730.8956
94 | 2625060.0343 | 1238706.907 | 2625048.2677 | 1238713.8924
95 | 2625081.3975 | 1238695.4054 | 2625071.0532 | 1238691.2592 | 2625062.1283 | 1238685.4912
96 | 2625123.4984 | 1238750.1727 | 2625117.0152 | 1238745.362
97 | 2625048.2677 | 1238713.8924 | 2625035.2353 | 1238721.6294
98 | 2625062.1283 | 1238685.4912 | 2625042.5336 | 1238672.8276 | 2625039.8098 | 1238671.1267
99 | 2625132.5335 | 1238759.828 | 2625131.4484 | 1238757.0995 | 2625128.6551 | 1238754.097 | 2625123.4984 | 1238750.1727
100 | 2625028.5726 | 1238664.1097 | 2625039.8098 | 1238671.1267
101 | 2625142.6026 | 1238477.9758 | 2625146.0225 | 1238470.9713 | 2625150.0301 | 1238465.8195
102 | 2625150.0301 | 1238465.8195 | 2625151.9542 | 1238463.3461
103 | 2625151.9542 | 1238463.3461 | 2625156.5793 | 1238457.4005
104 | 2625161.9831 | 1238450.4539 | 2625156.5793 | 1238457.4005
105 | 2625161.9831 | 1238450.4539 | 2625162.0272 | 1238450.3971
106 | 2625086.3932 | 1238482.7743 | 2625079.2764 | 1238479.2881
107 | 2625162.0272 | 1238450.3971 | 2625165.8182 | 1238445.5237
108 | 2624947.4581 | 1238490.6211 | 2624950.2177 | 1238490.0257 | 2624960.3354 | 1238474.3806 | 2624969.4553 | 1238474.8303 | 2624969.7311 | 1238474.405
109 | 2624881.4609 | 1238487.2028 | 2624882.2921 | 1238494.6331 | 2624893.2658 | 1238502.117 | 2624904.2143 | 1238486.3164
110 | 2625029.007 | 1238454.6634 | 2625039.4342 | 1238459.7712
111 | 2625041.0206 | 1238460.5483 | 2625039.4342 | 1238459.7712
112 | 2625041.0206 | 1238460.5483 | 2625057.7559 | 1238468.7462
113 | 2625032.2038 | 1238375.3266 | 2625034.9147 | 1238371.2124
114 | 2625057.7559 | 1238468.7462 | 2625064.3239 | 1238471.9635
115 | 2624880.1331 | 1238631.4867 | 2624878.4077 | 1238633.9133
116 | 2624895.8802 | 1238609.3393 | 2624880.1331 | 1238631.4867
117 | 2624878.4077 | 1238633.9133 | 2624873.0046 | 1238641.5125
118 | 2624895.8802 | 1238609.3393 | 2624880.1759 | 1238601.3366
119 | 2624895.8802 | 1238609.3393 | 2624905.2117 | 1238595.8108
120 | 2624873.0046 | 1238641.5125 | 2624857.3515 | 1238663.5276
121 | 2624859.8567 | 1238590.9823 | 2624880.1759 | 1238601.3366
122 | 2624950.805 | 1238607.2542 | 2624936.2018 | 1238587.5501 | 2624931.6407 | 1238584.0065 | 2624920.9788 | 1238577.9581 | 2624916.3047 | 1238579.7285 | 2624905.2117 | 1238595.8108
123 | 2624839.9445 | 1238580.8354 | 2624859.8567 | 1238590.9823
124 | 2624964.4998 | 1238631.8964 | 2624962.0813 | 1238622.4692 | 2624950.805 | 1238607.2542
125 | 2624839.9445 | 1238580.8354 | 2624822.5157 | 1238571.954
126 | 2624964.4998 | 1238631.8964 | 2624976.4992 | 1238634.604 | 2624976.9035 | 1238634.7015
127 | 2624822.5157 | 1238571.954 | 2624814.4022 | 1238567.8195
128 | 2625075.7285 | 1238477.5502 | 2625079.2764 | 1238479.2881
129 | 2625132.5335 | 1238759.828 | 2625132.0263 | 1238763.5282 | 2625129.8578 | 1238768.3776 | 2625117.1854 | 1238786.4443
130 | 2625014.6385 | 1238655.4086 | 2625028.5726 | 1238664.1097
131 | 2624772.7639 | 1238487.0731 | 2624775.601 | 1238485.2043 | 2624782.604 | 1238481.798 | 2624785.9178 | 1238480.1099
132 | 2625211.8007 | 1238535.5712 | 2625199.7763 | 1238531.9479 | 2625196.7996 | 1238530.9591
133 | 2625217.7396 | 1238537.3607 | 2625211.8007 | 1238535.5712
134 | 2625217.7396 | 1238537.3607 | 2625217.0322 | 1238529.3638 | 2625224.0028 | 1238515.2826
135 | 2625238.2553 | 1238492.1091 | 2625229.7192 | 1238503.7349 | 2625224.0028 | 1238515.2826
136 | 2625238.7307 | 1238491.4617 | 2625238.2553 | 1238492.1091
137 | 2625280.858 | 1238434.0863 | 2625238.7307 | 1238491.4617
138 | 2625221.0902 | 1238428.2661 | 2625201.5724 | 1238456.1415 | 2625208.2169 | 1238460.7617
139 | 2625239.7128 | 1238401.6692 | 2625221.0902 | 1238428.2661
140 | 2625280.858 | 1238434.0863 | 2625239.7128 | 1238401.6692
141 | 2625073.9527 | 1238476.6803 | 2625064.3239 | 1238471.9635
142 | 2625073.9527 | 1238476.6803 | 2625075.7285 | 1238477.5502
143 | 2625014.6385 | 1238655.4086 | 2624994.6335 | 1238642.9167
144 | 2624982.7403 | 1238636.1089 | 2624992.2705 | 1238641.4411 | 2624994.6335 | 1238642.9167
145 | 2624982.7403 | 1238636.1089 | 2624976.9035 | 1238634.7015

## bus_geodata
| x | y | coords
0 | 2625137.1193 | 1238567.4871
1 | 2625144.3116 | 1238553.486
2 | 2625135.0108 | 1238571.5917
3 | 2625146.4001 | 1238549.4205
4 | 2625124.7258 | 1238593.5244
5 | 2625147.6992 | 1238546.8915
6 | 2625116.1446 | 1238612.8003
7 | 2625148.2465 | 1238545.8261
8 | 2625113.3488 | 1238619.5831
9 | 2624906.08 | 1238415.0837
10 | 2624879.387 | 1238398.9502
11 | 2624934.3526 | 1238427.8649
12 | 2624870.8998 | 1238393.7003
13 | 2624862.2512 | 1238383.5429
14 | 2624932.3513 | 1238442.9479
15 | 2624868.2594 | 1238397.4583
16 | 2624830.066 | 1238368.3804
17 | 2624850.881 | 1238420.9468
18 | 2624840.2402 | 1238370.249
19 | 2624986.8026 | 1238439.7034
20 | 2624991.5558 | 1238440.7462
21 | 2624964.0987 | 1238415.9571
22 | 2624920.8888 | 1238462.2522
23 | 2624812.9157 | 1238356.3114
24 | 2625004.2429 | 1238417.7611
25 | 2624974.7312 | 1238466.6936
26 | 2625025.3282 | 1238452.8613
27 | 2624938.0766 | 1238400.1855
28 | 2624917.046 | 1238467.798
29 | 2624928.6018 | 1238477.2126
30 | 2625136.5787 | 1238645.6222
31 | 2625143.8705 | 1238649.4664
32 | 2625134.9016 | 1238644.738
33 | 2625142.8801 | 1238670.3825
34 | 2625108.6786 | 1238630.9135
35 | 2625163.7803 | 1238681.1943
36 | 2625124.5261 | 1238707.8677
37 | 2625100.0253 | 1238651.0376
38 | 2625126.3847 | 1238739.242
39 | 2624814.3263 | 1238283.7722
40 | 2624813.9487 | 1238284.262
41 | 2624815.0978 | 1238282.7714
42 | 2624789.5657 | 1238315.8902
43 | 2624824.9624 | 1238269.9757
44 | 2624799.4799 | 1238332.4735
45 | 2624786.6037 | 1238318.8019
46 | 2624836.4585 | 1238255.0636
47 | 2624803.0981 | 1238346.2355
48 | 2624766.6944 | 1238283.0169
49 | 2624842.115 | 1238247.7263
50 | 2624974.4767 | 1238221.8329
51 | 2624898.3316 | 1238173.7223
52 | 2624873.0606 | 1238207.5855
53 | 2624858.8015 | 1238165.1927
54 | 2624860.5351 | 1238223.8328
55 | 2624855.8204 | 1238229.9485
56 | 2624763.7188 | 1238277.6686
57 | 2624752.265 | 1238261.2141
58 | 2624742.184 | 1238247.2058
59 | 2624808.1113 | 1238352.2499
60 | 2624770.3395 | 1238210.5613
61 | 2624779.5371 | 1238549.8402
62 | 2624785.4379 | 1238553.0131
63 | 2624764.5256 | 1238541.6871
64 | 2624791.2589 | 1238556.026
65 | 2624752.067 | 1238534.5632
66 | 2624792.6771 | 1238556.7487
67 | 2624736.2033 | 1238524.8985
68 | 2624806.5613 | 1238563.8239
69 | 2624724.2128 | 1238542.0001
70 | 2624766.1992 | 1238492.503
71 | 2624790.7918 | 1238183.9425
72 | 2625161.2654 | 1238518.7545
73 | 2625172.8285 | 1238522.9416
74 | 2625129.8628 | 1238504.0682
75 | 2625183.9174 | 1238526.6798
76 | 2625101.1765 | 1238490.016
77 | 2625141.1408 | 1238480.9697
78 | 2625083.0658 | 1238714.3948
79 | 2625088.2656 | 1238722.8614
80 | 2625080.7722 | 1238700.2057
81 | 2625097.5198 | 1238730.8956
82 | 2625060.0342 | 1238706.907
83 | 2625081.3975 | 1238695.4054
84 | 2625117.0152 | 1238745.362
85 | 2625048.2677 | 1238713.8924
86 | 2625062.1283 | 1238685.4912
87 | 2625123.4984 | 1238750.1727
88 | 2625035.2353 | 1238721.6294
89 | 2625039.8098 | 1238671.1267
90 | 2625142.6026 | 1238477.9758
91 | 2625150.0301 | 1238465.8195
92 | 2625151.9542 | 1238463.3461
93 | 2625156.5793 | 1238457.4005
94 | 2625161.9831 | 1238450.4539
95 | 2625086.3932 | 1238482.7743
96 | 2625162.0272 | 1238450.3971
97 | 2625165.8182 | 1238445.5237
98 | 2624947.4581 | 1238490.6211
99 | 2624969.7311 | 1238474.405
100 | 2624904.2143 | 1238486.3164
101 | 2625029.007 | 1238454.6634
102 | 2625039.4342 | 1238459.7712
103 | 2625041.0206 | 1238460.5483
104 | 2625032.2038 | 1238375.3266
105 | 2625057.7559 | 1238468.7462
106 | 2625034.9147 | 1238371.2124
107 | 2624880.1331 | 1238631.4867
108 | 2624878.4077 | 1238633.9133
109 | 2624895.8802 | 1238609.3393
110 | 2624873.0046 | 1238641.5125
111 | 2624880.1759 | 1238601.3366
112 | 2624905.2117 | 1238595.8108
113 | 2624857.3515 | 1238663.5276
114 | 2624859.8567 | 1238590.9823
115 | 2624950.805 | 1238607.2542
116 | 2624839.9445 | 1238580.8354
117 | 2624964.4998 | 1238631.8964
118 | 2624822.5157 | 1238571.954
119 | 2624814.4022 | 1238567.8195
120 | 2624849.004 | 1238238.7903
121 | 2625079.2764 | 1238479.2881
122 | 2625132.5335 | 1238759.828
123 | 2625117.1854 | 1238786.4443
124 | 2624924.7351 | 1238380.7889
125 | 2624929.3078 | 1238373.6878
126 | 2625028.5726 | 1238664.1097
127 | 2624785.9178 | 1238480.1099
128 | 2624772.7639 | 1238487.0731
129 | 2625211.8007 | 1238535.5712
130 | 2625196.7996 | 1238530.9591
131 | 2625217.7395 | 1238537.3607
132 | 2625224.0028 | 1238515.2826
133 | 2625238.2553 | 1238492.1091
134 | 2625238.7307 | 1238491.4617
135 | 2625208.2169 | 1238460.7617
136 | 2625221.0902 | 1238428.2661
137 | 2625239.7128 | 1238401.6692
138 | 2625280.858 | 1238434.0863
139 | 2625064.3239 | 1238471.9635
140 | 2625073.9527 | 1238476.6803
141 | 2625075.7285 | 1238477.5502
142 | 2625014.6385 | 1238655.4086
143 | 2624994.6335 | 1238642.9167
144 | 2624982.7403 | 1238636.1089
145 | 2624976.9035 | 1238634.7015
146 | 2624881.4609 | 1238487.2028
147 | 2624991.5558 | 1238440.7462

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98876 | -0.078218 | 0.00060656 | 0.00015202
1 | 0.9896 | -0.072346 | 0.00049207 | 0.00012332
2 | 0.98852 | -0.079932 | 0.0018305 | 0.00045876
3 | 0.98984 | -0.070635 | 0.0044192 | 0.0011075
4 | 0.98726 | -0.088794 | 0.0038072 | 0.00095416
5 | 0.99 | -0.069529 | 0.001377 | 0.0003451
6 | 0.9862 | -0.096253 | 0 | 0
7 | 0.99007 | -0.069057 | 0.00099538 | 0.00024947
8 | 0.98583 | -0.09885 | 0.0014707 | 0.00036858
9 | 0.98315 | -0.11782 | 0.00034435 | 8.6302e-05
10 | 0.98175 | -0.12777 | 0 | 0
11 | 0.98457 | -0.1078 | 0 | 0
12 | 0.98132 | -0.13082 | 0 | 0
13 | 0.98171 | -0.1281 | 0.00078405 | 0.0001965
14 | 0.98528 | -0.10277 | 0.0023743 | 0.00059506
15 | 0.98131 | -0.13091 | 0 | 0
16 | 0.97937 | -0.14473 | 0.0023149 | 0.00058018
17 | 0.98124 | -0.13144 | 0.0017571 | 0.00044037
18 | 0.98169 | -0.12821 | 0.00041566 | 0.00010417
19 | 0.99398 | -0.041718 | 0 | 0
20 | 0.99401 | -0.041523 | 0 | 0
21 | 0.99379 | -0.043109 | 0.0021497 | 0.00053876
22 | 0.98638 | -0.095014 | 0 | 0
23 | 0.97859 | -0.15032 | 0.0002013 | 5.045e-05
24 | 0.99392 | -0.042168 | 0.0015535 | 0.00038935
25 | 0.99184 | -0.056696 | 0.0017523 | 0.00043916
26 | 0.99687 | -0.021645 | 0.00036961 | 9.2633e-05
27 | 0.99371 | -0.043674 | 0 | 0
28 | 0.98628 | -0.095738 | 0.0055618 | 0.0013939
29 | 0.98746 | -0.08742 | 0.00035133 | 8.8052e-05
30 | 0.98373 | -0.11375 | 0.0028258 | 0.00070822
31 | 0.9834 | -0.11607 | 0.0028548 | 0.00071549
32 | 0.9838 | -0.1132 | 0.014236 | 0.0035678
33 | 0.98235 | -0.1235 | 0 | 0
34 | 0.98523 | -0.10313 | 0 | 0
35 | 0.982 | -0.12603 | 0.0104 | 0.0026064
36 | 0.98096 | -0.13339 | 0.0046186 | 0.0011575
37 | 0.98513 | -0.10381 | 0.0030056 | 0.00075328
38 | 0.97966 | -0.14262 | 0.0046261 | 0.0011594
39 | 0.97593 | -0.16938 | 0.00098111 | 0.00024589
40 | 0.97594 | -0.16929 | 0.0020238 | 0.0005072
41 | 0.9759 | -0.16955 | 0.00064783 | 0.00016236
42 | 0.97687 | -0.16261 | 0 | 0
43 | 0.97561 | -0.17164 | 0.00079893 | 0.00020023
44 | 0.97684 | -0.16284 | 0.0011339 | 0.00028419
45 | 0.97698 | -0.16187 | 0 | 0
46 | 0.9753 | -0.17391 | 0.0013986 | 0.00035053
47 | 0.97807 | -0.15404 | 0.0017586 | 0.00044074
48 | 0.9766 | -0.16454 | 0.000472 | 0.00011829
49 | 0.97516 | -0.17489 | 0.00086451 | 0.00021667
50 | 0.97378 | -0.18483 | 0.0039763 | 0.00099657
51 | 0.9743 | -0.18105 | 0 | 0
52 | 0.97462 | -0.17876 | 0.00072786 | 0.00018242
53 | 0.97423 | -0.18156 | 0.0011785 | 0.00029536
54 | 0.9748 | -0.17749 | 0.00092399 | 0.00023157
55 | 0.97488 | -0.17693 | 0.0012211 | 0.00030603
56 | 0.97655 | -0.16491 | 0.00057914 | 0.00014515
57 | 0.9764 | -0.16601 | 0.00084085 | 0.00021074
58 | 0.97629 | -0.16679 | 0 | 0
59 | 0.97836 | -0.15198 | 0.00022262 | 5.5795e-05
60 | 0.976 | -0.1689 | 0.0031227 | 0.00078261
61 | 0.97187 | -0.1985 | 0.00061873 | 0.00015507
62 | 0.97199 | -0.19762 | 0.0013762 | 0.00034492
63 | 0.97158 | -0.20062 | 0.0015129 | 0.00037918
64 | 0.97213 | -0.19667 | 0.00078017 | 0.00019553
65 | 0.97136 | -0.20218 | 0.0013227 | 0.00033151
66 | 0.97216 | -0.19642 | 0.0013787 | 0.00034554
67 | 0.97112 | -0.20394 | 0 | 0
68 | 0.97234 | -0.19511 | 0.00077022 | 0.00019303
69 | 0.97098 | -0.20496 | 0.0046087 | 0.001155
70 | 0.97084 | -0.20596 | 0.0015561 | 0.00039
71 | 0.97594 | -0.16933 | 0.0012225 | 0.00030639
72 | 0.99177 | -0.057146 | 0 | 0
73 | 0.9914 | -0.059741 | 0.0010449 | 0.00026187
74 | 0.99408 | -0.041063 | 0 | 0
75 | 0.99107 | -0.062088 | 0.0015518 | 0.00038891
76 | 0.99635 | -0.02526 | 0.006217 | 0.0015581
77 | 0.99373 | -0.04352 | 0.0023288 | 0.00058366
78 | 0.9779 | -0.15524 | 0.0016918 | 0.000424
79 | 0.97813 | -0.15353 | 0.00098866 | 0.00024778
80 | 0.97756 | -0.15761 | 0 | 0
81 | 0.97843 | -0.1514 | 0.0024733 | 0.00061986
82 | 0.97737 | -0.15898 | 0.0010126 | 0.00025379
83 | 0.97747 | -0.15831 | 0 | 0
84 | 0.97905 | -0.147 | 0.0027654 | 0.00069308
85 | 0.97728 | -0.15968 | 0.0038674 | 0.00096927
86 | 0.97703 | -0.16143 | 0.0029578 | 0.00074129
87 | 0.97927 | -0.14546 | 0 | 0
88 | 0.97725 | -0.15983 | 0.00098891 | 0.00024784
89 | 0.97654 | -0.16497 | 0.0016364 | 0.00041012
90 | 0.99369 | -0.04376 | 0.0028166 | 0.00070591
91 | 0.9936 | -0.044385 | 0.00048513 | 0.00012159
92 | 0.99359 | -0.044506 | 0.00024333 | 6.0983e-05
93 | 0.99355 | -0.044779 | 0.00068362 | 0.00017133
94 | 0.99351 | -0.045037 | 0.0008165 | 0.00020463
95 | 0.99757 | -0.016802 | 0.0010263 | 0.00025722
96 | 0.99351 | -0.045038 | 0.0015661 | 0.00039249
97 | 0.99351 | -0.045071 | 0.00051561 | 0.00012922
98 | 0.98918 | -0.07529 | 0.00059431 | 0.00014895
99 | 0.99121 | -0.061054 | 0.0017311 | 0.00043386
100 | 0.98612 | -0.096871 | 0.003288 | 0.00082404
101 | 0.9972 | -0.019373 | 0.0040497 | 0.001015
102 | 0.9982 | -0.012468 | 0.0010629 | 0.00026638
103 | 0.99835 | -0.0114 | 0.00081862 | 0.00020516
104 | 0.99386 | -0.042613 | 0.00039234 | 9.833e-05
105 | 1 | 0 | -0.22584 | -0.056837
106 | 0.99385 | -0.042636 | 0.00047129 | 0.00011812
107 | 0.97315 | -0.18928 | 0.0011172 | 0.00028
108 | 0.97313 | -0.18943 | 0.0022678 | 0.00056837
109 | 0.97339 | -0.18757 | 0 | 0
110 | 0.9731 | -0.18968 | 0.00055679 | 0.00013955
111 | 0.97317 | -0.18912 | 0.0022576 | 0.00056581
112 | 0.97364 | -0.18578 | 0.00044512 | 0.00011156
113 | 0.97302 | -0.19026 | 0.0020162 | 0.0005053
114 | 0.97292 | -0.19094 | 0.0014876 | 0.00037284
115 | 0.97466 | -0.1784 | 0.00057299 | 0.0001436
116 | 0.97269 | -0.1926 | 0.0010027 | 0.00025131
117 | 0.97511 | -0.17519 | 0 | 0
118 | 0.9725 | -0.19399 | 0.0014632 | 0.00036671
119 | 0.97241 | -0.19459 | 0.0020366 | 0.00051041
120 | 0.97501 | -0.17599 | 0.001205 | 0.00030201
121 | 0.99816 | -0.01271 | 0.0033612 | 0.0008424
122 | 0.97918 | -0.14607 | 0 | 0
123 | 0.97898 | -0.14748 | 0.0043533 | 0.001091
124 | 0.99365 | -0.044101 | 0.0013865 | 0.00034748
125 | 0.99368 | -0.043848 | 0.00044116 | 0.00011056
126 | 0.9763 | -0.16666 | 0.0011089 | 0.00027792
127 | 0.97077 | -0.20645 | 0.0015402 | 0.00038601
128 | 0.9708 | -0.20621 | 0.0012215 | 0.00030613
129 | 0.99033 | -0.067319 | 0.00132 | 0.00033082
130 | 0.99072 | -0.064598 | 0.0011513 | 0.00028855
131 | 0.99019 | -0.068311 | 0 | 0
132 | 0.98965 | -0.072111 | 0.0030484 | 0.000764
133 | 0.98916 | -0.075637 | 0.0088284 | 0.0022126
134 | 0.98915 | -0.075669 | 0.002915 | 0.00073058
135 | 0.98893 | -0.077279 | 0.00036356 | 9.1117e-05
136 | 0.98895 | -0.077122 | 0.00053855 | 0.00013497
137 | 0.98899 | -0.076822 | 0 | 0
138 | 0.98906 | -0.076335 | 0 | 0
139 | 0.99943 | -0.0039094 | 0.0018471 | 0.00046294
140 | 0.99861 | -0.0095825 | 0.00026969 | 6.759e-05
141 | 0.99846 | -0.010628 | 0.00055894 | 0.00014008
142 | 0.97602 | -0.16869 | 0.0013055 | 0.0003272
143 | 0.97562 | -0.17151 | 0.0014095 | 0.00035325
144 | 0.97541 | -0.17308 | 0 | 0
145 | 0.97531 | -0.17377 | 0.00074698 | 0.00018721
146 | 0.98603 | -0.097531 | 0.0016065 | 0.00040262
147 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.1106 | -0.027836 | 0.11069 | 0.02787 | 9.0742e-05 | 3.4294e-05 | 0.16648 | 0.16648 | 0.16648 | 0.98876 | -0.078218 | 0.9896 | -0.072346 | 20.5532
1 | 0.10999 | 0.027684 | -0.10996 | -0.027674 | 2.6311e-05 | 9.9421e-06 | 0.16557 | 0.16557 | 0.16557 | 0.98876 | -0.078218 | 0.98852 | -0.079932 | 20.4405
2 | -0.11118 | -0.027993 | 0.11121 | 0.028003 | 2.6583e-05 | 1.0048e-05 | 0.16722 | 0.16722 | 0.16722 | 0.9896 | -0.072346 | 0.98984 | -0.070635 | 20.6445
3 | 0.10813 | 0.027215 | -0.108 | -0.027164 | 0.00013361 | 5.0459e-05 | 0.16281 | 0.16281 | 0.16281 | 0.98852 | -0.079932 | 0.98726 | -0.088794 | 20.1004
4 | -0.11562 | -0.029111 | 0.11564 | 0.029118 | 1.7877e-05 | 6.7661e-06 | 0.17386 | 0.17386 | 0.17386 | 0.98984 | -0.070635 | 0.99 | -0.069529 | 21.4646
5 | 0.10419 | 0.02621 | -0.10408 | -0.026169 | 0.00010828 | 4.0838e-05 | 0.15707 | 0.15707 | 0.15707 | 0.98726 | -0.088794 | 0.9862 | -0.096253 | 19.392
6 | -0.11702 | -0.029463 | 0.11703 | 0.029466 | 7.7108e-06 | 2.9195e-06 | 0.17593 | 0.17593 | 0.17593 | 0.99 | -0.069529 | 0.99007 | -0.069057 | 21.7201
7 | 0.10408 | 0.026169 | -0.10405 | -0.026155 | 3.7649e-05 | 1.42e-05 | 0.15707 | 0.15708 | 0.15708 | 0.9862 | -0.096253 | 0.98583 | -0.09885 | 19.392
8 | -0.11802 | -0.029715 | 0.11822 | 0.02979 | 0.00019674 | 7.4509e-05 | 0.17743 | 0.17743 | 0.17743 | 0.99007 | -0.069057 | 0.99177 | -0.057146 | 21.9048
9 | 0.10258 | 0.025787 | -0.10251 | -0.025764 | 6.1127e-05 | 2.3042e-05 | 0.15486 | 0.15486 | 0.15486 | 0.98583 | -0.09885 | 0.98523 | -0.10313 | 19.1179
10 | 0.030979 | 0.0077825 | -0.030936 | -0.0077664 | 4.2812e-05 | 1.6071e-05 | 0.046894 | 0.046894 | 0.046894 | 0.98315 | -0.11782 | 0.98175 | -0.12777 | 17.3682
11 | -0.031324 | -0.0078688 | 0.031367 | 0.0078852 | 4.3682e-05 | 1.6405e-05 | 0.047415 | 0.047415 | 0.047415 | 0.98315 | -0.11782 | 0.98457 | -0.1078 | 17.5612
12 | 0.029737 | 0.0074664 | -0.029724 | -0.0074617 | 1.2627e-05 | 4.7306e-06 | 0.045076 | 0.045076 | 0.045076 | 0.98175 | -0.12777 | 0.98132 | -0.13082 | 16.6948
13 | 0.0011998 | 0.00030003 | -0.0011997 | -0.00030035 | 5.5504e-08 | -3.1884e-07 | 0.0018182 | 0.0018183 | 0.0018183 | 0.98175 | -0.12777 | 0.98171 | -0.1281 | 0.67346
14 | -0.031367 | -0.0078852 | 0.031389 | 0.0078935 | 2.2014e-05 | 8.2672e-06 | 0.047415 | 0.047415 | 0.047415 | 0.98457 | -0.1078 | 0.98528 | -0.10277 | 17.5611
15 | 0.0017573 | 0.00044 | -0.0017572 | -0.00044005 | 2.0329e-08 | -5.0157e-08 | 0.0026645 | 0.0026645 | 0.0026645 | 0.98132 | -0.13082 | 0.98131 | -0.13091 | 0.98684
16 | 0.027967 | 0.0070217 | -0.027913 | -0.0070015 | 5.3929e-05 | 2.0136e-05 | 0.042412 | 0.042412 | 0.042412 | 0.98132 | -0.13082 | 0.97937 | -0.14473 | 15.7081
17 | 0.00041567 | 0.00010385 | -0.00041566 | -0.00010417 | 6.3683e-09 | -3.2267e-07 | 0.00062993 | 0.00063005 | 0.00063005 | 0.98171 | -0.1281 | 0.98169 | -0.12821 | 0.23335
18 | -0.033764 | -0.0084885 | 0.0338 | 0.0085023 | 3.6516e-05 | 1.3758e-05 | 0.051001 | 0.051001 | 0.051001 | 0.98528 | -0.10277 | 0.98638 | -0.095014 | 18.8892
19 | 0.0017572 | 0.00044005 | -0.0017571 | -0.00044037 | 1.2945e-07 | -3.1932e-07 | 0.0026645 | 0.0026646 | 0.0026646 | 0.98131 | -0.13091 | 0.98124 | -0.13144 | 0.98689
20 | 0.025598 | 0.0064214 | -0.025578 | -0.006414 | 1.9827e-05 | 7.3615e-06 | 0.038895 | 0.038895 | 0.038895 | 0.97937 | -0.14473 | 0.97859 | -0.15032 | 14.4054
21 | -0.0039783 | -0.00099545 | 0.0039784 | 0.00099543 | 1.0739e-07 | -2.1602e-08 | 0.0059551 | 0.005955 | 0.0059551 | 0.99398 | -0.041718 | 0.99401 | -0.041523 | 2.2056
22 | 0.0039783 | 0.00099545 | -0.0039775 | -0.00099561 | 7.6369e-07 | -1.5351e-07 | 0.0059551 | 0.0059552 | 0.0059552 | 0.99398 | -0.041718 | 0.99379 | -0.043109 | 2.2056
23 | 0.0024175 | 0.00060484 | -0.0024172 | -0.0006051 | 2.1523e-07 | -2.5864e-07 | 0.0036185 | 0.0036186 | 0.0036186 | 0.99401 | -0.041523 | 0.99392 | -0.042168 | 1.3402
24 | 0.049033 | 0.012364 | -0.048929 | -0.012325 | 0.00010404 | 3.9616e-05 | 0.073428 | 0.073428 | 0.073428 | 0.99401 | -0.041523 | 0.99184 | -0.056696 | 27.1955
25 | -0.055429 | -0.013964 | 0.055583 | 0.014023 | 0.00015457 | 5.8982e-05 | 0.083001 | 0.083001 | 0.083001 | 0.99401 | -0.041523 | 0.99687 | -0.021645 | 30.7412
26 | 0.0018279 | 0.00045685 | -0.0018277 | -0.00045719 | 1.4219e-07 | -3.3955e-07 | 0.0027365 | 0.0027366 | 0.0027366 | 0.99379 | -0.043109 | 0.99371 | -0.043674 | 1.0136
27 | 0.010458 | 0.0026204 | -0.010457 | -0.0026201 | 1.0479e-06 | 3.1694e-07 | 0.015777 | 0.015777 | 0.015777 | 0.98638 | -0.095014 | 0.98628 | -0.095738 | 5.8432
28 | -0.044258 | -0.011123 | 0.044305 | 0.011141 | 4.6835e-05 | 1.7798e-05 | 0.066777 | 0.066777 | 0.066777 | 0.98638 | -0.095014 | 0.98746 | -0.08742 | 24.7323
29 | 0.025377 | 0.0063635 | -0.025371 | -0.0063614 | 5.8456e-06 | 2.1693e-06 | 0.038589 | 0.038589 | 0.038589 | 0.97859 | -0.15032 | 0.97836 | -0.15198 | 14.2921
30 | 0.00086369 | 0.00021575 | -0.00086364 | -0.00021638 | 5.3008e-08 | -6.3819e-07 | 0.0012928 | 0.001293 | 0.001293 | 0.99392 | -0.042168 | 0.99386 | -0.042613 | 0.4789
31 | 0.047177 | 0.011885 | -0.047148 | -0.011874 | 2.8746e-05 | 1.0938e-05 | 0.070799 | 0.070799 | 0.070799 | 0.99184 | -0.056696 | 0.99121 | -0.061054 | 26.2219
32 | -0.055953 | -0.014116 | 0.055971 | 0.014123 | 1.7845e-05 | 6.81e-06 | 0.083553 | 0.083553 | 0.083553 | 0.99687 | -0.021645 | 0.9972 | -0.019373 | 30.9455
33 | 0.00044117 | 0.00011006 | -0.00044116 | -0.00011056 | 1.0592e-08 | -4.9992e-07 | 0.00066044 | 0.00066062 | 0.00066062 | 0.99371 | -0.043674 | 0.99368 | -0.043848 | 0.24467
34 | 0.0013866 | 0.00034712 | -0.0013865 | -0.00034748 | 8.1932e-08 | -3.6305e-07 | 0.0020762 | 0.0020763 | 0.0020763 | 0.99371 | -0.043674 | 0.99365 | -0.044101 | 0.769
35 | 0.0048953 | 0.0012262 | -0.0048946 | -0.0012262 | 7.6683e-07 | 7.4642e-09 | 0.0073855 | 0.0073856 | 0.0073856 | 0.98628 | -0.095738 | 0.98612 | -0.096871 | 2.7354
36 | -0.044656 | -0.011229 | 0.044732 | 0.011257 | 7.561e-05 | 2.8738e-05 | 0.067307 | 0.067307 | 0.067307 | 0.98746 | -0.08742 | 0.98918 | -0.07529 | 24.9284
37 | 0.082301 | 0.020679 | -0.082274 | -0.02067 | 2.658e-05 | 9.9094e-06 | 0.12451 | 0.12451 | 0.12451 | 0.98373 | -0.11375 | 0.9834 | -0.11607 | 15.3716
38 | -0.085126 | -0.021388 | 0.085133 | 0.02139 | 6.5403e-06 | 2.4433e-06 | 0.12878 | 0.12878 | 0.12878 | 0.98373 | -0.11375 | 0.9838 | -0.1132 | 15.8993
39 | 0.079419 | 0.019954 | -0.079337 | -0.019924 | 8.1968e-05 | 3.0489e-05 | 0.12019 | 0.12019 | 0.12019 | 0.9834 | -0.11607 | 0.98235 | -0.1235 | 14.8383
40 | -0.099369 | -0.024958 | 0.099508 | 0.02501 | 0.00013932 | 5.2453e-05 | 0.15032 | 0.15032 | 0.15032 | 0.9838 | -0.1132 | 0.98523 | -0.10313 | 18.5575
41 | 0.010403 | 0.0026075 | -0.0104 | -0.0026064 | 3.6463e-06 | 1.1046e-06 | 0.015758 | 0.015759 | 0.015759 | 0.98235 | -0.1235 | 0.982 | -0.12603 | 5.8365
42 | 0.068934 | 0.017316 | -0.068839 | -0.017281 | 9.468e-05 | 3.4832e-05 | 0.10443 | 0.10443 | 0.10443 | 0.98235 | -0.1235 | 0.98096 | -0.13339 | 12.8929
43 | 0.0030059 | 0.00075311 | -0.0030056 | -0.00075328 | 2.8173e-07 | -1.7057e-07 | 0.0045398 | 0.0045399 | 0.0045399 | 0.98523 | -0.10313 | 0.98513 | -0.10381 | 1.6815
44 | 0.064221 | 0.016124 | -0.064139 | -0.016094 | 8.2214e-05 | 3.0046e-05 | 0.097427 | 0.097427 | 0.097427 | 0.98096 | -0.13339 | 0.97966 | -0.14262 | 12.028
45 | 0.059512 | 0.014934 | -0.059489 | -0.014926 | 2.3476e-05 | 8.5078e-06 | 0.0904 | 0.090401 | 0.090401 | 0.97966 | -0.14262 | 0.97927 | -0.14546 | 11.1606
46 | -0.01394 | -0.0034927 | 0.013941 | 0.0034927 | 1.7436e-07 | 5.9332e-08 | 0.021255 | 0.021255 | 0.021255 | 0.97593 | -0.16938 | 0.97594 | -0.16929 | 7.8722
47 | 0.012959 | 0.0032468 | -0.012959 | -0.0032467 | 3.0784e-07 | 1.0261e-07 | 0.019759 | 0.019759 | 0.019759 | 0.97593 | -0.16938 | 0.9759 | -0.16955 | 7.3181
48 | -0.015964 | -0.0039999 | 0.015979 | 0.0040051 | 1.4764e-05 | 5.179e-06 | 0.024341 | 0.02434 | 0.024341 | 0.97594 | -0.16929 | 0.97687 | -0.16261 | 9.015
49 | 0.012311 | 0.0030843 | -0.012308 | -0.0030832 | 3.5524e-06 | 1.1645e-06 | 0.018771 | 0.018771 | 0.018771 | 0.9759 | -0.16955 | 0.97561 | -0.17164 | 6.9523
50 | 0.001134 | 0.00028396 | -0.0011339 | -0.00028419 | 3.5969e-08 | -2.2804e-07 | 0.0017272 | 0.0017273 | 0.0017273 | 0.97687 | -0.16261 | 0.97684 | -0.16284 | 0.63974
51 | -0.017113 | -0.0042891 | 0.017115 | 0.0042897 | 1.7588e-06 | 6.2454e-07 | 0.026068 | 0.026068 | 0.026068 | 0.97687 | -0.16261 | 0.97698 | -0.16187 | 9.6547
52 | 0.011509 | 0.0028829 | -0.011505 | -0.0028818 | 3.62e-06 | 1.1572e-06 | 0.017553 | 0.017553 | 0.017553 | 0.97561 | -0.17164 | 0.9753 | -0.17391 | 6.501
53 | -0.023357 | -0.0058528 | 0.023383 | 0.0058622 | 2.5328e-05 | 9.3396e-06 | 0.035575 | 0.035575 | 0.035575 | 0.97698 | -0.16187 | 0.97807 | -0.15404 | 13.1758
54 | 0.0062424 | 0.0015631 | -0.0062401 | -0.0015628 | 2.3097e-06 | 3.7575e-07 | 0.0095072 | 0.0095074 | 0.0095074 | 0.97698 | -0.16187 | 0.9766 | -0.16454 | 3.5212
55 | 0.010106 | 0.0025312 | -0.010105 | -0.0025308 | 1.3744e-06 | 4.1302e-07 | 0.015419 | 0.015419 | 0.015419 | 0.9753 | -0.17391 | 0.97516 | -0.17489 | 5.7107
56 | -0.025141 | -0.0063029 | 0.025148 | 0.0063056 | 7.1701e-06 | 2.6591e-06 | 0.03825 | 0.03825 | 0.03825 | 0.97807 | -0.15404 | 0.97836 | -0.15198 | 14.1667
57 | 0.0057681 | 0.0014445 | -0.0057678 | -0.0014444 | 2.9496e-07 | 3.6869e-08 | 0.0087882 | 0.0087882 | 0.0087882 | 0.9766 | -0.16454 | 0.97655 | -0.16491 | 3.2549
58 | 0.0092406 | 0.0023142 | -0.0092392 | -0.0023138 | 1.3997e-06 | 3.9761e-07 | 0.0141 | 0.0141 | 0.0141 | 0.97516 | -0.17489 | 0.97501 | -0.17599 | 5.2221
59 | -0.0039763 | -0.00099657 | 0.0039784 | 0.00099624 | 2.0749e-06 | -3.2307e-07 | 0.0060762 | 0.0060758 | 0.0060762 | 0.97378 | -0.18483 | 0.9743 | -0.18105 | 2.2504
60 | -0.005157 | -0.0012911 | 0.0051586 | 0.0012912 | 1.6355e-06 | 1.026e-07 | 0.0078756 | 0.0078754 | 0.0078756 | 0.9743 | -0.18105 | 0.97462 | -0.17876 | 2.9169
61 | 0.0011786 | 0.00029488 | -0.0011785 | -0.00029536 | 8.2164e-08 | -4.7454e-07 | 0.0017998 | 0.0018 | 0.0018 | 0.9743 | -0.18105 | 0.97423 | -0.18156 | 0.66666
62 | -0.0058865 | -0.0014736 | 0.0058875 | 0.0014738 | 1.0338e-06 | 1.4192e-07 | 0.0089867 | 0.0089866 | 0.0089867 | 0.97462 | -0.17876 | 0.9748 | -0.17749 | 3.3284
63 | -0.0068115 | -0.0017054 | 0.006812 | 0.0017055 | 5.2088e-07 | 1.0406e-07 | 0.010397 | 0.010397 | 0.010397 | 0.9748 | -0.17749 | 0.97488 | -0.17693 | 3.8508
64 | -0.0080331 | -0.0020115 | 0.0080341 | 0.0020118 | 1.0472e-06 | 2.6357e-07 | 0.012261 | 0.012261 | 0.012261 | 0.97488 | -0.17693 | 0.97501 | -0.17599 | 4.541
65 | 0.0051886 | 0.0012993 | -0.0051879 | -0.0012992 | 7.8253e-07 | 4.9983e-08 | 0.0079058 | 0.0079059 | 0.0079059 | 0.97655 | -0.16491 | 0.9764 | -0.16601 | 2.9281
66 | 0.004347 | 0.0010885 | -0.0043465 | -0.0010885 | 4.726e-07 | -3.4068e-08 | 0.0066244 | 0.0066245 | 0.0066245 | 0.9764 | -0.16601 | 0.97629 | -0.16679 | 2.4535
67 | 0.0043465 | 0.0010885 | -0.0043453 | -0.0010886 | 1.2655e-06 | -9.0961e-08 | 0.0066245 | 0.0066247 | 0.0066247 | 0.97629 | -0.16679 | 0.976 | -0.1689 | 2.4536
68 | 0.0012226 | 0.000306 | -0.0012225 | -0.00030639 | 7.2773e-08 | -3.9149e-07 | 0.0018638 | 0.001864 | 0.001864 | 0.976 | -0.1689 | 0.97594 | -0.16933 | 0.69037
69 | -0.012391 | -0.003105 | 0.012392 | 0.0031055 | 1.5046e-06 | 4.9568e-07 | 0.018971 | 0.018971 | 0.018971 | 0.97187 | -0.1985 | 0.97199 | -0.19762 | 7.0263
70 | 0.011772 | 0.0029499 | -0.011769 | -0.0029488 | 3.463e-06 | 1.1203e-06 | 0.018024 | 0.018024 | 0.018024 | 0.97187 | -0.1985 | 0.97158 | -0.20062 | 6.6755
71 | -0.013768 | -0.0034504 | 0.01377 | 0.003451 | 1.8172e-06 | 6.1766e-07 | 0.021078 | 0.021078 | 0.021078 | 0.97199 | -0.19762 | 0.97213 | -0.19667 | 7.8067
72 | 0.010256 | 0.0025696 | -0.010253 | -0.002569 | 2.2094e-06 | 6.7207e-07 | 0.015707 | 0.015707 | 0.015707 | 0.97158 | -0.20062 | 0.97136 | -0.20218 | 5.8173
73 | -0.01455 | -0.0036466 | 0.014551 | 0.0036467 | 4.927e-07 | 1.6976e-07 | 0.022272 | 0.022272 | 0.022272 | 0.97213 | -0.19667 | 0.97216 | -0.19642 | 8.2489
74 | 0.0089306 | 0.0022375 | -0.0089285 | -0.0022369 | 2.1708e-06 | 6.049e-07 | 0.01368 | 0.013681 | 0.013681 | 0.97136 | -0.20218 | 0.97112 | -0.20394 | 5.0669
75 | -0.01593 | -0.0039923 | 0.015933 | 0.003993 | 2.8904e-06 | 7.2519e-07 | 0.024382 | 0.024382 | 0.024382 | 0.97216 | -0.19642 | 0.97234 | -0.19511 | 4.5153
76 | 0.0046094 | 0.001155 | -0.0046087 | -0.001155 | 6.5012e-07 | -8.3278e-09 | 0.0070627 | 0.0070628 | 0.0070628 | 0.97112 | -0.20394 | 0.97098 | -0.20496 | 2.6159
77 | 0.0043191 | 0.0010818 | -0.0043179 | -0.0010819 | 1.2072e-06 | -8.2053e-08 | 0.0066178 | 0.006618 | 0.006618 | 0.97112 | -0.20394 | 0.97084 | -0.20596 | 2.4511
78 | -0.016703 | -0.0041861 | 0.016704 | 0.0041862 | 1.196e-06 | 1.3249e-07 | 0.025561 | 0.025561 | 0.025561 | 0.97234 | -0.19511 | 0.97241 | -0.19459 | 3.1557
79 | 0.0027618 | 0.00069191 | -0.0027617 | -0.00069197 | 9.55e-08 | -6.888e-08 | 0.004233 | 0.004233 | 0.004233 | 0.97084 | -0.20596 | 0.9708 | -0.20621 | 1.5678
80 | 0.020805 | 0.0052161 | -0.020798 | -0.0052134 | 7.4778e-06 | 2.7174e-06 | 0.031216 | 0.031216 | 0.031216 | 0.99177 | -0.057146 | 0.9914 | -0.059741 | 11.5616
81 | -0.13902 | -0.035006 | 0.13934 | 0.035125 | 0.00031315 | 0.0001191 | 0.20864 | 0.20864 | 0.20864 | 0.99177 | -0.057146 | 0.99408 | -0.041063 | 25.7586
82 | 0.019753 | 0.0049516 | -0.019747 | -0.0049492 | 6.4189e-06 | 2.3179e-06 | 0.029648 | 0.029648 | 0.029648 | 0.9914 | -0.059741 | 0.99107 | -0.062088 | 10.9807
83 | -0.1488 | -0.037495 | 0.14913 | 0.037621 | 0.00032983 | 0.00012561 | 0.2228 | 0.2228 | 0.2228 | 0.99408 | -0.041063 | 0.99635 | -0.02526 | 27.5067
84 | 0.0094598 | 0.0023705 | -0.0094566 | -0.0023696 | 3.2162e-06 | 9.0385e-07 | 0.01416 | 0.01416 | 0.01416 | 0.99408 | -0.041063 | 0.99373 | -0.04352 | 5.2445
85 | 0.018195 | 0.0045603 | -0.018188 | -0.0045581 | 6.3213e-06 | 2.2564e-06 | 0.027318 | 0.027318 | 0.027318 | 0.99107 | -0.062088 | 0.99072 | -0.064598 | 10.1178
86 | -0.15534 | -0.039179 | 0.15553 | 0.039249 | 0.00018444 | 7.0293e-05 | 0.23209 | 0.23209 | 0.23209 | 0.99635 | -0.02526 | 0.99757 | -0.016802 | 28.6529
87 | 0.0071278 | 0.0017859 | -0.0071275 | -0.0017859 | 2.3683e-07 | 4.7926e-08 | 0.010673 | 0.010673 | 0.010673 | 0.99373 | -0.04352 | 0.99369 | -0.04376 | 3.953
88 | -0.048837 | -0.012249 | 0.048849 | 0.012253 | 1.153e-05 | 4.0569e-06 | 0.074316 | 0.074316 | 0.074316 | 0.9779 | -0.15524 | 0.97813 | -0.15353 | 9.1748
89 | 0.047145 | 0.011825 | -0.04713 | -0.01182 | 1.5521e-05 | 5.4243e-06 | 0.071742 | 0.071742 | 0.071742 | 0.9779 | -0.15524 | 0.97756 | -0.15761 | 8.8571
90 | -0.049837 | -0.012501 | 0.049852 | 0.012506 | 1.4728e-05 | 5.2007e-06 | 0.07582 | 0.07582 | 0.07582 | 0.97813 | -0.15353 | 0.97843 | -0.1514 | 9.3605
91 | 0.0058706 | 0.0014709 | -0.0058695 | -0.0014707 | 1.1122e-06 | 1.4798e-07 | 0.0089358 | 0.0089359 | 0.0089359 | 0.97756 | -0.15761 | 0.97737 | -0.15898 | 3.3096
92 | 0.041259 | 0.010349 | -0.041255 | -0.010348 | 3.972e-06 | 1.3456e-06 | 0.062806 | 0.062806 | 0.062806 | 0.97756 | -0.15761 | 0.97747 | -0.15831 | 7.7539
93 | -0.052325 | -0.013126 | 0.052357 | 0.013138 | 3.1979e-05 | 1.1384e-05 | 0.079581 | 0.079581 | 0.079581 | 0.97843 | -0.1514 | 0.97905 | -0.147 | 9.8249
94 | 0.0048568 | 0.0012169 | -0.0048564 | -0.0012169 | 4.6686e-07 | 8.0873e-09 | 0.0073942 | 0.0073943 | 0.0073943 | 0.97737 | -0.15898 | 0.97728 | -0.15968 | 2.7386
95 | 0.041255 | 0.010348 | -0.041237 | -0.010342 | 1.7863e-05 | 6.052e-06 | 0.062806 | 0.062807 | 0.062807 | 0.97747 | -0.15831 | 0.97703 | -0.16143 | 7.7539
96 | -0.055123 | -0.013831 | 0.055134 | 0.013835 | 1.1788e-05 | 4.2291e-06 | 0.083784 | 0.083784 | 0.083784 | 0.97905 | -0.147 | 0.97927 | -0.14546 | 10.3437
97 | 0.00098893 | 0.00024766 | -0.00098891 | -0.00024784 | 2.1442e-08 | -1.8165e-07 | 0.0015057 | 0.0015058 | 0.0015058 | 0.97728 | -0.15968 | 0.97725 | -0.15983 | 0.55769
98 | 0.03828 | 0.0096002 | -0.038261 | -0.009594 | 1.8766e-05 | 6.2209e-06 | 0.058302 | 0.058302 | 0.058302 | 0.97703 | -0.16143 | 0.97654 | -0.16497 | 7.1978
99 | 0.0043545 | 0.001091 | -0.0043542 | -0.001091 | 3.6881e-07 | -2.7977e-08 | 0.0066167 | 0.0066167 | 0.0066167 | 0.97927 | -0.14546 | 0.97918 | -0.14607 | 2.4506
100 | 0.036624 | 0.0091839 | -0.036616 | -0.0091811 | 8.5828e-06 | 2.8039e-06 | 0.055809 | 0.055809 | 0.055809 | 0.97654 | -0.16497 | 0.9763 | -0.16666 | 6.89
101 | 0.0043109 | 0.00108 | -0.0043105 | -0.00108 | 3.724e-07 | -4.228e-08 | 0.0064553 | 0.0064553 | 0.0064553 | 0.99369 | -0.04376 | 0.9936 | -0.044385 | 2.3909
102 | 0.0038254 | 0.00095845 | -0.0038253 | -0.00095846 | 6.4175e-08 | -1.5904e-08 | 0.0057288 | 0.0057288 | 0.0057288 | 0.9936 | -0.044385 | 0.99359 | -0.044506 | 2.1218
103 | 0.003582 | 0.00089748 | -0.0035819 | -0.00089752 | 1.3526e-07 | -4.5532e-08 | 0.0053644 | 0.0053645 | 0.0053645 | 0.99359 | -0.044506 | 0.99355 | -0.044779 | 1.9868
104 | 0.0028983 | 0.00072619 | -0.0028982 | -0.00072627 | 1.0347e-07 | -7.4176e-08 | 0.0043406 | 0.0043407 | 0.0043407 | 0.99355 | -0.044779 | 0.99351 | -0.045037 | 1.6076
105 | 0.0020817 | 0.00052163 | -0.0020817 | -0.00052164 | 4.3542e-10 | -7.634e-10 | 0.0031178 | 0.0031178 | 0.0031178 | 0.99351 | -0.045037 | 0.99351 | -0.045038 | 1.1547
106 | -0.15656 | -0.039507 | 0.15664 | 0.039541 | 8.9964e-05 | 3.4291e-05 | 0.23362 | 0.23362 | 0.23362 | 0.99757 | -0.016802 | 0.99816 | -0.01271 | 28.8419
107 | 0.00051561 | 0.00012914 | -0.00051561 | -0.00012922 | 2.2976e-09 | -7.907e-08 | 0.00077222 | 0.00077225 | 0.00077225 | 0.99351 | -0.045038 | 0.99351 | -0.045071 | 0.28602
108 | -0.045326 | -0.011406 | 0.045417 | 0.011441 | 9.0244e-05 | 3.4309e-05 | 0.068201 | 0.0682 | 0.068201 | 0.98918 | -0.07529 | 0.99121 | -0.061054 | 25.2595
109 | 0.0016066 | 0.00040216 | -0.0016065 | -0.00040262 | 1.4662e-07 | -4.5364e-07 | 0.0024241 | 0.0024243 | 0.0024243 | 0.98612 | -0.096871 | 0.98603 | -0.097531 | 0.8979
110 | -0.06002 | -0.015138 | 0.060079 | 0.01516 | 5.8161e-05 | 2.2218e-05 | 0.089596 | 0.089596 | 0.089596 | 0.9972 | -0.019373 | 0.9982 | -0.012468 | 33.1836
111 | -0.061141 | -0.015426 | 0.061151 | 0.01543 | 9.1644e-06 | 3.5017e-06 | 0.09118 | 0.09118 | 0.09118 | 0.9982 | -0.012468 | 0.99835 | -0.0114 | 33.7704
112 | -0.061969 | -0.015635 | 0.062069 | 0.015673 | 9.9281e-05 | 3.7941e-05 | 0.0924 | 0.0924 | 0.0924 | 0.99835 | -0.0114 | 1 | 0 | 34.2223
113 | 0.0004713 | 0.00011805 | -0.00047129 | -0.00011812 | 1.5308e-09 | -6.326e-08 | 0.00070561 | 0.00070563 | 0.00070563 | 0.99386 | -0.042613 | 0.99385 | -0.042636 | 0.26134
114 | 0.16297 | 0.041164 | -0.16288 | -0.04113 | 8.9544e-05 | 3.4152e-05 | 0.24261 | 0.24261 | 0.24261 | 1 | 0 | 0.99943 | -0.0039094 | 29.9525
115 | 0.0048411 | 0.0012129 | -0.004841 | -0.0012129 | 1.018e-07 | 2.1631e-09 | 0.0074023 | 0.0074023 | 0.0074023 | 0.97315 | -0.18928 | 0.97313 | -0.18943 | 2.7416
116 | -0.0059583 | -0.0014929 | 0.0059597 | 0.0014931 | 1.4075e-06 | 2.0362e-07 | 0.0091106 | 0.0091104 | 0.0091106 | 0.97315 | -0.18928 | 0.97339 | -0.18757 | 3.3743
117 | 0.0025732 | 0.00064449 | -0.0025731 | -0.00064457 | 9.0072e-08 | -8.1194e-08 | 0.0039345 | 0.0039346 | 0.0039346 | 0.97313 | -0.18943 | 0.9731 | -0.18968 | 1.4573
118 | 0.024973 | 0.0062581 | -0.024968 | -0.0062567 | 5.3432e-06 | 1.3979e-06 | 0.038176 | 0.038176 | 0.038176 | 0.97339 | -0.18757 | 0.97317 | -0.18912 | 4.7131
119 | -0.030933 | -0.0077512 | 0.030941 | 0.0077535 | 7.6436e-06 | 2.3268e-06 | 0.047287 | 0.047286 | 0.047287 | 0.97339 | -0.18757 | 0.97364 | -0.18578 | 5.8378
120 | 0.0020163 | 0.00050502 | -0.0020162 | -0.0005053 | 1.6024e-07 | -2.7392e-07 | 0.0030832 | 0.0030833 | 0.0030833 | 0.9731 | -0.18968 | 0.97302 | -0.19026 | 1.142
121 | 0.02271 | 0.0056909 | -0.022704 | -0.0056895 | 5.7197e-06 | 1.35e-06 | 0.034724 | 0.034725 | 0.034725 | 0.97317 | -0.18912 | 0.97292 | -0.19094 | 4.287
122 | -0.031386 | -0.007865 | 0.031418 | 0.0078749 | 3.2109e-05 | 9.8435e-06 | 0.047967 | 0.047966 | 0.047967 | 0.97364 | -0.18578 | 0.97466 | -0.1784 | 5.9218
123 | 0.021217 | 0.0053167 | -0.021212 | -0.0053156 | 4.8948e-06 | 1.0502e-06 | 0.032449 | 0.03245 | 0.03245 | 0.97292 | -0.19094 | 0.97269 | -0.1926 | 4.0061
124 | -0.031991 | -0.0080185 | 0.032005 | 0.0080229 | 1.4225e-05 | 4.3988e-06 | 0.04884 | 0.04884 | 0.04884 | 0.97466 | -0.1784 | 0.97511 | -0.17519 | 6.0297
125 | 0.020209 | 0.0050643 | -0.020205 | -0.0050636 | 3.8889e-06 | 7.6745e-07 | 0.030916 | 0.030916 | 0.030916 | 0.97269 | -0.1926 | 0.9725 | -0.19399 | 3.8168
126 | -0.032005 | -0.0080229 | 0.032011 | 0.0080248 | 6.3095e-06 | 1.9507e-06 | 0.04884 | 0.04884 | 0.04884 | 0.97511 | -0.17519 | 0.97531 | -0.17377 | 6.0296
127 | 0.018742 | 0.0046969 | -0.018741 | -0.0046966 | 1.5577e-06 | 2.6018e-07 | 0.028677 | 0.028677 | 0.028677 | 0.9725 | -0.19399 | 0.97241 | -0.19459 | 3.5404
128 | -0.16001 | -0.040383 | 0.16005 | 0.040401 | 4.6795e-05 | 1.7843e-05 | 0.23863 | 0.23863 | 0.23863 | 0.99816 | -0.01271 | 0.99846 | -0.010628 | 29.4605
129 | 0.0043542 | 0.001091 | -0.0043533 | -0.001091 | 8.5006e-07 | -6.436e-08 | 0.0066167 | 0.0066169 | 0.0066169 | 0.97918 | -0.14607 | 0.97898 | -0.14748 | 2.4507
130 | 0.035507 | 0.0089032 | -0.035497 | -0.0088999 | 1.0008e-05 | 3.2331e-06 | 0.054119 | 0.054119 | 0.054119 | 0.9763 | -0.16666 | 0.97602 | -0.16869 | 6.6814
131 | -0.0015402 | -0.00038601 | 0.0015402 | 0.00038584 | 5.1832e-08 | -1.6433e-07 | 0.0023608 | 0.0023608 | 0.0023608 | 0.97077 | -0.20645 | 0.9708 | -0.20621 | 0.87439
132 | -0.017031 | -0.0042673 | 0.017037 | 0.0042695 | 6.4129e-06 | 2.2645e-06 | 0.025589 | 0.025589 | 0.025589 | 0.99033 | -0.067319 | 0.99072 | -0.064598 | 9.4774
133 | 0.015711 | 0.0039364 | -0.015709 | -0.0039357 | 2.1567e-06 | 7.497e-07 | 0.023606 | 0.023606 | 0.023606 | 0.99033 | -0.067319 | 0.99019 | -0.068311 | 8.7429
134 | 0.015709 | 0.0039357 | -0.0157 | -0.0039328 | 8.2548e-06 | 2.8697e-06 | 0.023606 | 0.023606 | 0.023606 | 0.99019 | -0.068311 | 0.98965 | -0.072111 | 8.7429
135 | 0.012652 | 0.0031688 | -0.012646 | -0.0031668 | 6.166e-06 | 2.0208e-06 | 0.019022 | 0.019022 | 0.019022 | 0.98965 | -0.072111 | 0.98916 | -0.075637 | 7.0454
136 | 0.0038173 | 0.00095419 | -0.0038173 | -0.0009542 | 1.6522e-08 | -3.9551e-09 | 0.0057416 | 0.0057416 | 0.0057416 | 0.98916 | -0.075637 | 0.98915 | -0.075669 | 2.1265
137 | 0.0009023 | 0.00022362 | -0.00090222 | -0.0002245 | 8.1746e-08 | -8.8216e-07 | 0.0013565 | 0.0013568 | 0.0013568 | 0.98915 | -0.075669 | 0.98906 | -0.076335 | 0.50251
138 | -0.00036356 | -9.1117e-05 | 0.00036357 | 9.058e-05 | 7.8629e-09 | -5.3743e-07 | 0.00054704 | 0.00054685 | 0.00054704 | 0.98893 | -0.077279 | 0.98895 | -0.077122 | 0.20261
139 | -0.00090212 | -0.00022555 | 0.00090216 | 0.00022515 | 3.7314e-08 | -4.0227e-07 | 0.0013572 | 0.001357 | 0.0013572 | 0.98895 | -0.077122 | 0.98899 | -0.076822 | 0.50266
140 | -0.00090216 | -0.00022515 | 0.00090222 | 0.0002245 | 6.0074e-08 | -6.479e-07 | 0.001357 | 0.0013568 | 0.001357 | 0.98899 | -0.076822 | 0.98906 | -0.076335 | 0.5026
141 | 0.16103 | 0.040667 | -0.16091 | -0.040618 | 0.00012831 | 4.8931e-05 | 0.23986 | 0.23986 | 0.23986 | 0.99943 | -0.0039094 | 0.99861 | -0.0095825 | 29.613
142 | 0.16064 | 0.04055 | -0.16061 | -0.040541 | 2.3584e-05 | 8.9933e-06 | 0.23946 | 0.23946 | 0.23946 | 0.99861 | -0.0095825 | 0.99846 | -0.010628 | 29.5633
143 | 0.034191 | 0.0085727 | -0.034178 | -0.0085685 | 1.3331e-05 | 4.2433e-06 | 0.052129 | 0.052129 | 0.052129 | 0.97602 | -0.16869 | 0.97562 | -0.17151 | 6.4357
144 | 0.032769 | 0.0082152 | -0.032761 | -0.008213 | 7.1214e-06 | 2.2257e-06 | 0.049979 | 0.04998 | 0.04998 | 0.97562 | -0.17151 | 0.97541 | -0.17308 | 6.1703
145 | 0.032761 | 0.008213 | -0.032758 | -0.008212 | 3.1196e-06 | 9.7504e-07 | 0.04998 | 0.04998 | 0.04998 | 0.97541 | -0.17308 | 0.97531 | -0.17377 | 6.1703

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2262 | 0.056927

## res_load
| p_mw | q_mvar
0 | 0.00060656 | 0.00015202
1 | 0.00049207 | 0.00012332
2 | 0.0018305 | 0.00045876
3 | 0.0044192 | 0.0011075
4 | 0.0038072 | 0.00095416
5 | 0.001377 | 0.0003451
6 | 0.00099538 | 0.00024947
7 | 0.0014707 | 0.00036858
8 | 0.00034435 | 8.6302e-05
9 | 0.00078405 | 0.0001965
10 | 0.0023743 | 0.00059506
11 | 0.0023149 | 0.00058018
12 | 0.0017571 | 0.00044037
13 | 0.00041566 | 0.00010417
14 | 0.0021497 | 0.00053876
15 | 0.0002013 | 5.045e-05
16 | 0.0015535 | 0.00038935
17 | 0.0017523 | 0.00043916
18 | 0.00036961 | 9.2633e-05
19 | 0.0055618 | 0.0013939
20 | 0.00035133 | 8.8052e-05
21 | 0.0028258 | 0.00070822
22 | 0.0028548 | 0.00071549
23 | 0.014236 | 0.0035678
24 | 0.0104 | 0.0026064
25 | 0.0046186 | 0.0011575
26 | 0.0030056 | 0.00075328
27 | 0.0046261 | 0.0011594
28 | 0.00098111 | 0.00024589
29 | 0.0020238 | 0.0005072
30 | 0.00064783 | 0.00016236
31 | 0.00079893 | 0.00020023
32 | 0.0011339 | 0.00028419
33 | 0.0013986 | 0.00035053
34 | 0.0017586 | 0.00044074
35 | 0.000472 | 0.00011829
36 | 0.00086451 | 0.00021667
37 | 0.0039763 | 0.00099657
38 | 0.00072786 | 0.00018242
39 | 0.0011785 | 0.00029536
40 | 0.00092399 | 0.00023157
41 | 0.0012211 | 0.00030603
42 | 0.00057914 | 0.00014515
43 | 0.00084085 | 0.00021074
44 | 0.00022262 | 5.5795e-05
45 | 0.0031227 | 0.00078261
46 | 0.00061873 | 0.00015507
47 | 0.0013762 | 0.00034492
48 | 0.0015129 | 0.00037918
49 | 0.00078017 | 0.00019553
50 | 0.0013227 | 0.00033151
51 | 0.0013787 | 0.00034554
52 | 0.00077022 | 0.00019303
53 | 0.0046087 | 0.001155
54 | 0.0015561 | 0.00039
55 | 0.0012225 | 0.00030639
56 | 0.0010449 | 0.00026187
57 | 0.0015518 | 0.00038891
58 | 0.006217 | 0.0015581
59 | 0.0023288 | 0.00058366
60 | 0.0016918 | 0.000424
61 | 0.00098866 | 0.00024778
62 | 0.0024733 | 0.00061986
63 | 0.0010126 | 0.00025379
64 | 0.0027654 | 0.00069308
65 | 0.0038674 | 0.00096927
66 | 0.0029578 | 0.00074129
67 | 0.00098891 | 0.00024784
68 | 0.0016364 | 0.00041012
69 | 0.0028166 | 0.00070591
70 | 0.00048513 | 0.00012159
71 | 0.00024333 | 6.0983e-05
72 | 0.00068362 | 0.00017133
73 | 0.0008165 | 0.00020463
74 | 0.0010263 | 0.00025722
75 | 0.0015661 | 0.00039249
76 | 0.00051561 | 0.00012922
77 | 0.00059431 | 0.00014895
78 | 0.0017311 | 0.00043386
79 | 0.003288 | 0.00082404
80 | 0.0040497 | 0.001015
81 | 0.0010629 | 0.00026638
82 | 0.00081862 | 0.00020516
83 | 0.00039234 | 9.833e-05
84 | 0.00036075 | 9.0414e-05
85 | 0.00047129 | 0.00011812
86 | 0.0011172 | 0.00028
87 | 0.0022678 | 0.00056837
88 | 0.00055679 | 0.00013955
89 | 0.0022576 | 0.00056581
90 | 0.00044512 | 0.00011156
91 | 0.0020162 | 0.0005053
92 | 0.0014876 | 0.00037284
93 | 0.00057299 | 0.0001436
94 | 0.0010027 | 0.00025131
95 | 0.0014632 | 0.00036671
96 | 0.0020366 | 0.00051041
97 | 0.001205 | 0.00030201
98 | 0.0033612 | 0.0008424
99 | 0.0043533 | 0.001091
100 | 0.0013865 | 0.00034748
101 | 0.00044116 | 0.00011056
102 | 0.0011089 | 0.00027792
103 | 0.0015402 | 0.00038601
104 | 0.0012215 | 0.00030613
105 | 0.00132 | 0.00033082
106 | 0.0011513 | 0.00028855
107 | 0.0030484 | 0.000764
108 | 0.0088284 | 0.0022126
109 | 0.002915 | 0.00073058
110 | 0.00036356 | 9.1117e-05
111 | 0.00053855 | 0.00013497
112 | 0.0018471 | 0.00046294
113 | 0.00026969 | 6.759e-05
114 | 0.00055894 | 0.00014008
115 | 0.0013055 | 0.0003272
116 | 0.0014095 | 0.00035325
117 | 0.00074698 | 0.00018721
118 | 0.0016065 | 0.00040262

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1